## General information
General Information
Electricity Distribution Companies
1 | Name of the DISCOM | Bangalore Electricity Supply Company Limited
2 | i) Year of Establishment | 2002
| (ii) Government/Public/Private | Government
3 | DISCOM's Contact details & Address
i | City/Town/Village | Bangalore
ii | District | Bangalore
iii | State | Karnataka |  | Pin | 560001
iv | Telephone |  |  | Fax
4 | Registered Office
i | Company's Chief Executive Name | Sri Mahantesh Bilagi
ii | Designation | Managing Director
iii | Address | BESCOM, Corporate Office, K.R.Circle
iv | City/Town/Village | Bangalore |  | P.O.
v | District | Bangalore
vi | State | Karnataka |  | Pin | 560001
vii | Telephone | 080-22343311 |  | Fax
5 | Nodal Officers Details
i | Nodal Officer name(Designated at DISCOM,s) | Sri. M L Nagaraja, BESCOM
ii | Designation | Chief General Manager - Operations
iii | Address | Corporate office, K R Circle, Bangalore-01
iv | City/Town/Village | Bangalore |  | P.O
v | District | Bangalore
vi | State | Karnataka |  | Pin | 560 001
vii | Telephone | 080-223522487 |  | Fax
6 | Energy Manager Details
i | Name | Mr. H. B. Basavaraju
ii | Designation | Deputy General Manager |  | Whether EA or EM | EA
iii | EA/EM Registration No. | EA - 6827
iv | Telephone |  |  | Fax
v | Mobile | 9449844860 | E-mail ID | eabescom17@gmail.com ,gmmcom123@gmail.com
7 | Period Of information
| Year of( FY)information including Date and Month(Start and End) | 1st April 2022 to 30th June 2022

## summary
Performance Summary of Electricity Distribution Companies
1 | Period of Information Year of (FY) information including Date and Month (Start & End) | 1st April 2022 to 30th June 2022
2 | Technical Details
(a) | Energy Input Details
(i) | Input Energy Purchase (From Generation Source) | Million kwh | 9365.558
(ii) | Net input energy (at DISCOM Periphery after adjusting the transmission losses and energy traded) | Million kwh | 8970.7685
(iii) | Total Energy billed (is the Net energy billed, adjusted for energy traded)) | Million kwh | 8033.1953
(b) | Transmission and Distribution (T&D) loss Details | Million kwh | 937.5733
|  | % | 10.45%
| Collection Efficiency | % | 94.1%
(c) | Aggregate Technical & Commercial Loss | % | 15.74%
I/We undertake that the information supplied in this Document and Pro-forma is accurate to the best of my knowledge and if any of the information supplied is found to be incorrect and such information result into loss to the Central Government or State Government or any of the authority under them or any other person affected, I/we undertake to indemnify such loss.
Authorised Signatory and Seal
Name of Authorised Signatory: CGM (Operations)
Name of the DISCOM:BESCOM |  | Signature:-
Full Address:- KR circle, Nrupathunga Rd, Nunegundlapalli, Ambedkar Veedhi, Bengaluru, Karnataka 560001 |  | Name of Energy Manager/Auditor*: Sri Basavaraju H B
Registration Number: EA :6827

## Infrastructure Details
Form-Details of Input Infrastructure
1 | Parameters | Total | Covered during in audit | Verified by Auditor in Sample Check | Remarks (Source of data)
i | Number of circles | 9
ii | Number of divisions | 32
iii | Number of sub-divisions | 147
iv | Number of feeders | 5988
v | Number of DTs | 462257
vi | Number of consumers | 13471203
2 | Parameters | 66kV and above | 33kV | 11/22kV | LT
a. | Consumer details
i. | Number of conventional metered consumers |  |  | 10682 | 12363235
ii | Number of consumers with 'smart' meters |  |  | 0 | 70(Pilot)
iii | Number of consumers with 'smart prepaid' meters |  |  | 0 | 0
iv | Number of consumers with 'AMR' meters | 99(EHT Consumers) |  | 9300 | 12078
v | Number of consumers with 'non-smart prepaid' meters |  |  | 0 | 70793
vi | Number of unmetered consumers |  |  | 0 | 1004946
vii | Number of total consumers | 99 |  | 19982 | 13451122
b.i. | Number of conventionally metered Distribution Transformers | - |  |  | 125385
ii | Number of DTs with communicable meters | - |  |  | 0
iii | Number of unmetered DTs | - |  |  | 336872 (Out of 3,36,872 nos. of unmetered DTs, 1,20,093 nos. of DTs are to be metered, as the balance DTs are on the exclusive IP feeder (segregated Agriculture feeders under NJY project) and single water supply installations with exclusive DTCs, which are exempted from metering. )
| Total no. of Transformers |  |  |  | 462257
i. | Number of metered feeders |  |  |  | 5988
ii | Number of feeders with communicable meters |  |  |  | Monitored by KPTCL
iii | Number of unmetered feeders |  |  |  | Monitored by KPTCL
| Total no. of feeders |  |  |  | 5988
i. | Line length (ct km) |  |  | 127034.7 | 180630.58
ii | Length of Aerial Bunched Cables | HT ABC=1034.53 LT ABC=5649.20
iii | Length of Underground Cables | HT UG=9090.92 LT UG=2206.69
3 | Energy Input details
Sl. No. | Voltage level | Particulars | MU
i | 66kV and above | Long-Term Conventional | 8461.2927 | Includes input energy for franchisees | (PROVISIONAL)
Medium Conventional
Short Term Conventional
Banking
|  | Long-Term Renewable energy | 1519.8789
|  | Medium and Short-Term RE |  | Includes power from bilateral/PX/DEEP
|  | Captive, open access input | 329 | Any Power wheeled for any purchase other than sale to DISCOM.Does not include input for franchisee
|  | Sale of surplus power | -678.6365
|  | Quantum of inter-state transmission loss | 668.15 | As confirmed by SLDC, RLDC etc
|  | Power procured from inter-state sources | 9631.5351 | Based on data from Form 5
|  | Power at state transmission boundary | 8963.3851
ii | 33kV | Long-Term Conventional
Medium Conventional
Short Term Conventional
Banking
|  | Long-Term Renewable energy | 31.6884
Medium and Short-Term RE
Captive, open access input
Sale of surplus power
|  | Quantum of intra-state transmission loss | 0
|  | Power procured from intra-state sources | 31.6884
iii |  | Input in DISCOM wires network | 8995.0735
iv | 33 kV | Renewable Energy Procurement
Small capacity conventional/ biomass/ hydro plants Procurement
|  | Captive, open access input |  |  | Note: The qty includes 855 Captive/Open Access Input
v | 11 kV | Renewable Energy Procurement | 31.3345
Small capacity conventional/ biomass/ hydro plants Procurement
Sales Migration Input
vi | LT | Renewable Energy Procurement | 28.96 |  | 1). The Details are energy Exported , from 310 installations under Surya 2)SRTPV details for 4444 installations,out of which 305 installations are gross.
Sales Migration Input
vii |  | Energy Embedded within DISCOM wires network | 60.2945
viii |  | Total Energy Available/ Input | 8934.779
4 | Voltage level | Energy Sales Particulars | MU | Reference
i | LT Level | DISCOM' consumers |  | Include sales to consumers in franchisee areas, unmetered consumers
|  | Demand from open access, captive |  | Non DISCOM's sales
|  | Embedded generation used at LT level | 53.04 | Demand from embedded generation at LT level | 1). The Details are energy Exported , from 310 installations under Surya 2)SRTPV details for 4444 installations,out of which 305 installations are gross.
|  | Sale at LT level | 0
|  | Quantum of LT level losses | 0
|  | Energy Input at LT level |  |  | DTC are not metered 100 %,so value not available
ii | 11 kV Level | DISCOM' consumers | 8033.1953 | Include sales to consumers in franchisee areas, unmetered consumers | Total Consumption of HT & LT Category Consumers including open access
|  | Demand from open access, captive |  | Non DISCOM's sales
|  | Embedded generation at 11 kV level used |  | Demand from embedded generation at 11kV level
|  | Sales at 11 kV level | 8033.1953
|  | Quantum of Losses at 11 kV | 937.5673
|  | Energy input at 11 kV level | 8970.7625
iii | 33 kV Level | DISCOM' consumers |  | Include sales to consumers in franchisee areas, unmetered consumers
|  | Demand from open access, captive |  | Non DISCOM's sales
|  | Embedded generation at 33 kV or below level |  | This is DISCOM and OA demand met via energy generated at same voltage level
|  | Sales at 33 kV level | 0
|  | Quantum of Losses at 33 kV | 0
|  | Energy input at 33kV Level | 0
iv | > 33 kV | DISCOM' consumers |  | Include sales to consumers in franchisee areas, unmetered consumers | Note: The Consumption of EHT Consumers are included under 11KV HT Consumption
|  | Demand from open access, captive |  | Non DISCOM's sales
Cross border sale of energy
Sale to other DISCOMs
Banking
Energy input at > 33kV Level
|  | Sales at 66kV and above (EHV) | 0
Total Energy Requirement |  |  | 8970.7625
Total Energy Sales |  |  | 8033.1953
Energy Accounting Summary
5 | DISCOM | Input (in MU) | Sale (in MU) | Loss (in MU) | Loss %
i | LT | 0 |  |  | #DIV/0!
ii | 11 Kv | 8970.7625 | 8033.1953 | 937.5673 | 10.4514
iii | 33 kv | 0 | 0 | 0 | #DIV/0!
iv | > 33 kv | 0 | 0 | 0 | #DIV/0!
6 | Open Access, Captive | Input (in MU) | Sale (in MU) | Loss (in MU)
i | LT
ii | 11 Kv
iii | 33 kv
iv | > 33 kv
| Loss Estimation for DISCOM |  | Note: | 1) BESCOM does not have 33kv
| T&D loss | 937.5673 |  | 2)LT side DTC metering not done completely
| D loss | 269.4173 |  | 3) >33kv Level is monitored by KPTCL.
| T&D loss (%) | 10.45% |  | 4)11kv sales have both LT and HT Consumers
| D loss (%) | 3.003%

## Form-Input energy
Form-Input energy(Details of Input energy & Infrastructure)
A. Summary of energy input & Infrastructure
S.No | Parameters | [15 empty] | 1st Qtr of FY-23 (Provisional) | Remarks (Source of data) |  |  | yes
A.1 | Input Energy purchased (MU) | [15 empty] | 9365.558 | PP data(Provisional)-Input of March april and May |  |  | no
A.2 | Transmission loss (%) | [15 empty] | 4.215%
A.3 | Transmission loss (MU) | [15 empty] | 394.7895
A.4 | Energy sold outside the periphery (MU) | [15 empty] | 1.51 | PP data
A.5 | Open access sale (MU) | [15 empty] | 9.2646 | PP data- 11kv and >66kv
A.6 | EHT sale | [15 empty] | 750.4158
A.7 | Net input energy (received at DISCOM periphery or at distribution point,after adjustment)-(MU) | [15 empty] | 8970.7685 | Input from March to May
A.8 | Is 100% metering available at 66/33 kV (Select yes or no from list) | [15 empty] | yes | -
A.9 | Is 100% metering available at 11 kV (Select yes or no from list) | [15 empty] | yes | -
A.10 | % of metering available at DT | [15 empty] | 27.12% | (Out of 3,36,872 nos. of unmetered DTs, 1,20,093 nos. of DTs are to be metered, as the balance DTs are on the exclusive IP feeder (segregated Agriculture feeders under NJY project) and single water supply installations with exclusive DTCs, which are exempted from metering. )
A.11 | % of metering available at consumer end | [15 empty] | 92.54% | (M&C Data)
A.12 | No of feeders at 66kV voltage level | [15 empty] | 0 | -
A.13 | No of feeders at 33kV voltage level | [15 empty] | Nil | -
A.14 | No of feeders at 11kV voltage level | [15 empty] | 5988 | ALDC data
A.15 | No of LT feeders level | [15 empty] | 0 | -
A.16 | Line length (ckt. km) at 66kV voltage level | [15 empty] | 0 | -
A.17 | Line length (ckt. km) at 33kV voltage level | [15 empty] | 0 | -
A.18 | Line length (ckt. km) at 11kV voltage level | [15 empty] | 127034.7 | OH=116909.25 UG=9090.92 ABC=1034.53
A.19 | Line length (km) at LT level | [15 empty] | 180630.58 | OH=172774.70 UG=2206.69 ABC=5649.20
A.20 | Length of Aerial Bunched Cables | [15 empty] | HT ABC=1034.53 LT ABC=5649.20 | Operation section data
A.21 | Length of Underground Cables | [15 empty] | HT UG=9090.92 LT UG=2206.69 | Operation section data
A.22 | HT/LT ratio | [15 empty] | 1:1.42 | -
B. Meter reading of Input energy at injection points
S.No | ZONE | Circle | Voltge Level (KVA) | Division (KVA) | Sub-Division (KVA) | Feeder ID | Feeder Name\Station name | Feeder Metering Status (Metered/ unmetered/ AMI/AMR) | Status of Meter (Functional/Non-functional) | Metering Date | Feeder Type (Agri/ Industrial/Mixed) | Status of Communication |  |  | Period from April 2022 to June 2022(Provisional) |  |  |  | Sales | Remarks (Source of data)
[10 empty] | Date of last actual meter reading/ communication |  | % data received through automatically if feeder AMR/AMI | Number of hours when meter was unable to communicate in period | Total Number of hours in the period | Meter S.No | CT/PT ratio | Import (MU) | Export (MU)
B.1 | BMANZ | East | 66/11 kV | Vidhanasoudha | W4 | Bank - 1 | A - STATION | Metered/DLMS | Functional | 1st of Every month | Bank | In BESCOM all 11kV feeders are emanating from 66/11kV and above voltage Class stations. All these Feeders and Banks are under the Control of KPTCL(Transmission Utility). Further Bescom is not having any 33kV feeders . |  |  | Q0258490 | 1200/1 | 22.513 | 0 | Meter Reading Of Input Energy at injection points is the Bank Reading of Station that is considered.
B.2 | BMANZ | East | 66/11 kV | Vidhanasoudha | W4 | Bank - 2 | A - STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258558 | 1200/1 | 9.7394 | 0
B.3 | BMANZ | East | 66/11 kV | Vidhanasoudha | W4 | Bank - 3 | A - STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258501 | 1200/1 | 15.2879 | 0
| BMANZ | East | 66/11 kV | Vidhanasoudha | W4 | Bank - 3A | A - STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19000184 | 1200/1-1 | 8.054 | 0
B.4 | BMANZ | East | 66/11 kV | Vidhanasoudha | W4 | Bank - 4 | A - STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258478 | 1200/1 | 11.7067 | 0
B.5 | BMANZ | North | 66/11 kV | Jalahalli | C3 | Bank - 1 | ABBIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479543 | 1200/1 | 11.9666 | 0
B.6 | BMANZ | North | 66/11 kV | Jalahalli | C3 | Bank - 2 | ABBIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479543 | 1200/1 | 14.8222 | 0
B.7 | BRAZ | Kolar | 66/11 kV | Kolar | Srinivaspura | BANK-1 | ADAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259856 | 600/1 | 3.6539 | 0
B.8 | BRAZ | Kolar | 66/11 kV | Kolar | Srinivaspura | BANK-2 | ADAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247150 | 800/1 | 1.5666 | 0
B.9 | BRAZ | Kolar | 66/11 KV | Kolar | Srinivaspura | BANK-3 | ADAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094141 | 800/1 | 3.0662 | 0
| BRAZ | Ramnagar | 66/11 KV | Kanakpura | Sathanur | BANK-1 | ACHHALU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009817 | 800/1 | 2.3211 | 0
| BRAZ | Ramnagar | 66/11 KV | Kanakpura | Sathanur | BANK-2 | ACHHALU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009822 | 800/1 | 0.883 | 0
B.10 | BRAZ | Ramnagar | 66/11 kV | Magadi | Magadi | Bank - 1 | AGALAKOTE ( HULIKATTE) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO245563 | 6001-1-1A | 2.1246 | 0
B.11 | BRAZ | Ramnagar | 66/11 kV | Magadi | Magadi | Bank - 2 | AGALAKOTE ( HULIKATTE) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246007 | 400/1-1-1A | 2.1475 | 0 | The Station & Bank feeders are monitored by KPTCL
B.12 | BRAZ | Ramnagar | 66/11 kV | Ramnagar | CHANNAPATNA RURAL | BANK-1 | AKKURMOLE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245681 | 800/1 | 2.7101 | 0
B.13 | BRAZ | Ramnagar | 66/11 kV | Ramnagar | CHANNAPATNA RURAL | BANK-1A | AKKURMOLE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245040 | 800/1 | 7.559 | 0
B.14 | BRAZ | Ramnagar | 66/11 kV | Ramnagar | CHANNAPATNA RURAL | BANK-2 | AKKURMOLE | Metered/DLMS | Functional | 1st of Every month | Bank | Note: Communication work is under process under the supervision of Scada KPTCL |  |  | Q0245708 | 800/1 | 4.1554 | 0
B.15 | BRAZ | Ramnagar | 66/11 kV | Kanakpura | Kanakpura Urban | Bank - 1 | ALLIMARANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16093950 | 800/1 | 3.2236 | 0
B.16 | BRAZ | BRC | 66/11 kV | Nelamangala | Nelamangala | Bank-1 | ALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17051090 | 800-400/1-1-1A | 8.0982 | 0
B.17 | BRAZ | BRC | 66/11 kV | Nelamangala | Nelamangala | BANK-2 | ALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17051093 | 800-400/1-1-1A | 10.956 | 0
B.18 | BMASZ | South | 66/11 kV | Kormangala | S3 | Bank - 1 | AMARJYOTHI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246508 | 1200/1 | 11.8464 | 0
B.19 | BMASZ | South | 66/11 kV | Kormangala | S3 | Bank - 2 | AMARJYOTHI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246528 | 1200/1 | 13.3932 | 0
B.20 | BMASZ | South | 66/11 kV | Kormangala | S3 | Bank - 2A | AMARJYOTHI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246915 | 1200/1 | 14.3076 | 0
B.21 | BRAZ | KOLAR | 66/11 kV | KGF | KGF_RA | BANK-1 | ANDERSONPET | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247080 | 800/1 | 8.261 | 0
B.22 | BRAZ | KOLAR | 66/11 kV | KGF | KGF_RA | BANK-2 | ANDERSONPET | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246981 | 800/1 | 6.1288 | 0
B.23 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ANEKAL | Bank-1 | ANEKAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245298 | 1200/1 | 11.2916 | 0
B.24 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ANEKAL | BANK-2 | ANEKAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245610 | 1200/1 | 13.4106 | 0
B.25 | BMASZ | South | 66/11 kV | HSR | S12 | Bank - 1 | ANJANAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258731 | 1200/1 | 10.14 | 0
B.26 | BMASZ | South | 66/11 kV | HSR | S12 | Bank - 2 | ANJANAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258732 | 1200/1 | 6.6872 | 0
B.27 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (U) | BANK-1 | APPAREL PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245088 | 1200/1 | 10.8346 | 0
B.28 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (U) | BANK-2 | APPAREL PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245069 | 1200/1 | 21.2412 | 0
B.29 | BMASZ | South | 66/11 kV | Jayanagar | S15 | Bank - 1 | AREHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258742 | 1200/1 | 12.4402 | 0
B.30 | BMASZ | South | 66/11 kV | Jayanagar | S15 | Bank - 2 | AREHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258743 | 1200/1 | 15.0848 | 0
B.31 | BRAZ | BRC | 66/11 kV | HOSAKOTE | AVALAHALLI | Bank - 1 | ARMY WELFARE HOUSING ORGANISATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247003 | 1200/1 | 6.8954 | 0
B.32 | BRAZ | BRC | 66/11 kV | HOSAKOTE | AVALAHALLI | Bank - 1A | ARMY WELFARE HOUSING ORGANISATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167052 | 2000/1 | 10.798 | 0
| BRAZ | BRC | 66/11 kV | HOSAKOTE | AVALAHALLI | Bank - 2A | ARMY WELFARE HOUSING ORGANISATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 21001401 | 1200/1 | 0.422 | 0
B.33 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ATTIBELE | BANK-1 | ATTIBELE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245287 | 2000/1 | 22.8864 | 0
B.34 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ATTIBELE | BANK-2 | ATTIBELE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245604 | 1200/1 | 21.2117 | 0
B.35 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ATTIBELE | BANK-2A | ATTIBELE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245451 | 1200/1 | 18.9074 | 0
B.36 | BMANZ | North | 66/11 kV | Hebbal | C7 | Bank - 1 | Attur YELAHANKA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259495 | 1200/1 | 18.6144 | 0
B.37 | BMANZ | North | 66/11 kV | Hebbal | C7 | Bank - 2 | Attur YELAHANKA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16195350 | 1200/1 | 23.9418 | 0
B.38 | BMASZ | South | 66/11 kV | Koramangala | S16 | Bank - 1 | AUDOGODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 21003055 | 1200/1 A | 18.118 | 0
B.39 | BMASZ | South | 66/11 kV | Koramangala | S16 | Bank - 2 | AUDOGODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005507 | 2000/11A | 18.24 | 0
B.40 | BMASZ | South | 66/11 kV | Koramangala | S16 | Bank - 3 | AUDOGODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259109 | 2000/1 | 20.0198 | 0
B.41 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 1 | AUSTIN TOWN | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008085 | 1200/1 | 17.274 | 0
B.42 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 2 | AUSTIN TOWN | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167051 | 1200/1 | 14.325 | 0
B.43 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 3 | AUSTIN TOWN | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259112 | 1200/1 | 12.3815 | 0
| BMASZ | South | 66/11 kV | HSR | S10 | Bank - 1 | ANNABEL (DLF) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005573 | 1200/1 | 0.704 | 0
| BMASZ | South | 66/11 kV | HSR | S10 | Bank - 2 | ANNABEL (DLF) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005555 | 1200/1 | 0.629 | 0
B.44 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-1 | AVANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246780 | 400/1 | 2.5235 | 0
B.45 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-1 | AVANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246780 | 400/1 | 0 | -0.10344
B.46 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-2 | AVANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0243371 | 800/1 | 3.7823 | 0
| BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-2 | AVANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0243371 | 800/1 | 0 | 0
B.47 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DABASPETE | BANK-1 | Averahalli | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19000135 | 800/1 | 6.3706 | 0
B.48 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DABASPETE | BANK-2 | Averahalli | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19000126 | 800/1 | 0 | 0
B.49 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 1 | B- STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q 0246663 | 1200/1 | 13.2686 | 0
B.50 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 2 | B- STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246868 | 1200/1 | 20.0344 | 0
B.51 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 3 | B- STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247082 | 1200/1 | 19.3922 | 0
B.52 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 4 | B- STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20005919 | 1200/1 | 15.007 | 0
B.53 | CTAZ | TUMKUR | 66/11 KV | MADHUGIRI | MADHUGIRI | Bank - 1 | B V Halli | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20005919 | 1200/1 | 4.2027 | 0
B.54 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-1 | BAGEPALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246323 | 1200/1 | 10.3152 | 0
B.55 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-2 | BAGEPALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245036 | 1200/1 | 12.69 | 0
B.56 | BRAZ | RAMANAGAR | 66/11 KV | CHANDAPURA | ANEKAL | Bank - 1 | BAGGANADODDI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009818 | 800/1 | 3.7437 | 0
B.57 | BMASZ | South | 66/11 kV | Koramangala | S17 | BANK-1 | BAGHMANE TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246515 | 1200/1 | 12.363 | 0
B.58 | BMASZ | South | 66/11 kV | Koramangala | S17 | BANK-1A | BAGHMANE TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246930 | 1200/1 | 10.7585 | 0
B.59 | BMASZ | South | 66/11 kV | Koramangala | S17 | BANK-2 | BAGHMANE TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246949 | 1200/1 | 0 | 0
B.60 | BMASZ | South | 66/11 kV | Koramangala | S17 | BANK-2A | BAGHMANE TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246989 | 1200/1 | 19.3772 | 0
B.61 | BMASZ | South | 66/11 kV | Koramangala | S17 | BANK-1 | BAGHMANE WORLD Trade Centre | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246735 | 1200/1 | 17.5564 | 0
B.62 | BMASZ | South | 66/11 kV | Koramangala | S17 | BANK-2 | BAGHMANE WORLD Trade Centre | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247256 | 2000/1 | 23.401 | 0
B.63 | BMASZ | West | 66/11 kV | RRNagar | W1 | Bank -1 | BANASHANKARI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258628 | 1200/1 | 14.8338 | 0
B.64 | BMASZ | West | 66/11 kV | RRNagar | W1 | Bank -1A | BANASHANKARI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 4183991 | 1200/1A | 0 | 0
B.65 | BMASZ | West | 66/11 kV | RRNagar | W1 | Bank -2 | BANASHANKARI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258636 | 2000/1 | 20.4978 | 0
B.66 | BMASZ | West | 66/11 kV | RRNagar | W1 | Bank -2A | BANASHANKARI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 4183999 | 1200/1A | 0 | 0
B.67 | BMASZ | West | 66/11 kV | RRNagar | W1 | Bank -3 | BANASHANKARI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258674 | 1200/1 | 16.405 | 0
B.68 | BMASZ | West | 66/11 kV | RRNagar | W1 | Bank -3A | BANASHANKARI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258669 | 1200/1 | 11.4656 | 0
B.69 | BMANZ | BANGALORE EAST | 66/11 kV | SHIVAJINAGAR | E8 | Bank - 1 | BANASWADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258891 | 1200/1 | 23.6827 | 0
B.70 | BMANZ | BANGALORE EAST | 66/11 kV | SHIVAJINAGAR | E8 | Bank - 1A | BANASWADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258894 | 1200/1 | 13.607 | 0
B.71 | BMANZ | BANGALORE EAST | 66/11 kV | SHIVAJINAGAR | E8 | Bank - 2 | BANASWADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258835 | 2000/1 | 21.8536 | 0
B.72 | BMANZ | BANGALORE EAST | 66/11 kV | SHIVAJINAGAR | E8 | Bank - 2A | BANASWADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258844 | 2000/1 | 5.161 | 0
B.73 | BMANZ | BANGALORE EAST | 66/11 kV | SHIVAJINAGAR | E8 | Bank - 3 | BANASWADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258832 | 1200/1 | 18.9259 | 0
B.74 | BRAZ | KOLAR | 66/11 kV | KGF | BANGARAPETE | BANK-1 | BANGARPET | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247010 | 800/1 | 7.7186 | 0
B.75 | BRAZ | KOLAR | 66/11 kV | KGF | BANGARAPETE | BANK-2 | BANGARPET | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247030 | 1200/1A | 11.8805 | 0
B.76 | BRAZ | KOLAR | 66/11 kV | KGF | BANGARAPETE | Bank-3 | BANGARPET | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247058 | 1200/1A | 12.8446 | 0
B.77 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | Bank-1 | BANNERGATTA RD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | L&T 21003077 | 1200/1 | 15.5056 | 0
B.78 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | Bank-2 | BANNERGATTA RD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | L&T 21001938 | 1200/1 | 16.693 | 0
B.79 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | Bank- 1 | BEGUR (BIAL) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246414 | 800/1 | 12.7381 | 0
B.80 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | Bank- 2 | BEGUR (BIAL) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246430 | 800/1 | 3.2514 | 0
B.81 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BEVOORU | Bank-1 | BEVOOR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245031 | 400/1 | 3.2199 | 0
B.82 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BEVOORU | Bank-2 | BEVOOR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245617 | 800/1 | 4.5405 | 0
B.83 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | Bank -1 | BIDADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KEB16469 | 1200/1 | 7.6 | 0
B.84 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | Bank -1A | BIDADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258538 | 1200/1 | 2.9956 | 0
B.85 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | Bank -2 | BIDADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KEB16466 | 2000/1 | 26.9906 | 0
B.86 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | Bank -3 | BIDADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258437 | 2000/1 | 19.7756 | 0
B.87 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | Bank -3 | BIDADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258437 | 2000/1 | 0 | -0.0086
B.88 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | NELAMANGALA | Bank - 1 | BIEC | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18088384 | 1200/1 | 0 | 0
B.89 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | NELAMANGALA | Bank - 2 | BIEC | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18088414 | 1200/1 | 18.4466 | 0
B.90 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR RURAL | Bank -1 | BIJJAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245682 | 800/1 | 1.7526 | 0
B.91 | BMASZ | South | 66/11 kV | Jayanagar | S2 | BANK 1 | BMTC | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259119 | 1200/1 | 12.6898 | 0
B.92 | BMASZ | South | 66/11 kV | Jayanagar | S2 | BANK 1A | BMTC | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259101 | 1200/1 | 4.8298 | 0
B.93 | BMASZ | South | 66/11 kV | Jayanagar | S2 | BANK 2 | BMTC | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259042 | 1200/1 | 15.4538 | 0
B.94 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | CHANDAPURA | Bank -1 | Bommasandra Industrial Area | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246201 | 2000/1 | 34.9032 | 0
B.95 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | CHANDAPURA | Bank -2 | Bommasandra Industrial Area | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245950 | 2000/1 | 30.5322 | 0
| BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI RURAL | Bank -1 | BOMMEPALLI CROSS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | L&T-19004932 | 200/1 | 3.2006 | 0
| BRAZ | KOLAR | 66/11 kV | Chintamani | Chintamani Rural | Bank -1 | BURUDUGUNTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19007988 | 800/1 | 1.7357 | 0
B.96 | BMANZ | North | 66/11 kV | Malleshwaram | C2 | Bank - 1 | BRIGADE GATEWAY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259430 | 1200/1 | 8.4902 | 0
B.97 | BMANZ | North | 66/11 kV | Malleshwaram | C2 | Bank - 2 | BRIGADE GATEWAY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259374 | 1200/1 | 7.7 | 0
B.98 | BMANZ | East | 66/11 kV | WhiteField | E12 | BANK-1 | BRIGADA METROPOLIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247244 | 2000/1 | 13.2302 | 0
B.99 | BMANZ | East | 66/11 kV | WhiteField | E12 | BANK-1A | BRIGADA METROPOLIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16191975 | 2000/1 | 11.9207 | 0
B.100 | BMANZ | East | 66/11 kV | WhiteField | E12 | BANK-2 | BRIGADA METROPOLIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246983 | 1200/1 | 11.3265 | 0
| BMANZ | East | 66/11 kV | WhiteField | E12 | BANK-2A | BRIGADA METROPOLIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19004123 | 2000/1 | 0.25672 | 0
B.101 | BMASZ | West | 66/11 kV | Kengeri | K3 | Bank -1 | BRIGADE MEADOWS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17031112 | 1200/1 | 5.315 | 0
B.102 | BMASZ | West | 66/11kv | Kengeri | K3 | BANK 2 | BRIGADE MEADOWS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17031027 | 1200/1 | 8.986 | 0
B.103 | BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 1 | BRINDAVAN | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245299 | 2000/1 | 0 | 0
B.104 | BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 2 | BRINDAVAN | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245977 | 2000/1 | 0 | 0
B.105 | BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 3 | BRINDAVAN | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245586 | 1200/1 | 0 | 0
| BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 1 | 220kV Brindavan GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245299 | 2000/1A | 29.0144 | 0
| BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 2 | 220kV Brindavan GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245977 | 2000/1 | 24.5972 | 0
| BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 3 | 220kV Brindavan GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245586 | 1200/1 | 16.0949 | 0
B.106 | BMASZ | South | 66/11 kV | HSR | S8 | BANK 1 | BTM IV Phase | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259119 | 1200/1 | 20.9723 | 0
| BMASZ | South | 66/11 kV | HSR | S8 | BANK 1A | BTM IV Phase | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259101 | 1200/1 | 0 | 0
B.107 | BMASZ | South | 66/11 kV | HSR | S8 | BANK 2 | BTM IV Phase | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259042 | 1200/1 | 21.329 | 0
B.108 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | Bank - 1 | BUDIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247477 | 1200/1 | 8.3964 | 0
B.109 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | Bank - 2A | BUDIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247487 | 1200/1 | 8.4296 | 0
B.110 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | Bank - 2B | BUDIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247525 | 1200/1 | 10.1933 | 0
B.111 | BRAZ | KOLAR | 66/11 kV | KGF | BANGARAPETE | BANK-1 | BUDIKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246865 | 800/1 | 3.8391 | 0
B.112 | BRAZ | KOLAR | 66/11 kV | KGF | BANGARAPETE | BANK-1 | BUDIKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246865 | 800/1 | 0 | -0.13584
B.113 | BRAZ | KOLAR | 66/11 kV | KGF | BANGARAPETE | BANK-2 | BUDIKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247011 | 800/1 | 4.5937 | 0
B.114 | BRAZ | KOLAR | 66/11 kV | KGF | BANGARAPETE | BANK-2 | BUDIKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247011 | 800/1 | 0 | 0
B.115 | BMASZ | West | 66/11 kV | Kengeri | K2 | BANK-1 | BYADARAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245470 | 1200/1 | 20.8632 | 0
B.116 | BMASZ | West | 66/11 kV | Kengeri | K2 | BANK-2 | BYADARAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245488 | 2000/1 | 28.3346 | 0
B.117 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-1 | BYRAKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247234 | 800/400/1-1-1A | 5.5055 | 0
B.118 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-2 | BYRAKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246711 | 800/400/1-1-1A | 4.901 | 0
B.119 | BMANZ | East | 66/11 kV | Shivajinagar | E1 | Bank - 1 | C - STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258900 | 1200/1 | 23.5567 | 0
B.120 | BMANZ | East | 66/11 kV | Shivajinagar | E1 | Bank - 1A | C - STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258907 | 1200/1 | 9.7802 | 0
B.121 | BMANZ | East | 66/11 kV | Shivajinagar | E1 | Bank - 2 | C - STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258905 | 1200/1 | 12.2677 | 0
B.122 | BMANZ | East | 66/11 kV | Shivajinagar | E1 | Bank - 2A | C - STATION | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258834 | 1200/1 | 12.8694 | 0
B.123 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | CHIKKABALLAPURA_RA | BANK-1 | C.B.PURA(I.A) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0 245383 | 800/1 | 5.1894 | 0
B.124 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | CHIKKABALLAPURA_RA | BANK-2 | C.B.PURA(I.A) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245399 | 800/1 | 10.2746 | 0
B.125 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | CHIKKABALLAPURA_RA | BANK-3 | C.B.PURA(I.A) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245419 | 1200/1 | 16.4849 | 0
B.126 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK 1 | CESSNA PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246888 | 2000/1 | 28.459 | 0
B.127 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK 2 | CESSNA PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247051 | 2000/1 | 15.1532 | 0
B.128 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | Bank-1 | CHAKAVELU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246336 | 1200/1 | 4.9633 | 0
B.129 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | Bank -2 | CHAKAVELU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246371 | 600/1 | 3.8738 | 0
B.130 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | CHANDAPURA | BANK-1 | CHANDAPUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q.0245366 | 1200/1 | 8.698 | 0
B.131 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | CHANDAPURA | BANK-2 | CHANDAPUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q.0245213 | 1200/1 | 19.3982 | 0
B.132 | BMASZ | West | 66/11 kV | Rajajinagar | N2 | Bank - 1 | CHANDRA LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245808 | 2000/1 | 18.9738 | 0
B.133 | BMASZ | West | 66/11 kV | Rajajinagar | N2 | Bank - 2 | CHANDRA LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245914 | 2000/1 | 21.6982 | 0
B.134 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | TAVAREKERE | Bank - 1 | CHANDRAPPA CIRCLE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245993 | 800/1-1-1A | 5.1317 | 0
B.135 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | TAVAREKERE | Bank - 2 | CHANDRAPPA CIRCLE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245573 | 1200/1-1-1A | 16.294 | 0
B.136 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | CHANNAPATNA_RA | BANK-1 | CHANNAPATNA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245547 | 800/1 | 8.2085 | 0
B.137 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | CHANNAPATNA_RA | BANK-2 | CHANNAPATNA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246226 | 1200/1 | 17.3532 | 0
B.138 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | Bank-1 | CHANNARAYAPATNA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005492 | 800/1 A | 1.1878 | 0
B.139 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | Bank -2 | CHANNARAYAPATNA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005530 | 600/1 A | 3.0957 | 0
B.140 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR URBAN | BANK-1 | CHATHRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16195344 | 400/1 | 3.9916 | 0
B.141 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR URBAN | BANK-2 | CHATHRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16194175 | 200/1 | 2.0413 | 0
B.142 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR URBAN | BANK-2 | CHATHRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16194175 | 200/1 | 0 | -0.1128
B.143 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | Bank-1 | CHEEMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247214 | 400/1 | 5.837 | 0
B.144 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | Bank-2 | CHEEMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246832 | 800/1 | 5.0006 | 0
B.145 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-1 | CHELUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252698 | 1200/1 | 2.4802 | 0
B.146 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-1 | CHELUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252698 | 1200/1 | 0 | -0.36018
B.147 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | CHIKKABALLAPURA_RA | BANK-1 | CHIKKABALLAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245196 | 1200/1 | 10.8348 | 0
B.148 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | CHIKKABALLAPURA_RA | BANK-2 | CHIKKABALLAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245376 | 1200/1 | 12.8304 | 0
B.149 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGARA RURAL | RAMANAGARA RURAL | BANK-1 | CHIKKAGANGANAWADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258400 | 400/1 | 1.8636 | 0
B.150 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR URBAN | BANK-1 | CHIKKENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245855 | 800/1 | 4.7325 | 0
B.151 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR URBAN | BANK-2 | CHIKKENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245909 | 800/1 | 3.3885 | 0
B.152 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI_RA | BANK-1 | CHINTAMANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247026 | 1200/1 | 14.6822 | 0
B.153 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI_RA | BANK-2 | CHINTAMANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246592 | 1200/1 | 13.4474 | 0
| BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | VEERASANDRA | BANK-1 | CHOKKASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008224 | 800/1 | 4.8386 | 0
| BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | VEERASANDRA | BANK-2 | CHOKKASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008232 | 800/1 | 4.9129 | 0
B.154 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALLAPURA_RA | BANK-1 | D CROSS (DB PURA) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245207 | 1200/1 | 13.6194 | 0
B.155 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALLAPURA_RA | BANK-2 | D CROSS (DB PURA) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245059 | 1200/1 | 19.3278 | 0
| BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (U) | BANK-1 | DBPura | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 21001956 | 1200/1 | 0.792 | 0
| BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (U) | BANK-2 | DBPura | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 21001328 | 1200/1 | 0.365 | 0
B.156 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (U) | BANK-1 | D.B.PURA KIADB (220KV ) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245134 | 1200/1 | 16.1072 | 0
B.157 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (U) | BANK-2 | D.B.PURA KIADB (220KV ) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245117 | 1200/1 | 14.3324 | 0
| BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (U) | BANK-1B | D.B.PURA KIADB (220KV ) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245101 | 1200/1 | 2.2679 | 0
B.158 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (U) | BANK-3 | D.B.PURA KIADB (220KV ) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20006018 | 1200/1 | 6.7291 | 0
B.159 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GUDIBANDE | Bank-I | D.PALYA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246293 | 600/1 | 4.3313 | 0
B.160 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GUDIBANDE | Bank-2 | D.PALYA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246403 | 600/1 | 6.2122 | 0
B.161 | BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | BANK-1 | DALASNUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259851 | 600/1 | 3.7135 | 0
B.162 | BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | BANK-2 | DALASNUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247121 | 600/1 | 4.4512 | 0
B.163 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BEVOORU | BANK-1 | DASHAWARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17117796 | 1200/1 | 5.1293 | 0
B.164 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | BANK-1 | DEVANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245265 | 1200/1 | 16.7045 | 0
B.165 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | BANK-2 | DEVANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245243 | 1200/1 | 13.2716 | 0
B.166 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | BANK-3 | DEVANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245097 | 1200/1 | 17.5309 | 0
B.167 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | BANK-1 | DEVANAHALLI (220kV KIADB Hardware Park) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0469725 | 1200/1 | 7.5433 | 0
B.168 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-1 | DEVANGUNDHI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | X0623951 | 1200/1 | 6.988 | 0
B.169 | BRAZ | BANGALORE RURAL | 66/11 KV | HOSAKOTE | HOSAKOTE | BANK-1 | DEVANGUNDHI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | X0623951 | 1200/1 | 0 | -0.02886
B.170 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-2 | DEVANGUNDHI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258468 | 600/1 | 7.1566 | 0
B.171 | BMASZ | South | 66/11 kV | Koramangala | S7 | Bank - 1 | DEVARABISENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19004915 | 2000/1 | 13.9944 | 0
B.172 | BMASZ | South | 66/11 kV | Koramangala | S7 | Bank - 2 | DEVARABISENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005560 | 2000/1 | 18.271 | 0
B.173 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-1 | DIBBURAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246556 | 800/1 | 7.0072 | 0
B.174 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-2 | DIBBURAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246503 | 800/1 | 4.6488 | 0
B.175 | BMANZ | North | AUX | Hebbal |  | AUX | Disel Plant Consumption including Colony (KPCL) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | PNL09637 | 300/1 | 0 | 0
B.176 | BMANZ | North | AUX | Hebbal |  | AUX | Disel Plant Consumption including Colony (KPCL) (6.3MVA Transformer) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 210053282 | 300/1 | 0 | 0
B.177 | BMANZ | North | AUX | Hebbal |  | AUX | Disel Plant Consumption including Colony (KPCL) (GENERATOR TRANSFORMER-1) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  |  | 300/1 | 0 | 0
B.178 | BMANZ | North | AUX | Hebbal |  | AUX | Disel Plant Consumption including Colony (KPCL) (GENERATOR TRANSFORMER-3) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 210053286 | 300/1 | 0 | 0
B.179 | BMASZ | South | 66/11 kV | Koramangala | S7 | Bank -1 | DIVYASHREE TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247262 | 1200/1 | 18.1955 | 0
B.180 | BMASZ | South | 66/11 kV | Koramangala | S7 | Bank -2 | DIVYASHREE TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247236 | 1200/1 | 15.0707 | 0
B.181 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK-3 | DIVYASHREE TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247259 | 1200/1 | 7.4101 | 0
B.182 | BRAZ | BANGALORE RURAL | 220/66/11 kV | NELAMANGALA | DABASPETE | BANK-1 | DOBBESPET | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245160 | 2000/1-1-1A | 27.5872 | 0
B.183 | BRAZ | BANGALORE RURAL | 220/66/11 kV | NELAMANGALA | DABASPETE | BANK-2 | DOBBESPET | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245333 | 2000/1-1-1A | 12.5602 | 0
B.184 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (R) | BANK-1 | DODDABELAVANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245267 | 600/1 | 6.014 | 0
B.185 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (R) | BANK-2 | DODDABELAVANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245062 | 1200/1 | 11.5648 | 0
B.186 | BRAZ | KOLAR | 66/11 kV | KGF | BETHAMANGLA | BANK-1 | DODDAKARI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17051101 | 800/1 | 4.2084 | 0
B.187 | BRAZ | KOLAR | 66/11 kV | KGF | BETHAMANGLA | BANK-2 | DODDAKARI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17031048 | 800/1 | 4.3326 | 0
B.188 | BRAZ | KOLAR | 66/11 kV | KGF | BETHAMANGLA | BANK-2 | DODDAKARI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17031048 | 800/1 | 0 | -0.0012
B.189 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | SATHANURU | BANK-1 | DODDALAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245934 | 400/1 | 3.546 | 0
B.190 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | SATHANURU | BANK-2 | DODDALAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245668 | 400/1 | 3.0392 | 0
B.191 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ATTIBELE | BANK-1 | DOMMASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245494 | 2000/1 | 18.8464 | 0
B.192 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ATTIBELE | BANK-2 | DOMMASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245548 | 2000/1 | 10.531 | 0
B.193 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 1 | EAST DIVN COMPOUND | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258985 | 2000/1 | 9.7072 | 0
B.194 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 2 | EAST DIVN COMPOUND | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258947 | 2000/1 | 8.1568 | 0
B.195 | BMASZ | South | 66/11 kV | HSR | S13 | Bank -1 | ELECTRONIC CITY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259190 | 1200/1 | 20.0095 | 0
B.196 | BMASZ | South | 66/11 kV | HSR | S13 | Bank -2 | ELECTRONIC CITY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259228 | 1200/1 | 20.1815 | 0
B.197 | BMASZ | South | 66/11 kV | HSR | S13 | BANK-3 | ELECTRONIC CITY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259170 | 1200/1 | 23.4798 | 0
B.198 | BMASZ | South | 66/11 kV | HSR | S8 | Bank -1 | ELECTRONIC CITY- Ph -1 Sec-2 | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259187 | 1200/1 | 13.943 | 0
B.199 | BMASZ | South | 66/11 kV | HSR | S8 | Bank -3 | ELECTRONIC CITY- Ph-1 Sec-2 | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259054 | 1200/1 | 21.423 | 0
B.200 | BMASZ | South | 66/11 kV | HSR | S8 | Bank -2 | ELECTRONIC CITY- Ph-1 Sec-2 | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KEB02288 | 1200/1A | 16.145 | 0
B.201 | BMASZ | South | 66/11 kV | HSR | S13 | Bank -1 | ELECTRONIC CITY- Ph-2 Sec-2 | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259200 | 1200/1 | 14.7572 | 0
B.202 | BMASZ | South | 66/11 kV | HSR | S13 | Bank -2 | ELECTRONIC CITY- Ph-2 Sec-2 | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259306 | 1200/1 | 19.9046 | 0
B.203 | BMASZ | South | 66/11 kV | HSR | S13 | Bank -3 | ELECTRONIC CITY- Ph-2 Sec-2 | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094083 | 1200/1 | 20.526 | 0
B.204 | BMASZ | South | 66/11 kV | Jayanagar | S6 | Bank -1 | ELITA PARAMONEDE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258691 | 800/1 | 7.5154 | 0
B.205 | BMASZ | South | 66/11 KV | Koramangala | S7 | Bank -1 | EMBASY TECH VILLAGE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18093018 | 2000/1 | 5.7466 | 0
B.206 | BMASZ | South | 66/11 KV | Koramangala | S7 | Bank -2 | EMBASY TECH VILLAGE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18093235 | 2000/1 | 0.063333 | 0
B.207 | BMASZ | South | 66/11 KV | Koramangala | S7 | Bank -3 | EMBASY TECH VILLAGE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18092917 | 2000/1 | 0.21333 | 0
B.208 | BMASZ | South | 66/11 KV | Koramangala | S7 | Bank -4 | EMBASY TECH VILLAGE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18093142 | 2000/1 | 10.2783 | 0
B.209 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK-1 | EPIP | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008001 | 1200/1 | 20.221 | 0
B.210 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK-1A | EPIP | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19004222 | 1200/1 | 13.93 | 0
B.211 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK-2 | EPIP | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008074 | 1200/1 | 21.363 | 0
B.212 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK-2A | EPIP | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16383200 | 1200/1 | 12.712 | 0
B.213 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK-3 | EPIP | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005533 | 1200/1 | 11.65 | 0
B.214 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK-3A | EPIP | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17000066 | 1200/1 | 9.731 | 0
B.215 | BMASZ | South | 66/11 kV | Koramangala | S17 | Bank -1 | EXORA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246579 | 2000/1 | 22.5484 | 0
B.216 | BMASZ | South | 66/11 kV | Koramangala | S17 | Bank -2 | EXORA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246613 | 1200/1 | 19.9336 | 0
B.217 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-1 | GANJIGUNTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246556 | 800/1 | 5.8318 | 0
B.218 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-2 | GANJIGUNTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246503 | 800/1 | 7.4222 | 0
B.219 | BMASZ | South | 66/11 kV | HSR | S11 | Bank -1 | Global Tech Park | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259308 | 1200/1 | 3.4163 | 0
B.220 | BMASZ | South | 66/11 kV | HSR | S11 | Bank -2 | Global Tech Park | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259143 | 1200/1 | 5.16 | 0
B.221 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | HAROHALLY | BANK-1 | GODUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167042 | 800/1 | 1.4698 | 0
B.222 | BMANZ | North | 66/11 kV | Jalahalli | C3 | Bank-1 | GOKULA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245887 | 1200/1 | 10.0834 | 0
B.223 | BMANZ | North | 66/11 kV | Jalahalli | C3 | Bank-2 | GOKULA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245927 | 1200/1 | 9.1696 | 0
B.224 | BMANZ | East | 66/11 kV | Indiranagar | E6 | BANK-1 | Golf Link Software Park | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246844 | 2000/1 | 10.9136 | 0
B.225 | BMANZ | East | 66/11 kV | Indiranagar | E6 | BANK-2 | Golf Link Software Park | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246561 | 2000/1 | 6.691 | 0
| BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | BANK-1 | GOWNIPALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20007727 | 800/1 | 3.549 | 0
| BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | BANK-2 | GOWNIPALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20007726 | 800/1 | 2.0226 | 0
B.226 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GOWRIBIDANUR | BANK-1 | GOWRIBIDANUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246248 | 1200/1 | 13.4779 | 0
B.227 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GOWRIBIDANUR | BANK-2 | GOWRIBIDANUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246241 | 1200/1 | 8.5429 | 0
B.228 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | KUDUR | BANK-1 | GUDEMARANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245176 | 1200/1 | 7.8452 | 0
B.229 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | KUDUR | BANK-2 | GUDEMARANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245970 | 1200/1 | 2.8871 | 0
B.230 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GUDIBANDE | BANK-1 | GUDIBANDE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246416 | 800/1 | 3.9455 | 0
B.231 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GUDIBANDE | BANK-2 | GUDIBANDE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247409 | 800/1 | 5.6454 | 0
B.232 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (R) | BANK-1 | GUNDAMGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246416 | 800/1 | 4.3801 | 0
B.233 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (R) | BANK-2 | GUNDAMGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247409 | 800/1 | 5.0798 | 0
B.234 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GUDIBANDE | BANK-1 | GUNDLU KOTTUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245246 | 600/1 | 3.1995 | 0
B.235 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GUDIBANDE | BANK-2 | GUNDLU KOTTUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245263 | 600/1 | 2.7253 | 0
B.236 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | SATHANURU | BANK-1 | GURUVINAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246274 | 600/1 | 4.3575 | 0
B.237 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-1 | H GOLLAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247432 | 600/1 | 3.0133 | 0
B.238 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-2 | H GOLLAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167045 | 800/1 | 5.0208 | 0
B.239 | BMANZ | East | 66/11 kV | Indiranagar | E6 | BANK-1 | HAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20000523 | 2000/1 | 17.8433 | 0
B.240 | BMANZ | East | 66/11 kV | Indiranagar | E6 | BANK-1A | HAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246678 | 2000/1 | 10.2234 | 0
B.241 | BMANZ | East | 66/11 kV | Indiranagar | E6 | BANK-2 | HAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009808 | 2000/1 | 21.0366 | 0
B.242 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | HAROHALLY | Bank-1 | HANUMANTANAGARA (Jain College) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245750 | 800/1 | 6.9822 | 0
B.243 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | HAROHALLY | Bank-1 | HANUMANTANAGARA (Jain College) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245750 | 800/1 | 0 | -0.00792
B.244 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | HAROHALLY | Bank-2 | HANUMANTANAGARA (Jain College) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245671 | 800/1 | 7.5286 | 0
B.245 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | SATHANURU | BANK-1 | HAROBELE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246203 | 600/1 | 3.7881 | 0
B.246 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | SATHANURU | BANK-2 | HAROBELE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245947 | 1200/1 | 3.0485 | 0
B.247 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | Bank - 1 | HBR Layout | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259341 | 1200/1 | 17.5859 | 0
B.248 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | Bank - 2 | HBR Layout | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259467 | 1200/1 | 11.3419 | 0
B.249 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | Bank - 3 | HBR Layout | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259386 | 1200/1 | 16.323 | 0
B.250 | BMANZ | North | 66/11 kV | Hebbal | C4 | Bank - 1 | HEBBAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259387 | 1200/1 | 17.8368 | 0
B.251 | BMANZ | North | 66/11 kV | Hebbal | C4 | Bank - 2 | HEBBAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259487 | 1200/1A | 20.5668 | 0
B.252 | BMANZ | North | 66/11 kV | Hebbal | C4 | Bank - 3 | HEBBAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259450 | 1200/1 | 17.7024 | 0
B.253 | BMANZ | North | 66/11 kV | Hebbal | C4 | Bank - 3A | HEBBAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259348 | 1200/1 | 10.188 | 0
B.254 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | BANK-1 | HEJJALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258500 | 800/1 | 10.7628 | 0
B.255 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | BANK-2 | HEJJALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258451 | 800/1 | 4.8506 | 0
B.256 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | Bank-1 | Hennur Road (Geddalahalli) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258899 | 2000-1200/1A | 22.731 | 0
B.257 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | Bank-2 | Hennur Road (Geddalahalli) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258909 | 2000-1200/1A | 23.2806 | 0
B.258 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | SATHANURU | BANK-1 | HONNAGANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245818 | 800/1 | 2.1123 | 0
B.259 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | SATHANURU | BANK-2 | HONNAGANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246146 | 800/1 | 3.978 | 0
B.260 | BMANZ | East | 66/11 kV | WhiteField | E12 | Bank -1 | HOODY 220KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246826 | 1200/1 | 15.153 | 0
B.261 | BMANZ | East | 66/11 kV | WhiteField | E12 | Bank -1A | HOODY 220KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246529 | 1200/1 | 11.8501 | 0
B.262 | BMANZ | East | 66/11 kV | WhiteField | E12 | Bank -2 | HOODY 220KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246757 | 1200/1 | 14.4271 | 0
B.263 | BMANZ | East | 66/11 kV | WhiteField | E12 | Bank -2A | HOODY 220KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247098 | 1200/1 | 7.9448 | 0
B.264 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | KUDUR | BANK-1 (MCVCB) | HOSAPALYA CIRCLE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094098 | 800-400/1-1-1A | 3.5605 | 0
B.265 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-1 | HOSKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246415 | 1200/1 | 9.158 | 0
B.266 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-2 | HOSKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247486 | 1200/1 | 14.2462 | 0
B.267 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-3 | HOSKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008046 | 1200/1 | 7.0488 | 0
B.268 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-4 | HOSKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20002615 | 1200/1 | 12.0838 | 0
B.269 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-5 | HOSKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247492 | 800/1 | 5.4857 | 0
B.270 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-6 | HOSKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247457 | 800/1 | 5.6977 | 0
B.271 | BRAZ | BANGALORE RURAL | 220/66/11 kV | HOSAKOTE | HOSAKOTE | BANK-1 | HOSKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247528 | 1200/1 | 13.1369 | 0
B.272 | BMASZ | South | 66/11 kV | HSR | S13 | Bank -1 | HSR LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479585 | 2000/1 | 14.2872 | 0
B.273 | BMASZ | South | 66/11 kV | HSR | S13 | Bank -1A | HSR LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479493 | 2000/1 | 20.2774 | 0
B.274 | BMASZ | South | 66/11 kV | HSR | S13 | Bank -2 | HSR LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479534 | 2000/1 | 16.8559 | 0
B.275 | BMASZ | South | 66/11 kV | HSR | S13 | Bank -2A | HSR LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479529 | 2000/1 | 10.2917 | 0
B.276 | BMASZ | South | 66/11 kV | HSR | S13 | Bank -3 | HSR LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479535 | 2000/1 | 18.7548 | 0
B.277 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR RURAL | BANK-1 | HUKUNDA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245722 | 400/1 | 1.6087 | 0
| BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR RURAL | BANK-2 | HUKUNDA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18135730 | 600/1 | 2.2862 | 0
B.278 | BRAZ | RAMANAGAR | 66/11 KV | CHANDAPURA | JIGANI | Bank - 1 | HULIMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18128549 | 800/1 | 6.3405 | 0
B.279 | BRAZ | RAMANAGAR | 66/11 KV | CHANDAPURA | JIGANI | Bank - 2 | HULIMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18128556 | 800/1 | 5.7727 | 0
B.280 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | KUDUR | BANK-1 | HULLENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245510 | 800-400/1-1-1A | 4.2518 | 0
B.281 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | KUDUR | BANK-2 | HULLENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q 0245363 | 800-400/1-1-1A | 4.0146 | 0
B.282 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA URBAN | BANK-1 | HUNASENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245755 | 600/1 | 0.8967 | 0
B.283 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA URBAN | BANK-1 | HUNASENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245755 | 600/1 | 0 | -0.54012
B.284 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA URBAN | BANK-2 | HUNASENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245917 | 400/1 | 1.0783 | 0
B.285 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA URBAN | BANK-2 | HUNASENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245917 | 400/1 | 0 | -0.31804
B.286 | BMANZ | North | 66/11 kV | Malleshwaram | C2 | Bank - 1 | I.I.SC. (TATA INSTITUTE) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245817 | 1200/1 | 12.2762 | 0
B.287 | BMANZ | North | 66/11 kV | Malleshwaram | C2 | Bank - 2 | I.I.SC. (TATA INSTITUTE) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245793 | 1200/1 | 17.7042 | 0
B.288 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | CHANNAPATNA RURAL | BANK-1 | IGGALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245442 | 400/1 | 1.6791 | 0
B.289 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | CHANNAPATNA RURAL | BANK-2 | IGGALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245596 | 400/1 | 2.8023 | 0
B.290 | BRAZ | RAMANAGAR | 66/11 KV | RAMANAGAR | CHANNAPATNA RURAL | BANK-2 | IGGALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245596 | 400/1 | 0 | -0.39556
B.291 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | CHANNAPATNA RURAL | BANK-3 | IGGALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245528 | 800/1 | 5.6762 | 0
B.292 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | CHANNAPATNA RURAL | BANK-3 | IGGALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245528 | 800/1 | 0 | 0
B.293 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI RURAL | BANK-1 | IRAGAMPALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 66/11 KV BANK-1 | 1200/1 | 5.7581 | 0
B.294 | BRAZ | KOLAR | 66/11 KV | CHINTHAMANI | CHINTHAMANI RURAL | BANK-1 | IRAGAMPALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 66/11 KV BANK-1 | 1200/1 | 0 | -0.17736
B.295 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI RURAL | BANK-2 | IRAGAMPALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 66/11 KV BANK-2 | 800/1 | 6.6606 | 0
B.296 | BMASZ | South | 66/11 kV | Jayanagar | S5 | Bank - 1 | ISKON | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258616 | 1600/1 | 9.3607 | 0
B.297 | BMASZ | South | 66/11 kV | Jayanagar | S5 | Bank - 2 | ISKON | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258623 | 1600/1 | 4.2912 | 0
B.298 | BMASZ | South | 66/11 kV | Jayanagar | S5 | Bank -1 | ISRO Layout | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258755 | 1200/1 | 14.5057 | 0
B.299 | BMASZ | South | 66/11 kV | Jayanagar | S5 | Bank -2 | ISRO Layout | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258756 | 1200/1 | 15.9826 | 0
B.300 | BMANZ | East | 66/11 kV | WhiteField | E7 | Bank - 1 | ITI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247286 | 2000/1 | 35.072 | 0
B.301 | BMANZ | East | 66/11 kV | WhiteField | E7 | Bank - 2 | ITI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247292 | 2000/1 | 34.5846 | 0
| BMANZ | East | 66/11 kV | WhiteField | E7 | Bank - 3 | ITI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18128533 | 2000/1 | 21.6249 | 0
B.302 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-1 | JADIGENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258462 | 1200-800/1A | 9.6622 | 0
B.303 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-2 | JADIGENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258447 | 1200-800/1A | 10.7676 | 0
B.304 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-2A | JADIGENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258385 | 1200-800/1A | 0 | 0
B.305 | BMASZ | South | 66/11 KV | HSR | S8 | Bank - 1 | Jakkasandra | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259135 | 1200/1 | 11.5849 | 0
B.306 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | RAMANAGARA RURAL | BANK-1 | JALAMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258413 | 400/1 | 1.434 | 0
B.307 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | RAMANAGARA RURAL | BANK-1 | JALAMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258413 | 400/1 | 0 | -0.01912
B.308 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-1 | JANGAMAKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247169 | 600/1 | 4.3661 | 0
B.309 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-2 | JANGAMAKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246451 | 600/1 | 5.4016 | 0
B.310 | BMASZ | South | 66/11 kV | Jayanagar | S1 | Bank -1 | JAYADEVA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479497 | 1200/1 | 18.7484 | 0
B.311 | BMASZ | South | 66/11 kV | Jayanagar | S1 | Bank -1A | JAYADEVA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479549 | 1200/1 | 11.4336 | 0
B.312 | BMASZ | South | 66/11 kV | Jayanagar | S1 | Bank -2 | JAYADEVA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479494 | 1200/1 | 10.5795 | 0
B.313 | BMASZ | South | 66/11 kV | Jayanagar | S1 | Bank -2A | JAYADEVA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479513 | 1200/1 | 15.2974 | 0
B.314 | BMASZ | South | 66/11 kV | Jayanagar | S1 | Bank - 1 | Jayanagar GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258945 | 2000/1A | 15.3246 | 0
B.315 | BMASZ | South | 66/11 kV | Jayanagar | S1 | Bank - 2 | Jayanagar GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258941 | 2000/1A | 14.0536 | 0
B.316 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | BANK-1 | JIGANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245844 | 1200/1 | 13.3597 | 0
B.317 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | BANK-2 | JIGANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245838 | 1200/1 | 23.1497 | 0
B.318 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | BANK-3 | JIGANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246166 | 1200/1 | 17.3161 | 0
B.319 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | BANK-1 | JIGANI LINK ROAD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246107 | 2000/1 | 24.2304 | 0
B.320 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | BANK-2 | JIGANI LINK ROAD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246068 | 2000/1 | 17.5552 | 0
B.321 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | BANK-1 | JIGANI(220kV) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246131 | 2000/1 | 31.3172 | 0
B.322 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | BANK-2 | JIGANI(220kV) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246155 | 2000/1 | 28.0838 | 0
B.323 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-1 | JULUPALYA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247453 | 1200/1A | 2.1968 | 0
B.324 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-2 | JULUPALYA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246280 | 800/1 | 3.521 | 0
B.325 | BMASZ | South | 66/11 kV | Koramangala | S3 | Bank - 1 | K & C VALLEY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20002613 | 1200/1 | 5.583 | 0
B.326 | BMASZ | South | 66/11 kV | Koramangala | S3 | Bank - 1A | K & C VALLEY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246939 | 1200/1 | 2.5171 | 0
B.327 | BMASZ | South | 66/11 kV | Koramangala | S3 | Bank - 2 | K & C VALLEY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20006033 | 1200/1 | 13.761 | 0
B.328 | BMASZ | South | 66/11 kV | Koramangala | S3 | Bank - 2A | K & C VALLEY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246978 | 1200/1 | 4.2157 | 0
B.329 | BMANZ | East | 66/11 kV | WhiteField | E4 | Bank - 1 | KACHAMARANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246728 | 1200/1 | 10.2895 | 0
B.330 | BMANZ | East | 66/11 kV | WhiteField | E4 | Bank - 2 | KACHAMARANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247226 | 1200/1 | 28.6619 | 0
B.331 | BMASZ | South | 66/11 kV | Koramangala | S17 | Bank - 1 | KADUBISENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20005933 | 2000/1 | 15.5116 | 0
B.332 | BMASZ | South | 66/11 kV | Koramangala | S17 | Bank - 2 | KADUBISENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20005926 | 2000/1 | 27.1166 | 0
B.333 | BMANZ | East | 66/11 kV | WhiteField | E4 | Bank - 1 | KADUGODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247261 | 1200/1 | 25.9741 | 0
B.334 | BMANZ | East | 66/11 kV | WhiteField | E4 | Bank - 1A | KADUGODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247347 | 1200/1 | 15.2533 | 0
B.335 | BMANZ | East | 66/11 kV | WhiteField | E4 | Bank - 2 | KADUGODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247216 | 1200/1 | 22.5961 | 0
B.336 | BMANZ | East | 66/11 kV | WhiteField | E4 | Bank -2A | KADUGODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247280 | 1200/1 | 8.9855 | 0
B.337 | BMASZ | South | 66/11 kV | Koramangala | S17 | Bank -1 | Kalyani Tech Park MUSS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167054 | 2000/1 | 0 | 0
B.338 | BMASZ | South | 66/11 kV | Koramangala | S17 | Bank -2 | Kalyani Tech Park MUSS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18053958 | 2000/1 | 6.216 | 0
B.339 | BRAZ | KOLAR | 66/11 kV | KGF | BANGARAPETE | BANK-1 | KAMASAMUDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247028 | 800/1 | 7.2875 | 0
B.340 | BRAZ | KOLAR | 66/11 kV | KGF | BANGARAPETE | BANK-2 | KAMASAMUDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246950 | 800/1 | 4.3498 | 0
B.341 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR_RA | BANK-1 | KANAKAPURA 66 KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246162 | 1200/1 | 11.0123 | 0
B.342 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR_RA | BANK-2 | KANAKAPURA 66 KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245677 | 1200/1 | 11.5441 | 0
B.343 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (R) | BANK-1 | KANASWADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245093 | 600/1 | 5.0843 | 0
B.344 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (R) | BANK-2 | KANASWADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245094 | 600/1 | 6.2802 | 0
B.345 | BMANZ | East | 66/11 kV | VidhanaSoudha | W4 | Bank - 1 | KANTEERAVA STADIUM | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258956 | 1200/1A | 11.7782 | 0
B.346 | BMANZ | East | 66/11 kV | VidhanaSoudha | W4 | Bank - 2 | KANTEERAVA STADIUM | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258960 | 1200/1A | 9.2652 | 0
B.347 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | Bank-I | KEMBODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247380 | 800/1 | 4.1644 | 0
B.348 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | Bank-I | KEMBODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247380 | 800/1 | 0 | -0.00352
B.349 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | Bank-2 | KEMBODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247345 | 800/1 | 5.1898 | 0
B.350 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | BANK-1 | KEMPANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258390 | 600/1 | 2.3226 | 0
B.351 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | BANK-2 | KEMPANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258390 | 600/1 | 7.0144 | 0
B.352 | BMASZ | West | 66/11 kV | Kengeri | K4 | Bank - 1 | Kengeri Satellite Town | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245552 | 1200/1 | 6.97 | 0
B.353 | BMASZ | West | 66/11 kV | Kengeri | K4 | Bank - 2 | Kengeri Satellite Town | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245555 | 1200/1 | 12.2042 | 0
B.354 | BRAZ | KOLAR | 66/11 kV | KGF | KGF | BANK-1 | KGF | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246937 | 800/1 | 4.3935 | 0
B.355 | BRAZ | KOLAR | 66/11 kV | KGF | KGF | BANK-2 | KGF | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247061 | 800/1 | 6.549 | 0
B.356 | BRAZ | KOLAR | 66/11 kV | KGF | KGF | BANK-3 | KGF | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246886 | 800/1 | 5.6946 | 0
B.357 | BRAZ | KOLAR | 66/11 kV | KGF | KGF | BANK-4 | KGF | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247070 | 800/1 | 1.9281 | 0
B.358 | BMANZ | North | 66/11 kV | Hebbal | C7 | Bank-1 | KHB Colony (Yelahanka) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259766 | 1200/1 | 10.3234 | 0
B.359 | BMANZ | North | 66/11 kV | Hebbal | C7 | Bank-2 | KHB Colony (Yelahanka) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259456 | 1200/1 | 13.7005 | 0
B.360 | BMASZ | South | 66/11 kV | HSR | S12 | BANK-1 | KHODAY'S GLASS FACTORY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258700 | 1200/1 | 9.0998 | 0
B.361 | BMASZ | South | 66/11 kV | HSR | S12 | BANK-2 | KHODAY'S GLASS FACTORY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258701 | 1200/1 | 11.5505 | 0
B.362 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | AVALAHALLI | BANK-1 | KOANDASPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258562 | 1200/1 | 27.3585 | 0
B.363 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | AVALAHALLI | BANK-2 | KOANDASPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258392 | 1200/1 | 26.0555 | 0
B.364 | BMASZ | West | 66/11 kV | Kengeri | K4 | BANK-1 | KODIGEHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245517 | 1200/1-1-1A | 20.0567 | 0
B.365 | BMASZ | West | 66/11 kV | Kengeri | K4 | BANK-2 | KODIGEHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245581 | 1200/1-1-1A | 15.1895 | 0
B.366 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR RURAL | BANK-1 | KODIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245827 | 600/1 | 3.8233 | 0
B.367 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR RURAL | BANK-1 | KODIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245827 | 600/1 | 0 | -0.00464
B.368 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR RURAL | BANK-2 | KODIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245710 | 600/1 | 3.3677 | 0
| BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR RURAL | BANK-2 | KODIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245710 | 600/1 | 0 | -8e-05
B.369 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR RURAL | BANK-1 | KODIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245827 | 600/1 | 3.3868 | 0
B.370 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR RURAL | BANK-2 | KODIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245710 | 600/1 | 3.1133 | 0
B.371 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR URBAN | BANK-1 | KOLAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247144 | 1200/1 | 16.8334 | 0
B.372 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR URBAN | BANK-2 | KOLAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246701 | 1200/1 | 17.7605 | 0
B.373 | BMASZ | South | 66/11 kV | Koramangala | S4 | Bank - 1 | KORAMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | XD435002 | 2000/1 | 14.7259 | 0
B.374 | BMASZ | South | 66/11 kV | Koramangala | S4 | Bank - 2 | KORAMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | XD434649 | 2000/1 | 17.2012 | 0
| BMASZ | South | 66/11 kV | Koramangala | S4 | Bank - 3 | KORAMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | X1499066 | 2000/1 | 1.1117 | 0
| BRAZ | RAMANAGAR | 220/66/11kV | RAMANAGAR | RAMANAGARA URBAN | Bank - 1 | Kothipura | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17151014 | 800/1 | 6.2046 | 0
B.375 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | KUDUR | BANK-1 | KUDUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18027825 | 1200/1 | 0 | 0
B.376 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | KUDUR | BANK-2 | KUDUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094122 | 800/1 | 0 | 0
B.377 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | KUDUR | Bank - 1(MCVCB) | KUDUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18027825 | 1200/1-1-1A | 5.7373 | 0
B.378 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | KUDUR | Bank - 2(MCVCB) | KUDUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094122 | 800/1-1-1A | 5.1251 | 0
| BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | Bank -1 | KUMBARANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19007944 | 800/1 | 13.447 | 0
| BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | JIGANI | Bank -2 | KUMBARANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19007905 | 400/1 | 3.0485 | 0
B.379 | BMASZ | West | 66/11 kV | Kengeri | K1 | Bank -1 | KUMBALAGODU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258781 | 1200 /1A | 27.1424 | 0
B.380 | BMASZ | West | 66/11 kV | Kengeri | K1 | Bank -2 | KUMBALAGODU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258773 | 2000/1 | 16.7816 | 0
B.381 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | BANK-1 | KUNDANA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245377 | 800/1 | 7.3062 | 0
B.382 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | BANK-2 | KUNDANA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245079 | 800/1 | 8.0492 | 0
| BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | KANAKAPUR URBAN | Bank -1 | KUNNUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009820 | 800/1 | 2.4234 | 0
B.383 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | RAMANAGARA RURAL | Bank-1 | KUTAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258431 | 400/1 | 3.1447 | 0
B.384 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-1 | KYALANUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246997 | 600/1 | 5.3707 | 0
B.385 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-2 | KYALANUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246549 | 600/1 | 5.2755 | 0
B.386 | BRAZ | KOLAR | 66/11 kV | KGF | BETHAMANGLA | BANK-1 | KYASAMBALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246914 | 800/1 | 3.709 | 0
B.387 | BRAZ | KOLAR | 66/11 kV | KGF | BETHAMANGLA | BANK-2 | KYASAMBALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246600 | 800/1 | 3.0622 | 0
B.388 | BRAZ | KOLAR | 66/11 kV | KGF | BETHAMANGLA | BANK-3 | KYASAMBALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247072 | 800/1 | 4.12 | 0
B.389 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-1 | LAKKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246903 | 800/1 | 5.0327 | 0
B.390 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-2 | LAKKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247056 | 800/1 | 10.4189 | 0
B.391 | BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | BANK -1 | LAKSHMIPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247125 | 800/1 | 5.3218 | 0
B.392 | BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | BANK-2 | LAKSHMIPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0249847 | 800/1 | 4.5631 | 0
B.393 | BMANZ | East | 66/11 kV | Indiranagar | E6 | Bank - 1 | LEELA VENTURE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246667 | 1200/1 | 17.124 | 0
B.394 | BMANZ | East | 66/11 kV | Indiranagar | E6 | Bank - 2 | LEELA VENTURE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247075 | 1200/1 | 12.5124 | 0
B.395 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-1 | M.GOLLAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246574 | 400/1 | 6.0027 | 0
B.396 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-2 | M.GOLLAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246527 | 800/1 | 2.139 | 0
B.397 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | MAGADI | BANK-1 | MAGADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246022 | 1200/1-1-1A | 7.1614 | 0
B.398 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | MAGADI | BANK-2 | MAGADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245495 | 1200/1-1-1A | 6.1222 | 0
B.399 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | MAGADI | Bank-1 | MAGADI 220/66/11kV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246023 | 1200/1-1-1A | 1.784 | 0
B.400 | BMASZ | West | 66/11 kV | Rajajinagar | N1 | Bank-1 | MAHALAXMI LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245742 | 2000/1 | 18.8478 | 0
B.401 | BMASZ | West | 66/11 kV | Rajajinagar | N1 | Bank-2 | MAHALAXMI LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245785 | 1200/1 | 11.3639 | 0
B.402 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-1 | MALLANAYAKANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247364 | CT- 600/1-1-1A | 3.6624 | 0
| BRAZ | KOLAR |  | KGF | MULABAGILU | BANK-2 | MALLANAYAKANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0480380 | 800/1 | 0.2961 | 0
| CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | Bank-1 | MALLAPPANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19004903 | 400/1 | 1.6124 | 0
| CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | Bank-2 | MALLAPPANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005590 | 400/1 | 0 | -2.051
B.403 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-1 | MALLASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252661 | 800/1 | 4.227 | 0
B.404 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-2 | MALLASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252944 | 800/1 | 4.4228 | 0
B.405 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-1 | MALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18093015 | 800/1 | 6.591 | 0
B.406 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-1A | MALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246946 | 1200/1 | 9.8767 | 0
B.407 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-2 | MALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18053996 | 800/1 | 7.437 | 0
B.408 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-3 | MALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247000 | 800-400/1-1-1A | 8.9834 | 0
B.409 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-1 | MALUR INDUSTRIAL AREA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247008 | 1200/1-1-1A | 9.0521 | 0
B.410 | BRAZ | KOLAR | 66/11 KV | KGF | MALUR | BANK-1A | MALUR INDUSTRIAL AREA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18092713 | 1200/1 | 14.028 | 0
B.411 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-2 | MALUR INDUSTRIAL AREA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247017 | 1200/1-1-1A | 13.0009 | 0
B.412 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GOWRIBIDANUR | BANK-1 | MANCHENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246339 | 800/1 | 7.2786 | 0
B.413 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GOWRIBIDANUR | BANK-2 | MANCHENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246281 | 800/1 | 7.407 | 0
B.414 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | BANK-1 | MANDIKAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO247450 | 1200/1 | 5.5359 | 0
B.415 | BMANZ | North | 220/66/11 KV | Hebbal | C8 | Bank - 1 | Manyatha GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17125516 | 2000/1 | 2.844 | 0
B.416 | BMANZ | North | 220/66/11 KV | Hebbal | C8 | Bank - 2 | Manyatha GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17125529 | 2000/1 | 7.56 | 0
B.417 | BMANZ | North | 220/66/11 KV | Hebbal | C8 | Bank - 3 | Manyatha GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17125489 | 2000/1 | 11.378 | 0
B.418 | BMANZ | North | 220/66/11 KV | Hebbal | C8 | Bank - 4 | Manyatha GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17125492 | 2000/1 | 12.802 | 0
B.419 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | BANK-1 | MANYATHA TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259473 | 1200/1 | 9.6198 | 0
B.420 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | BANK-2 | MANYATHA TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259482 | 1200/1 | 24.6499 | 0
B.421 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | BANK-3 | MANYATHA TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17125521 | 1200/1 | 12.0564 | 0
B.422 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | HAROHALLY | BANK-1 | MARALAWADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245764 | 800/1 | 5.5432 | 0
B.423 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | HAROHALLY | BANK-2 | MARALAWADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245743 | 800/1 | 4.4648 | 0
B.424 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-1 | MASTI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246830 | 1200/1 | 10.6014 | 0
B.425 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-1A | MASTI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246821 | 1200/1 | 0.66528 | 0
B.426 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-2 | MASTI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246970 | 1200/1 | 16.7834 | 0
B.427 | BMANZ | North | 11 kV | Malleshwaram | C6 | BANK-1 | MATHIKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246191 | 1200/1 | 10.9428 | 0
B.428 | BMANZ | North | 11 kV | Malleshwaram | C6 | BANK-2 | MATHIKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245746 | 1200/1 | 13.0246 | 0
B.429 | BMANZ | North | 66/11 kV | Malleshwaram | C6 | Bank-1 | MATHIKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246191 | 1200/1 | 1.6054 | 0
B.430 | BMANZ | North | 11 kV | Peenya | N5 | BANK-1 | MEI Layout | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245167 | 1200/1 | 11.6602 | 0
B.431 | BMANZ | North | 11 kV | Peenya | N5 | BANK-2 | MEI Layout | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245225 | 1200/1 | 12.6781 | 0
B.432 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | RAMANAGARA RURAL | BANK-1 | MELEHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258497 | 600/1 | 2.4834 | 0
B.433 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | RAMANAGARA RURAL | BANK-2 | MELEHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258524 | 600/1 | 3.2726 | 0
B.434 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-1 | MELUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246574 | 600/1-1-1A | 2.3774 | 0
B.435 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-2 | MELUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246527 | 600/1-1-1A | 3.8124 | 0
B.436 | BRAZ | KOLAR | 66/11 KV | CHIKKABALLAPURA | BAGEPALLI | BANK-1 | MITTEMARI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17125664 | 800/1 | 3.419 | 0
B.437 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-1 | MUDIYANUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18053959 | 600/1 | 3.3876 | 0
B.438 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-2 | MUDIYANUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247166 | 600/1 | 3.2748 | 0
B.439 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-1 | MULABAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246736 | 1200/1 | 8.7259 | 0
B.440 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-2 | MULABAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247341 | CT = 800/1 & PT= 11kv/110v-110v | 7.6843 | 0
B.441 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-3 | MULABAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247187 | CT = 800/1 & PT= 11kv/110v-110v | 10.1733 | 0
B.442 | BMASZ | South | 66/11 kV | HSR | S13 | Bank - 1 | NAGANATHAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259176 | 2000/1A | 32.3558 | 0
B.443 | BMASZ | South | 66/11 kV | HSR | S13 | Bank - 2 | NAGANATHAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259028 | 2000/1A | 22.1234 | 0
B.444 | BMASZ | South | 66/11 kV | HSR | S13 | Bank - 3 | NAGANATHAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17166992 | 1200/1A | 25.665 | 0
B.445 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | BANK-1 | NALLIMARADANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245092 | 1200/1 | 7.2432 | 0
B.446 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | BANK-2 | NALLIMARADANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245258 | 1200/1 | 9.5736 | 0
B.447 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | NANDAGUDI | BANK-1 | NANDAGUDI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247488 | 1200/1 | 8.0051 | 0
B.448 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | NANDAGUDI | BANK-2 | NANDAGUDI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247508 | 800/1 | 7.8894 | 0
B.449 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI URBAN | BANK-1 | NANDIGANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246606 | 800/1 | 3.6874 | 0
B.450 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI URBAN | BANK-1 | NANDIGANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246606 | 800/1 | 0 | -0.0012
B.451 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI URBAN | BANK-2 | NANDIGANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246504 | 800/1 | 4.5636 | 0
B.452 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI URBAN | BANK-2 | NANDIGANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246504 | 800/1 | 0 | -0.01444
B.453 | BMANZ | North | 66/11 kV | Malleshwaram | C1 | Bank - 1 | NANDINI LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245984 | 1200/1A | 16.3602 | 0
B.454 | BMANZ | North | 66/11 kV | Malleshwaram | C1 | Bank - 2 | NANDINI LAYOUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245471 | 2000/1 | 24.9942 | 0
B.455 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-1 | NANGLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246447 | 600/1 | 5.4832 | 0
B.456 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-2 | NANGLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246497 | 1200/1 | 10.233 | 0
B.457 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-1 | NARASAPUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247228 | 1200/1A | 11.9504 | 0
B.458 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-2 | NARASAPUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247113 | 800/1A | 5.8842 | 0
B.459 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-3 | NARASAPUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247295 | 1200/1A | 14.0278 | 0
| BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-4 | NARASAPUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246871 | 800/1A | 6.4695 | 0
B.460 | BMASZ | West | 66/11 kV | RRNagar | W2 | Bank - 1 | National College GIS Station | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258929 | 2000/1 | 12.841 | 0
B.461 | BMASZ | West | 66/11 kV | RRNagar | W2 | Bank - 2 | National College GIS Station | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258912 | 2000/1 | 16.402 | 0
B.462 | BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 1 | NELAKADARANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20009643 | 2000/1 | 18.4867 | 0
B.463 | BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 2 | NELAKADARANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20009623 | 2000/1 | 23.53 | 0
B.464 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | NELAMANGALA | BANK-1 | NELAMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245050 | 1200-800/1-1-1A | 25.2851 | 0
B.465 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | NELAMANGALA | BANK-2 | NELAMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245344 | 1200-800/1-1-1A | 16.785 | 0
B.466 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | NELAMANGALA | BANK-3 | NELAMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245336 | 1200-800/1-1-1A | 19.1218 | 0
B.467 | BRAZ | KOLAR | 66/11 kV | KGF | BETHAMANGLA | BANK-1 | NG HULKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259073 | 1200-800/1-1-1A | 4.172 | 0
| BRAZ | KOLAR | 66/11 kV | KGF | BETHAMANGLA | BANK-1 | NG HULKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259073 | 1200-800/1-1-1A | 0 | -0.01112
B.468 | BRAZ | KOLAR | 66/11 kV | KGF | BETHAMANGLA | BANK-2 | NG HULKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259257 | 1200-800/1-1-1A | 2.6513 | 0
B.469 | BRAZ | KOLAR | 66/11 kV | KGF | BETHAMANGLA | BANK-2 | NG HULKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259257 | 1200-800/1-1-1A | 0 | -0.48304
B.470 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 1 | NGEF | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 13196187 | 200/1 | 13.733 | 0
B.471 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank -1 A | NGEF | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246697 | 1200/1 | 9.34 | 0
B.472 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank - 2 | NGEF | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246927 | 1200/1 | 13.5781 | 0
B.473 | BMANZ | East | 66/11 kV | Indiranagar | E3 | Bank -2 A | NGEF | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247384 | 1200/1 | 14.045 | 0
B.474 | BMASZ | South | 66/11 kV | Jayanagar | S1 | BANK1 | NIMHANS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246759 | 1200/1A | 19.2254 | 0
B.475 | BMASZ | South | 66/11 kV | Jayanagar | S1 | BANK 2 | NIMHANS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247293 | 1200/1A | 8.2872 | 0
B.476 | BMANZ | East | 66/11 kV | VidhanaSoudha | W3 | Bank - 1 | NRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KAU09496 | 1200/1 | 12.309 | 0
B.477 | BMANZ | East | 66/11 kV | VidhanaSoudha | W3 | Bank - 2 | NRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KEB 16544 | 1200/1 | 13.2434 | 0
B.478 | BMANZ | East | 66/11 kV | VidhanaSoudha | W3 | Bank - 3 | NRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KEB-16543 | 1200/1 | 8.8686 | 0
B.479 | BMANZ | East | 66/11 kV | VidhanaSoudha | W3 | Bank - 4 | NRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KEB-16542 | 1200/1 | 10.6384 | 0
B.480 | BMANZ | East | 66/11 kV | VidhanaSoudha | W3 | Bank - 5 | NRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KEB17049 | 1200/1 | 13.2766 | 0
B.481 | BMANZ | East | 66/11 kV | VidhanaSoudha | W3 | Bank - 5A | NRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KAU0887 | 2000/1 | 13.4818 | 0
B.482 | BMASZ | South | 66/11 kV | Jayanagar | S9 | BANK 1 | PADMANABHANAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258792 | 2000/1 | 22.1378 | 0
B.483 | BMASZ | South | 66/11 kV | Jayanagar | S9 | BANK 1A | PADMANABHANAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258783 | 2000/1 | 6.5188 | 0
B.484 | BMASZ | South | 66/11 kV | Jayanagar | S9 | BANK 2 | PADMANABHANAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258793 | 12000/1 | 14.0658 | 0
B.485 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-1 | PALCHERLU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259269 | 600/1 | 4.6247 | 0
B.486 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-1 | PATHAPALYA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247462 | 800/1 | 4.423 | 0
B.487 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | BANK-1 | PERESANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247435 | 1200/1 | 9.5296 | 0
B.488 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | BANK-2 | PERESANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246294 | 800/1 | 8.6306 | 0
B.489 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-1 | PILLAGUPPA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247517 | 1200/1 | 22.2488 | 0
B.490 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-2 | PILLAGUPPA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247531 | 1200/1 | 20.4455 | 0
B.491 | BMANZ | North | 66/11 kV | Peenya | N5 | Bank - 1 | PLATINUM CITY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 2002935 | 2000/1 | 0 | 0
B.492 | BMANZ | North | 66/11 kV | Peenya | N5 | Bank - 2 | PLATINUM CITY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005600 | 2000/1 | 13.0933 | 0
B.493 | BMANZ | East | 66/11 kV | Shivajinagar | E5 | Bank - 1 | POTTERY ROAD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258827 | 1200/1 | 23.5842 | 0
B.494 | BMANZ | East | 66/11 kV | Shivajinagar | E5 | Bank - 2 | POTTERY ROAD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258883 | 1200/1 | 18.5723 | 0
B.495 | BMANZ | East | 66/11 kV | Shivajinagar | E5 | Bank - 2A | POTTERY ROAD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258862 | 1200/1 | 8.5721 | 0
B.496 | BMANZ | East | 66/11 kV | WhiteField | E12 | Bank -1 | PRESTIGE SHANTHINIKETHAN | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247282 | 2000/1 | 29.4864 | 0
B.497 | BMANZ | East | 66/11 kV | WhiteField | E12 | Bank -2 | PRESTIGE SHANTHINIKETHAN | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247278 | 2000/1 | 19.4146 | 0
B.498 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK 1 | PRIMAL TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259308 | 2000/1 | 17.1908 | 0
B.499 | BMASZ | South | 66/11 kV | Koramangala | S7 | BANK 2 | PRIMAL TECH PARK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259143 | 2000/1 | 14.105 | 0
B.500 | BMASZ | West | 66/11 kV | Kengeri | K1 | BANK 1 | PROVIDENT HOUSING | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258768 | 1200/1 | 0 | 0
B.501 | BMANZ | East | 66/11 KV | Shivajinagar | E8 | BANK-1 | PURVANKARA PALM BEACH | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19000006 | 200/1 | 0.89617 | 0
B.502 | BMANZ | East | 66/11 KV | Shivajinagar | E8 | Bank-2 | PURVANKARA PALM BEACH | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19001112 | 1200/1 | 0.001 | 0
B.503 | BMANZ | North | 66/11 kV | Hebbal | C7 | Bank - 1 | Puttenahalli YELAHANKA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259431 | 2000/1 | 26.7296 | 0
B.504 | BMANZ | North | 66/11 kV | Hebbal | C7 | Bank - 2 | Puttenahalli YELAHANKA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259398 | 2000/1 | 21.5128 | 0
B.505 | BMASZ | South | 66/11 kV | Jayanagar | S6 | Bank -1 | R.B.I. | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258806 | 1200/1 | 19.13 | 0
B.506 | BMASZ | South | 66/11 kV | Jayanagar | S6 | Bank - 2 | R.B.I. | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258807 | 1200/1 | 16.9901 | 0
B.507 | BMANZ | North | 66/11 kV | Malleshwaram | C6 | Bank - 1 | R.M.V. | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245283 | 2000/1 | 15.826 | 0
| BMANZ | North | 66/11 kV | Malleshwaram | C6 | Bank - 2 | R.M.V. | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245530 | 1200/1 | 23.872 | 0
| BMANZ | North | 66/11 kV | Malleshwaram | C6 | Bank - 2 | R.M.V. | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245530 | 1200/1 | 0 | 0
B.508 | [16 empty] | 0 | 0
B.509 | BMASZ | West | 66/11 kV | RRNagar | W7 | Bank -1 | R.R. NAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19004913 | 1200/1 | 25.293 | 0
B.510 | BMASZ | West | 66/11 kV | RRNagar | W7 | Bank - 2 | R.R. NAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19004140 | 1200/1 | 22.491 | 0
B.511 | BMASZ | West | 66/11 kV | RRNagar | W7 | Bank - 2A | R.R. NAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258824 | 1200/1 A | 2.7155 | 0
B.512 | BMANZ | North | 66/11 kV | Hebbal | C7 | Bank - 1 | RAJANAKUNTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0603595 | 1200/1 | 10.6358 | 0
B.513 | BMANZ | North | 66/11 kV | Hebbal | C7 | Bank - 2 | RAJANAKUNTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258621 | 1200/1 | 11.711 | 0
B.514 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | RAMANAGARA_RA | BANK-1 | RAMANAGARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258377 | 800/1 | 7.692 | 0
B.515 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | RAMANAGARA_RA | BANK-2 | RAMANAGARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258456 | 1200/1 | 11.3764 | 0
B.516 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | Bank-1 | RAMAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247415 | 800/1 | 2.6286 | 0
B.517 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | Bank-2 | RAMAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246342 | 400/1 | 4.8561 | 0
| BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | Bank-1 | Rayalpad | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20002631 | 800/1 | 0.1025 | 0
| BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | Bank-2 | Rayalpad | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20007750 | 800/1 | 2.5418 | 0
B.518 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | HAROHALLY | BANK-1 | RANGANADODDI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245915 | 1200/1 | 25.9836 | 0
B.519 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | HAROHALLY | BANK-2 | RANGANADODDI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245916 | 1200/1 | 16.5756 | 0
B.520 | BMANZ | West | 66/11 kV | RRNagar | W6 | Bank - 1 | REMCO GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259434 | 2000/1A | 17.5984 | 0
B.521 | BMANZ | West | 66/11 kV | RRNagar | W6 | Bank - 2 | REMCO GIS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259434 | 2000/1A | 25.6704 | 0
| BMANZ | North | 66/11 kV | Hebbal | C4 | Bank -1 | RMZ | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17031037 | 2000/1 | 9.5466 | 0
B.523 | BMANZ | North | 66/11 kV | Hebbal | C4 | Bank -2 | RMZ | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17031093 | 2000/1 | 9.435 | 0
B.524 | BMANZ | North | 66/11 kV | Hebbal | C4 | Bank -3 | RMZ | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17031106 | 2000/1 | 7.4783 | 0
B.525 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-1 | S M MANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247253 | 800/1 | 4.4557 | 0
B.526 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-2 | S M MANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247357 | 800/1 | 3.6979 | 0
B.527 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-1 | SADALI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18092704 | 400-800/1-1-1 | 2.5255 | 0
B.528 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | BANK-2 | SADALI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246540 | 300-600/1 | 2.702 | 0
B.529 | BMANZ | North | 66/11 kV | Jalahalli | C9 | Bank-1 | SAHAKARINAGARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259392 | 1200/1 | 22.5556 | 0
B.530 | BMANZ | North | 66/11 kV | Jalahalli | C9 | Bank-2 | SAHAKARINAGARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259461 | 1200/1 | 22.8608 | 0
B.531 | BMANZ | North | 66/11 kV | Jalahalli | C9 | Bank-3 | SAHAKARINAGARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259413 | 1200/1 | 14.2415 | 0
B.532 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | CHANNAPATNA URBAN | Bank - 1 | SANKALAGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245592 | 600/1 | 4.6815 | 0
| BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ANEKAL | Bank-1 | SAMANDURU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 15192680 | 600/1 | 2.5426 | 0
| BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ANEKAL | Bank-2 | SAMANDURU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 15192661 | 600/1 | 2.36 | 0
B.533 | BMASZ | South | 66/11 kV | JAYANAGAR | S14 | Bank -1 | SARAKKI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259018 | 1200/1 | 3.6918 | 0
B.534 | BMASZ | South | 66/11 kV | JAYANAGAR | S14 | Bank -1A | SARAKKI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259302 | 1200/1 | 14.8308 | 0
B.535 | BMASZ | South | 66/11 kV | JAYANAGAR | S14 | Bank - 2 | SARAKKI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259280 | 1200/1 | 0 | 0
B.536 | BMASZ | South | 66/11 kV | JAYANAGAR | S14 | Bank - 2A | SARAKKI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259094 | 1200/1 | 15.6286 | 0
B.537 | BMASZ | South | 66/11 kV | JAYANAGAR | S14 | Bank - 3 | SARAKKI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259034 | 1200/1 | 13.5245 | 0
B.538 | BMASZ | South | 66/11 kV | JAYANAGAR | S14 | Bank - 3A | SARAKKI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259309 | 1200/1 | 8.9329 | 0
B.539 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ATTIBELE | BANK-1 | SARJAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245425 | 1200/1 | 8.7137 | 0
B.540 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | ATTIBELE | BANK-2 | SARJAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245857 | 1200/1 | 14.5848 | 0
B.541 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | Bank -1 | SAUDELA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167050 | 1200/1 | 14.893 | 0
B.542 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA RURAL | Bank - 2 | SAUDELA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167049 | 1200/1 | 9.98 | 0
B.543 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | RAMANAGARA RURAL | BANK-1 | SHIVANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258533 | 400/1 | 2.9832 | 0
B.544 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | RAMANAGARA RURAL | BANK-2 | SHIVANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16093984 | 800/1 | 1.6944 | 0
B.545 | BMASZ | South | 66/11 kV | HSR | S11 | Bank -1 | SHOBHA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259243 | 2000/1 | 13.7984 | 0
B.546 | BMASZ | South | 66/11 kV | HSR | S11 | Bank -1A | SHOBHA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259250 | 2000/1 | 10.7436 | 0
B.547 | BMASZ | South | 66/11 kV | HSR | S11 | Bank -2 | SHOBHA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259126 | 2000/1 | 10.146 | 0
| BMANZ | East | 66/11 kV | VidhanaSoudha | W3 | Bank -1 | Shobha Indraprastha | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 11489134 | 1200/1 | 5.36 | 0
| BMANZ | East | 66/11 kV | VidhanaSoudha | W3 | Bank -2 | Shobha Indraprastha | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19004886 | 1200/1 | 1.319 | 0
B.548 | BMANZ | East | 66/11 KV | Shivajinagar | E9 | BANK-1 | SHOBHA CITY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259243 | 2000/1 | 12.507 | 0
B.549 | BMANZ | East | 66/11 KV | Shivajinagar | E9 | Bank-2 | SHOBHA CITY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259126 | 2000/1 | 15.083 | 0
B.550 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA_RA | BANK-1 | SIDDLAGHATTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259064 | 1200/1 | 9.8794 | 0
B.551 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA_RA | BANK-2 | SIDDLAGHATTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259241 | 1200/1 | 13.383 | 0
B.552 | BMASZ | West | 66/11 kV | Kengeri | K4 | Bank-1 | Sir.M.V.Layout | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245998 | 1200/1 | 20.8738 | 0
B.553 | BMASZ | West | 66/11 kV | Kengeri | K4 | Bank-2 | Sir.M.V.Layout | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245998 | 2000/1 | 22.7181 | 0
B.554 | BMASZ | South | 66/11 kV | HSR | S12 | Bank - 1 | Sobha Forest View | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 11489134 | 50/5 | 2.3282 | 0
B.555 | BMANZ | North | 66/11 kV | Jalahalli | N9 | Bank - 1 | SOLADEVANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246052 | 1200/1A | 15.005 | 0
B.556 | BMANZ | North | 66/11 kV | Jalahalli | N9 | Bank - 1 | SOLADEVANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246052 | 1200/1A | 0 | 0
B.557 | BMANZ | North | 66/11 kV | Jalahalli | N9 | Bank - 2 | SOLADEVANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246084 | 1200/1A | 11.716 | 0
B.558 | BMASZ | West | 66/11 kV | Kengeri | K3 | Bank -1 | SOMANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20009668 | 1200/1 | 6.142 | 0
B.559 | BMASZ | West | 66/11 kV | Kengeri | K3 | Bank - 2 | SOMANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20009756 | 800/1 | 8.7158 | 0
B.560 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-1 | SOMANATHPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246365 | 600/1 | 5.8723 | 0
B.561 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-2 | SOMANATHPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246368 | 600/1 | 4.2646 | 0
B.562 | BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | Bank-1 | SOMAYAJANAPALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247119 | 600/1 | 3.6471 | 0
B.563 | BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | Bank-2 | SOMAYAJANAPALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246773 | 600/1 | 3.219 | 0
B.564 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GUDIBANDE | BANK-1 | SOMENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247420 | 800/1 | 6.525 | 0
B.565 | BMASZ | South | 66/11 kV | HSR | S12 | Bank -1 | SOUTH CITY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258676 | 1200/1 | 14.5189 | 0
B.566 | BMASZ | South | 66/11 kV | HSR | S12 | Bank -2 | SOUTH CITY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258675 | 1200/1 | 23.0374 | 0
B.567 | BMASZ | South | 66/11 KV | HSR | S12 | Bank -2A | SOUTH CITY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18053986 | 1200/1 A | 0.415 | 0
B.568 | BMASZ | West | 66/11 kV | Rajajinagar | N6 | Bank - 1 | SRIGANDHA KAVAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245810 | 1200/1 | 11.4066 | 0
B.569 | BMASZ | West | 66/11 kV | Rajajinagar | N6 | Bank - 2 | SRIGANDHA KAVAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245676 | 1200/1 | 14.6545 | 0
B.570 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-1 (PCVCB) | SRIGIRIPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16093991 | 800/1-1-1A | 2.5518 | 0
B.571 | BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | BANK-1 | SRINIVASAPUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247162 | 1200/1 | 11.6288 | 0
B.572 | BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | BANK-2 | SRINIVASAPUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247138 | 1200/1 | 7.6675 | 0
B.573 | BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 1 | SRS PEENYA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245183 | 1200/1 | 24.1516 | 0
B.574 | BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 2 | SRS PEENYA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479583 | 1200/1 | 18.2154 | 0
B.575 | BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 3 | SRS PEENYA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245178 | 1200/1 | 15.5806 | 0
B.576 | BMANZ | North | 66/11 kV | Peenya | N4 | Bank - 4 | SRS PEENYA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245327 | 2000/1 | 34.5068 | 0
B.577 | BMASZ | South | 66/11 kV | Koramangala | S16 | Bank -1 | ST. JOHNS HOOD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259291 | 1200/1 | 18.2678 | 0
B.578 | BMASZ | South | 66/11 kV | Koramangala | S16 | Bank -2 | ST. JOHNS HOOD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259031 | 1200/1 | 17.7667 | 0
B.579 | BMASZ | South | 66/11 kV | Jayanagar | S18 | Bank -1 | SUBRAMANYAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258600 | 1200/1 | 17.9252 | 0
B.580 | BMASZ | South | 66/11 kV | Jayanagar | S18 | Bank -2 | SUBRAMANYAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258603 | 1200/1 | 10.139 | 0
B.581 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-1 | SUGATUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246785 | 400/1 | 2.5168 | 0
B.582 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-1 | SUGATUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246785 | 400/1 | 0 | 0
B.583 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-2 | SUGATUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247378 | 400/1 | 2.424 | 0
B.584 | BRAZ | KOLAR | 66/11 KV | KOLAR | KOLAR RURAL | BANK-2 | SUGATUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247378 | 400/1 | 0 | -0.01584
B.585 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-2 | SUGATUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247378 | 400/1 | 0 | 0
B.586 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | NANDAGUDI | BANK-1 | SULIBELE(66KV ) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246251 | 600/1 | 7.2358 | 0
B.587 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | NANDAGUDI | BANK-2 | SULIBELE(66KV ) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246308 | 800/1 | 5.0494 | 0
B.588 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | CHANDAPURA | BANK-1 | SURYANAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q.0245564 | 1200/1 | 8.0537 | 0
B.589 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | NELAMANGALA | Bank - 1 | T.BEGUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245532 | 1200/1-1-1A | 20.3592 | 0
B.590 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | NELAMANGALA | Bank - 2 | T.BEGUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245203 | 1200/1-1-1A | 13.7621 | 0
| BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | Bank - 1 | TADIGOL CROSS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008235 | 800/1 | 2.7216 | 0
| BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | Bank - 2 | TADIGOL CROSS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008214 | 800/1 | 4.117 | 0
B.591 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI RURAL | BANK-1 | TALAGAWARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247123 | 1200/1 | 13.0573 | 0
B.592 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI RURAL | BANK-2 | TALAGAWARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246664 | 1200/1 | 5.2852 | 0
B.593 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR URBAN | BANK-1 | TAMAKA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246794 | 800/1A | 9.5821 | 0
B.594 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR URBAN | BANK-2 | TAMAKA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247328 | 1200/1A | 13.4471 | 0
B.595 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | Bank - 1 | TAVAREKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253529 | 600/1 | 13.5628 | 0
B.596 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-2 | TAVAREKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253549 | 600/1 | 9.0333 | 0
B.597 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | BANK-1 | TAYALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246702 | 800/1A & 11KV/110V-110V | 4.5706 | 0
B.598 | BRAZ | KOLAR | 66/11 kV | KGF | MULABAGILU | Bank - 2 | TAYALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246730 | 800/1A & 11000/110-110V | 5.8762 | 0
B.599 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-1 | TEKAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247009 | 800-400/1-1-1A | 6.746 | 0
B.600 | BRAZ | KOLAR | 66/11 kV | KGF | MALUR | BANK-2 | TEKAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246815 | 800-400/1-1-1A | 9.7421 | 0
| BRAZ | RAMANAGAR | 66/11 kV | MAGADI | TAVAREKERE | BANK-1 | T.GOLLAHALLI(220/66/11) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18135755 | 800/1 | 1.9413 | 0
B.601 | BMASZ | West | 66/11 kV | Rajajinagar | N2 | BANK-1 | TELECOM LAY-OUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246117 | 1200/1 | 21.1957 | 0
B.602 | BMASZ | West | 66/11 kV | Rajajinagar | N2 | BANK-2 | TELECOM LAY-OUT | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245738 | 1200/1 | 23.712 | 0
B.603 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | TAVAREKERE | Bank - 1 | TG HALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17125719 | 400/1A | 3.3275 | 0
| BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-1 | THALAGUNDA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247364 | CT- 600/1-1-1A | 0.0713 | 0
| BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-2 | THALAGUNDA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0480380 | CT-800/1-1-1A | 2.9826 | 0
B.604 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-1 | THIMAMPALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247466 | 800/1 | 3.3054 | 0
B.605 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-2 | THIMAMPALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246356 | 400/1 | 3.4876 | 0
B.606 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GOWRIBIDANUR | BANK-1 | THONDEBHAVI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247447 | 1200/1 | 8.151 | 0
B.607 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GOWRIBIDANUR | BANK-2 | THONDEBHAVI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247468 | 1200/1 | 10.2019 | 0
| CTAZ | TUMKUR | 66/11 kV | TIPTUR | TURUVEKERE | BANK-1 | THORALAKKI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20006068 | 800-400/1-1-1 A | 4.5686 | 0
B.608 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DABASPETE | Bank - 1 | THYAMAGONDLU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16083131 | 1200-800/1-1-1A | 24.0547 | 0
B.609 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DABASPETE | Bank - 2 | THYAMAGONDLU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17031024 | 1200-800/1-1-1A | 10.2755 | 0
B.610 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (R) | BANK-1 | TUBUGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245260 | 800/1 | 4.2648 | 0
B.611 | BRAZ | BANGALORE RURAL | 66/11 kV | NELAMANGALA | DODDABALAPURA (R) | BANK-2 | TUBUGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245244 | 800/1 | 5.8101 | 0
| BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | BANK-1 | URAGAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094143 | 600/1 | 2.6804 | 0
| BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | BANK-2 | URAGAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18053983 | 600/1 | 2.1466 | 0
B.612 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | MAGADI | BANK-I | V.G.Doddi | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246026 | 600-300/1-1 | 0.41346 | 0
| BRAZ | RAMANAGAR | 66/11 kV | MAGADI | MAGADI | BANK-2 | V.G.Doddi | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18053769 | 600-300/1-1 | 2.3716 | 0
B.613 | BRAZ | RAMANAGAR | 66/11 KV | RAMANAGAR | BEVOORU | Bank - 1 | Vandaraguppe | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094112 | 800/1 | 2.159 | 0
B.614 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GUDIBANDE | BANK-1 | VATADAHOSAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246418 | 800/1 | 3.8775 | 0
B.615 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GUDIBANDE | BANK-2 | VATADAHOSAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247407 | 800/1 | 1.6343 | 0
B.616 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-1 | VEMAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005463 | 1200/1 & 11 kV/110V/√3 | 8.188 | 0
B.617 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-2 | VEMAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19004895 | 1200/1 & 11 kV/110V/√3 | 14.045 | 0
B.618 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | SATHANURU | Bank 1 | VENKATARAYANA DODDI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245811 | 800/1 | 3.6022 | 0
B.619 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | SATHANURU | Bank 2 | VENKATARAYANA DODDI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245700 | 800/1 | 3.4998 | 0
B.620 | BMANZ | East | 66/11 kV | VidhanaSoudha | W5 | Bank - 1 | VICTORIA HOSPITAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246211 | 1200/1 | 16.7974 | 0
B.621 | BMANZ | East | 66/11 kV | VidhanaSoudha | W5 | Bank - 2 | VICTORIA HOSPITAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245897 | 1200/1 | 18.434 | 0
B.622 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GOWRIBIDANUR | BANK-1 | VIDURASHWATHA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246886 | 1200/1 | 16.2497 | 0
B.623 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | GOWRIBIDANUR | BANK-2 | VIDURASHWATHA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246327 | 1200/1 | 11.1882 | 0
B.624 | BRAZ | BRC | 66/11 kV | HOSAKOTE | VIDYANAGAR | Bank - 1 | VIDYANAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247445 | 1200/1 | 16.4178 | 0
B.625 | BRAZ | BRC | 66/11 kV | HOSAKOTE | VIDYANAGAR | Bank - 2 | VIDYANAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247452 | 1200/1 | 17.0119 | 0
B.626 | BMASZ | BANGALORE WEST | 66/11 kV | RAJAJINAGAR | N2 | Bank - 1 | VIJAYANAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246206 | 2000/1 | 29.5844 | 0
B.627 | BMASZ | BANGALORE WEST | 66/11 kV | RAJAJINAGAR | N2 | Bank - 2 | VIJAYANAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246151 | 2000/1 | 27.455 | 0
B.628 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | BANK-1 | VIJAYAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245321 | 800/1 | 9.7512 | 0
B.629 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | BANK-2 | VIJAYAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245197 | 1200/1 | 8.7162 | 0
B.630 | BMASZ | South | 66/11 kV | Koramangala | S7 | Bank -1 | Vikas Tech Park | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258627 | 800/1 | 14.6868 | 0
B.631 | BMASZ | South | 66/11 kV | Koramangala | S7 | Bank -2 | Vikas Tech Park | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258635 | 2000/1 | 1.1604 | 0
B.632 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-1 | VOKKALERI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18048706 | 400/200 | 7.037 | 0
B.633 | BRAZ | KOLAR | 66/11 kV | KOLAR | KOLAR RURAL | BANK-2 | VOKKALERI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246778 | 800/1A & 11 kV/110V/√3 | 5.4842 | 0
B.634 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-1 | VOLVO | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259870 | 600/1 | 7.1756 | 0
B.635 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | HOSAKOTE | BANK-2 | VOLVO | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259869 | 600/1 | 7.7395 | 0
B.636 | BMASZ | BANGALORE WEST | 66/11 kV | RAJARAJESHWARINAGARA | W6 BYATARAYANAPURA | Bank - 1 | VRISHABHAWATI VALLEY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17125644 | 2000/1 | 22.6509 | 0
B.637 | BMASZ | BANGALORE WEST | 66/11 kV | RAJARAJESHWARINAGARA | W6 BYATARAYANAPURA | Bank - 2 | VRISHABHAWATI VALLEY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17125645 | 2000/1 | 14.1793 | 0
B.638 | BMANZ | North | 66/11 kV | Peenya | N5 | BANK - 1 | WELL CAST | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479600 | 1200/1 | 10.0658 | 0
B.639 | BMANZ | North | 66/11 kV | Peenya | N5 | BANK - 2 | WELL CAST | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479571 | 1200/1 | 5.8585 | 0
B.640 | BMANZ | North | 66/11 kV | Peenya | N5 | BANK - 2A | WELL CAST | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246186 | 800/1 | 3.8318 | 0
| BMANZ | North | 66/11 kV | Peenya | N5 | Bank -1 | WIDIA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479491 | 1200/1 | 11.634 | 0
B.641 | BMANZ | North | 66/11 kV | Peenya | N5 | Bank -2 | WIDIA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479491 | 1200/1 | 8.2897 | 0
wati | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA URBAN | BANK-1 | Y. HUNSENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247140 | 800/1-1-1A | 5.645 | 0
B.643 | BRAZ | KOLAR | 66/11 KV | CHINTHAMANI | SHIDLAGATTA URBAN | BANK-1 | Y. HUNSENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247140 | 600/1 | 0 | 0
B.644 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA URBAN | BANK-2 | Y. HUNSENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246462 | 800/1 | 5.6402 | 0
B.645 | BRAZ | KOLAR | 66/11 KV | CHINTHAMANI | SHIDLAGATTA URBAN | BANK-2 | Y. HUNSENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246462 | 800/1 | 0 | -0.02208
B.646 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | SHIDLAGATTA URBAN | BANK-3 | Y. HUNSENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | D421810 | 800/1 | 0 | 0
B.647 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | HAROHALLY | BANK-1 | YADAMADU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247202 | 400/1 | 2.5296 | 0
B.648 | BRAZ | RAMANAGAR | 66/11 kV | KANAKAPUR | HAROHALLY | BANK-2 | YADAMADU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246738 | 800/1A | 2.1898 | 0
B.649 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | CHANDAPURA | Bank - 1 | YARENDANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246205 | 1200/1 | 15.0317 | 0
B.650 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | CHANDAPURA | Bank - 2 | YARENDANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246164 | 1200/1 | 6.3937 | 0
B.651 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | CHANDAPURA | BANK-3 | YARENDANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246105 | 1200/1 | 18.6691 | 0
B.652 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | CHANDAPURA | BANK-4 | YARENDANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245963 | 1200/1 | 23.3884 | 0
B.653 | BRAZ | RAMANAGAR | 66/11 kV | CHANDAPURA | CHANDAPURA | BANK-5 | YARENDANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245774 | 1200/1 | 13.5368 | 0
B.654 | BRAZ | RAMANAGAR | 66/11 KV | CHANDAPURA | CHANDAPURA | Bank -6 | YARENDANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246213 | 1200/1 | 9.0234 | 0
B.655 | BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | BANK-1 | YELDUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094159 | 800/1 | 4.8028 | 0
B.656 | BRAZ | KOLAR | 66/11 kV | KOLAR | SRINIVASAPURA | BANK-2 | YELDUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247149 | 600/1 | 4.8264 | 0
B.657 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | BANK-1 | YELLARBANDE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259498 | 1200/1 | 21.1542 | 0
B.658 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | Bank-2 | YELLARBANDE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259502 | 1200/1 | 23.2132 | 0
B.659 | BMANZ | East | 66/11 kV | Shivajinagar | E9 | Bank-2A | YELLARBANDE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259339 | 1200/1 | 11.3903 | 0
B.660 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI RURAL | BANK-1 | YENIGDALE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246506 | 600/1 | 2.8226 | 0
B.661 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI RURAL | BANK-2 | YENIGDALE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0246471 | 800/1 | 6.1745 | 0
B.662 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-1 | ANAGODU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253537 | 800/1 | 8.999 | 0
B.663 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-2 | ANAGODU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253452 | 400/1 | 5.5776 | 0
B.664 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-1 | ATTIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253225 | 400/1 | 4.7109 | 0
B.665 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-2 | ATTIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253342 | 400/1 | 4.5136 | 0
B.666 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-1 | AVARGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19000035 | 800/1 | 2.9164 | 0
B.667 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-2 | AVARGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19000965 | 800/1 | 3.8733 | 0
B.668 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-3 | AVARGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253208 | 800/1 | 3.8234 | 0
B.669 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-4 | AVARGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253315 | 800/1 | 11.009 | 0
B.670 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-1 | BALENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248720 | 400/1 | 1.5486 | 0
B.671 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-1 | BALENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248720 | 400/1 | 0 | -0.2728
B.672 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-2 | BALENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248392 | 400/1 | 3.4748 | 0
B.673 | CTAZ | DAVANAGERE | 66/11 KV | HIRIYURU | CHALLAKERE | BANK-2 | BALENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248392 | 400/1 | 0 | 0
B.674 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOSADURGA | BANK-1 | BAGUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248619 | 600/1 | 3.7808 | 0
B.675 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOSADURGA | BANK-2 | BAGUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248426 | 600/1 | 2.989 | 0
B.676 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-1 | BIDARAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO2534191 | 600/1 | 4.3893 | 0
| CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-2 | BIDARAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19007933 | 600/1 | 1.3516 | 0
B.677 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | BANK-1 | B.G.KERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248351 | 600/1 | 5.0734 | 0
B.678 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | BANK-1 | B.G.KERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248351 | 600/1 | 0 | 0
B.679 | CTAZ | DAVANAGERE | 66/11 KV | HIRIYURU | MOLAKALMURU | BANK-2 | B.G.KERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248724 | 300/1 | 0.91524 | 0
B.680 | CTAZ | DAVANAGERE | 66/11 KV | HIRIYURU | MOLAKALMURU | BANK-2 | B.G.KERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248724 | 300/1 | 0 | -0.92601
B.681 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-1 | BANUVALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253185 | 400/1 | 3.7914 | 0
B.682 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-2 | BANUVALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253333 | 400/1 | 3.8306 | 0
B.683 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | SANTEBENNUR | BANK-1 | BASAVAPATNA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253114 | 800/1A | 6.046 | 0
B.684 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | SANTEBENNUR | BANK-2 | BASAVAPATNA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO253244 | 800/1 | 3.8629 | 0
B.685 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARAPANAHALLI | BANK-1 | BENNEHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0249175 | 600/1 | 3.1302 | 0
B.686 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARAPANAHALLI | BANK-2 | BENNEHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0249180 | 800/1 | 0.15144 | 0
B.687 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARAPANAHALLI | BANK-2 | BENNEHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0249180 | 800/1 | 0 | -2.5437
B.688 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARAPANAHALLI | BANK-1 | BENKIKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259916 | 400/1 | 5.1976 | 0
B.689 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARAPANAHALLI | BANK-2 | BENKIKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259919 | 400/1 | 3.5975 | 0
B.690 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-1 | BHARAMASAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248706 | 800/1 | 6.424 | 0
B.691 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-2 | BHARAMASAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248539 | 800/1 | 6.6952 | 0
| CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-3 | BHARAMASAGAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19000128 | 800/1 | 0.82781 | 0
B.692 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-1 | BILCHODU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253356 | 400/1 | 3.4457 | 0
B.693 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-2 | BILCHODU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253409 | 400/1 | 3.6776 | 0
B.694 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-1 | CHALLAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248542 | 800/1 | 13.1358 | 0
B.695 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-2 | CHALLAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248237 | 800/1 | 5.2831 | 0
B.696 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-1 | CHANNAGIRI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0469800 | 800/1 | 6.464 | 0
B.697 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-2 | CHANNAGIRI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0469783 | 800/1 | 6.2418 | 0
B.698 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-3 | CHANNAGIRI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0469764 | 12000/1 | 3.1318 | 0
B.699 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-1 | CHIKKAJAJUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248677 | 800/1 | 5.2719 | 0
B.700 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-2 | CHIKKAJAJUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248579 | 800/1 | 6.3797 | 0
B.701 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | NYAMATHI | BANK-1 | CHILUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253226 | 400/1 | 5.3809 | 0
B.702 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | NYAMATHI | BANK-2 | CHILUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253572 | 800/1 | 5.4202 | 0
B.703 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA_RA | BANK-1 | CHITRADURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248424 | 800/1 | 5.5203 | 0
B.704 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA_RA | BANK-1 | CHITRADURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248424 | 800/1 | 0 | -0.03904
B.705 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA_RA | BANK-2 | CHITRADURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248700 | 800/1 | 5.681 | 0
B.706 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA_RA | BANK-2 | CHITRADURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248700 | 800/1 | 0 | -0.65464
B.707 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA_RA | BANK-3 | CHITRADURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248306 | 800/1 | 12.911 | 0
B.708 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA_RA | BANK-3 | CHITRADURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248306 | 800/1 | 0 | 0
B.709 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA_RA | Bank-1 | CHITRADURGA-SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248389 | 800/1 | 7.7396 | 0
B.710 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA_RA | Bank-1 | CHITRADURGA-SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248389 | 800/1 | 0 | -0.00088
B.711 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA_RA | Bank-2 | CHITRADURGA-SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248505 | 800/1 | 2.6334 | 0
B.712 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-1 | CHITHRAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248463 | 400/1 | 2.4115 | 0
B.713 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | Bank 2 | CHITHRAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248332 | 800/1 | 6.0002 | 0
B.714 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | BANK-1 | DEVARAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253363 | 600/1 | 4.2139 | 0
B.715 | BRAZ | BANGALORE RURAL | 66/11 kV | HOSAKOTE | DEVANAHALLI | BANK-2 | DEVARAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253132 | 800/1 | 3.6492 | 0
B.716 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-1_RA | BANK-1 | DAVANGERE (MUSS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253236 | 800/1 | 8.0274 | 0
B.717 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-1_RA | BANK-2 | DAVANGERE (MUSS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253125 | 800/1 | 8.941 | 0
B.718 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-1_RA | BANK-3 | DAVANGERE (MUSS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KEB165298 | 200/1 | 9.8754 | 0
B.719 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-1_RA | BANK-4 | DAVANGERE (MUSS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253339 | 800/1 | 9.7429 | 0
B.720 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-1_RA | BANK-1 | DAVANGERE SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253410 | 1200/1 | 3.6544 | 0
B.721 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-1_RA | BANK-2 | DAVANGERE SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253256 | 800/1 | 12.3839 | 0
B.722 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-1_RA | BANK-3 | DAVANGERE SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253203 | 1200/1 | 2.6147 | 0
B.723 | CTAZ | DAVANAGERE | 66/11 KV | DAVANAGERE | DAVANAGERE CSD-1_RA | BANK-4 | DAVANGERE SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094144 | 800/1 | 6.0363 | 0
B.724 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-1 | DEVARABELAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253275 | 400/1 | 0 | 0
B.725 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-2 | DEVARABELAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253484 | 400/1 | 4.3986 | 0
B.726 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-1 | DYAVARAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248570 | 400/1 | 0.6144 | 0
B.727 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-1 | DYAVARAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248570 | 400/1 | 0 | -1.528
B.728 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-2 | DYAVARAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167037 | 400/1-1-1A | 2.116 | 0
B.729 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-2 | DYAVARAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167037 | 400/1-1-1A | 0 | -0.60364
B.730 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | SRIRAMPURA | BANK-1 | GARAGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248569 | 600/1 | 3.5197 | 0
B.731 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | SRIRAMPURA | BANK-2 | GARAGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248572 | 400/1 | 3.8418 | 0
B.732 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-1 | GOPPENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253075 | 400/1 | 5.4612 | 0
B.733 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-2 | GOPPENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253572 | 800/1 | 10.4439 | 0
B.734 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-1 | GOWRASAMUDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0469753 | 600/1 | 3.55 | 0
B.735 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-1 | GOWRASAMUDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0469753 | 600/1 | 0 | -0.00342
B.736 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-2 | GOWRASAMUDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0469742 | 400/1 | 1.0886 | 0
B.737 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-2 | GOWRASAMUDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0469742 | 400/1 | 0 | -0.39066
B.738 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-1 | GUTTUR 66KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253186 | 400/1 | 2.0642 | 0
B.739 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-2 | GUTTUR 66KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253564 | 800/1 | 5.035 | 0
B.740 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK 3 | GUTTUR 66KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253576 | 800/1 | 3.277 | 0
B.741 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | BANK-1 | HALAVAGULU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253253 | 600/1 | 2.2267 | 0
B.742 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | BANK-2 | HALAVAGULU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253511 | 600/1 | 2.7065 | 0
B.743 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | BANK-3 | HALAVAGULU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253105 | 400/1 | 3.3555 | 0
B.744 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOSADURGA | BANK-1 | HALURAMESWARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248688 | 800/1 | 5.3227 | 0
B.745 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOSADURGA | BANK-2 | HALURAMESWARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248390 | 400/1 | 3.233 | 0
B.746 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | BANK-1 | HANAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248557 | 800/1 | 5.063 | 0
B.747 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | BANK-1 | HANAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248557 | 800/1 | 0 | 0
B.748 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | BANK-2 | HANAGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248598 | 600/1 | 5.3233 | 0
B.749 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARAPANAHALLI | BANK-1 | HARAPANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0470355 | 600/1 | 3.1426 | 0
B.750 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARAPANAHALLI | BANK-2 | HARAPANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0470380 | 600/1 | 6.8514 | 0
B.751 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARAPANAHALLI | BANK-3 | HARAPANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0470369 | 800/1 | 5.2094 | 0
B.752 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-1 | HARIHARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253477 | 800/1 | 5.3538 | 0
B.753 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-2 | HARIHARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253430 | 800/1 | 2.2488 | 0
B.754 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-1 | HARIYABBE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248580 | 800/1 | 5.384 | 0
B.755 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | HARIYABBE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248571 | 400/1 | 3.2128 | 0
B.756 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-3 | HARIYABBE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248223 | 600/1 | 4.9326 | 0
B.757 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-3 | HARIYABBE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248223 | 600/1 | 0 | 0
B.758 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-1 | HD PURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248252 | 600/1 | 6.8012 | 0
B.759 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-2 | HD PURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248421 | 600/1 | 5.1876 | 0
B.760 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK 1 | HINDUSGHATTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248273 | 800/1 | 9.1803 | 0
B.761 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK 2 | HINDUSGHATTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248466 | 800/1 | 4.5034 | 0
B.762 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-1 | HIRIYUR 66 KV SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248263 | 1200/1 | 4.4676 | 0
B.763 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | HIRIYUR 66 KV SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248290 | 800/1 | 1.9809 | 0
B.764 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | HIRIYUR 66 KV SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248263 | 1200/1 | 0 | -0.00784
B.765 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-1 | HIRIYUR(66KV) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248244 | 800/1 | 5.9766 | 0
B.766 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | HIRIYUR(66KV) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248645 | 800/1 | 7.2531 | 0
B.767 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK1 | HIREGUNTANUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248698 | 400/1 | 6.8224 | 0
B.768 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK2 | HIREGUNTANUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248459 | 600/1 | 7.4536 | 0
B.769 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-1 | HIREMALLANAHOLE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258291 | 600/1 | 0.99144 | 0
B.770 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-1 | HIREMALLANAHOLE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258291 | 600/1 | 0 | -1.7264
B.771 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-2 | HIREMALLANAHOLE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258283 | 600/1 | 0.27168 | 0
B.772 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-2 | HIREMALLANAHOLE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO258283 | 600/1 | 0 | -2.3489
B.773 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-1 | HOLALKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248473 | 800/1 | 3.0617 | 0
B.774 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-2 | HOLALKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0308176 | 800/1 | 7.1553 | 0
B.775 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-3 | HOLALKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18135649 | 1200/1 | 0.4896 | 0
B.776 | CTAZ | DAVANAGERE | 66/11 KV | CHITRADURGA | HOLALKERE | BANK-4 | HOLALKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248609 | 1200/1 | 4.4942 | 0
B.777 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HONNALI | BANK-1 | HONNALI 66 KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253135 | 400/1 | 4.3102 | 0
B.778 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HONNALI | BANK-2 | HONNALI 66 KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253542 | 800/1 | 3.943 | 0
B.779 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HONNALI | BANK-3 | HONNALI 66 KV | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253194 | 400/1 | 4.2408 | 0
B.780 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HONNALI | Bank-1 | HONNALI-SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253334 | 800/1 | 4.8032 | 0
B.781 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HONNALI | Bank-2 | HONNALI-SRS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253243 | 800/1 | 2.9701 | 0
B.782 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOSADURGA | BANK-1 | HOSADURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248221 | 800/1 | 7.2376 | 0
B.783 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOSADURGA | BANK-2 | HOSADURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248287 | 800/1 | 7.212 | 0
B.784 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-1 | IMMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248308 | 800/1 | 5.2464 | 0
B.785 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | IMMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248369 | 800/1 | 2.2961 | 0
B.786 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-3 | IMMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248697 | 800/1 | 2.664 | 0
B.787 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-3 | IMMANGALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248697 | 800/1 | 0 | -1.36
B.788 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-1 | JAGALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253439 | 800/1 | 5.6072 | 0
B.789 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-2 | JAGALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253522 | 800/1 | 3.6111 | 0
B.790 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-3 | JAGALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253067 | 800/1 | 2.4557 | 0
B.791 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-3 | JAGALUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253067 | 800/1 | 0 | -0.26408
B.792 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-1 | JAVAGONDANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KAU07656 | 400/1 | 6.815 | 0
| CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-1 | JAVAGONDANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KAU07656 | 400/1 | 0 | -8e-05
B.793 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | JAVAGONDANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248625 | 800/1 | 3.3702 | 0
B.794 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | JAVAGONDANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248625 | 800/1 | 0 | -0.13392
| CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA URBAN | BANK-1 | JN Kote | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20006073 | 800/1 | 0 | 0
| CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA URBAN | BANK-2 | JN Kote | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20006073 | 800/1 | 0 | -1.9382
B.795 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE RURAL | BANK-1 | KADAJJI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253392 | 400/1 | 3.3031 | 0
B.796 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE RURAL | BANK-2 | KADAJJI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253346 | 400/1 | 3.4752 | 0
B.797 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-1 | KALAMARANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KAU07656 | 400/1 | 3.2098 | 0
B.798 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-1 | KALAMARANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KAU07656 | 400/1 | 0 | -0.043135
| CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-2 | KALAMARANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009824 | 400/1 | 2.2614 | 0
| CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-2 | KALAMARANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009824 | 400/1 | 0 | -0.0161
B.799 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | SRIRAMPURA | BANK-1 | KANCHIPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248715 | 600/1 | 2.1204 | 0
B.800 | CTAZ | DAVANAGERE | 66/11 KV | CHITRADURGA | SRIRAMPURA | BANK-2 | KANCHIPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18092720 | 400/1 | 2.087 | 0
B.801 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | NYAMATHI | BANK-1 | KATTIGE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253481 | 400/1 | 3.6537 | 0
B.802 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | NYAMATHI | BANK-1 | KATTIGE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253481 | 400/1 | 0 | -0.097
B.803 | CTAZ | DAVANAGERE | 66/11 KV | HARIHARA | NYAMATHI | BANK-2 | KATTIGE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18077741 | 400/1 | 2.3741 | 0
B.804 | CTAZ | DAVANAGERE | 66/11 KV | HARIHARA | NYAMATHI | BANK-2 | KATTIGE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18077741 | 400/1 | 0 | 0
B.805 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | SANTEBENNUR | BANK-1 | KEREBILACHI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253249 | 400/1 | 2.3114 | 0
B.806 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | SANTEBENNUR | BANK-2 | KEREBILACHI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253526 | 400/1 | 3.3958 | 0
B.807 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE RURAL | BANK-1 | KUKKAVADA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO253407 | 600/1 | 4.9051 | 0
B.808 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE RURAL | BANK-2 | KUKKAVADA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO253554 | 300/1 | 3.0002 | 0
B.809 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE RURAL | BANK-3 | KUKKAVADA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO253387 | 400/1 | 0 | 0
B.810 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HONNALI | BANK-1 | KUNDUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253332 | 400/1 | 5.3857 | 0
B.811 | CTAZ | DAVANAGERE | 66/11 KV | HARIHARA | HONNALI | BANK-2 | KUNDUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094169 | 800/1 | 1.3528 | 0
B.812 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK1 | KURUBARAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253322 | 800/1 | 3.0598 | 0
B.813 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK2 | KURUBARAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253568 | 400/1 | 3.7868 | 0
B.814 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOSADURGA | BANK1 | MADADAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094134 | 400/1-1-1A | 2.7689 | 0
B.815 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOSADURGA | BANK2 | MADADAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094180 | 400/1-1-1A | 2.4582 | 0
B.816 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-1 | LINGADAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253267 | 800/1 | 6.7752 | 0
B.817 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-2 | LINGADAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253444 | 800/1A | 5.6469 | 0
B.818 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA URBAN | BANK-1 | MADANAYAKANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248297 | 400/1 | 3.2228 | 0
B.819 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA URBAN | BANK-1 | MADANAYAKANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248297 | 400/1 | 0 | -0.54348
B.820 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA URBAN | BANK-2 | MADANAYAKANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248428 | 400/1 | 3.1228 | 0
B.821 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA URBAN | BANK-2 | MADANAYAKANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248428 | 400/1 | 0 | 0
B.822 | CTAZ | DAVANAGERE | 66/11 KV | CHITRADURGA | HOLALKERE | BANK-1 | MALLADIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248530 | 400/1 | 3.3625 | 0
B.823 | CTAZ | DAVANAGERE | 66/11 KV | CHITRADURGA | HOLALKERE | BANK-2 | MALLADIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248349 | 800/1 | 3.526 | 0
B.824 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-1 | MALEBENNUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253250 | 800/1 | 11.0099 | 0
B.825 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-2 | MALEBENNUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253560 | 800/1 | 1.048 | 0
B.826 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | SRIRAMPURA | Bank -1 | MATHOD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248286 | 800/1 | 3.2158 | 0
B.827 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | SRIRAMPURA | Bank - 2 | MATHOD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248613 | 800/1 | 3.2597 | 0
B.828 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | SRIRAMPURA | Bank - 2 | MATHOD | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248613 | 800/1 | 0 | -0.09848
B.829 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-1 | MAVINAKATTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253545 | 600/1 | 3.7365 | 0
B.830 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-1 | MAVINAKATTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253545 | 600/1 | 0 | -0.05964
B.831 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-2 | MAVINAKATTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253419 | 600/1 | 3.7895 | 0
B.832 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-2 | MAVINAKATTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253419 | 600/1 | 0 | 0
B.833 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-1 | MAYAKONDA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253503 | 400/1 | 5.9974 | 0
B.834 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-2 | MAYAKONDA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253233 | 600/1 | 6.5452 | 0
B.835 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-1 | MELLEKATTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253063 | 800/1 | 4.7661 | 0
B.836 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-2 | MELLEKATTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253345 | 800/1 | 6.7249 | 0
B.837 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-1 | MYLANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248481 | 400/1 | 4.1923 | 0
B.838 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-1 | MYLANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248481 | 400/1 | 0 | -0.13412
B.839 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK 2 | MYLANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248576 | 800/1 | 2.6073 | 0
B.840 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK 2 | MYLANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248576 | 800/1 | 0 | -0.62312
B.841 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | BANK-1 | NAGASAMUDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005511 | 600/1 | 4.8438 | 0
| CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | MOLAKALMURU | BANK-2 | NAGASAMUDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009707 | 400/1 | 0 | 0
B.842 | CTAZ | DAVANAGERE | 66/11 KV | DAVANAGERE | CHANNAGIRI | BANK-1 | NALLUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18128615 | 800-400/1 | 4.0769 | 0
B.843 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-1 | NANDIGUDI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258300 | 400/1 | 3.883 | 0
B.844 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HARIHARA | BANK-2 | NANDIGUDI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258289 | 800/1 | 4.2866 | 0
B.845 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-1 | NAYAKANAHATTY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248296 | 800/1 | 3.8294 | 0
B.846 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-1 | NAYAKANAHATTY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248296 | 800/1 | 0 | -0.26576
B.847 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-2 | NAYAKANAHATTY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248367 | 800/1 | 6.1475 | 0
B.848 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-1 | NERALAGUNTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008251 | 800/1 | 2.5655 | 0
| CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-1 | NERALAGUNTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008251 | 800/1 | 0.9854 | 0
| CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | BANK-1 | NEERAGUNDA GATE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17094100 | 400/1 | 1.6099 | 0
B.849 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOSADURGA | BANK-1 | NEELAGUNDA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253303 | 800/1 | 4.1598 | 0
B.850 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | NYAMATHI | BANK-1 | NYAMTI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253178 | 400/1 | 2.4737 | 0
B.851 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | NYAMATHI | BANK-2 | NYAMTI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253479 | 800/1 | 5.3472 | 0
B.852 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE RURAL | BANK-1 | OBAJIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253519 | 600/1 | 3.6392 | 0
B.853 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-1 | PALLAGATTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253400 | 800/1 | 3.1263 | 0
B.854 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-2 | PALLAGATTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253123 | 600/1 | 2.2366 | 0
B.855 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-3 | PALLAGATTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253196 | 400/1 | 2.643 | 0
B.856 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-1 | PANDRALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248477 | 800/1 | 7.1131 | 0
B.857 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-1 | PANDRALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248477 | 800/1 | 0 | 0
B.858 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-3 | PANDRALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248666 | 1200/1 | 10.6686 | 0
B.859 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-3 | PANDRALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248666 | 1200/1 | 0 | -0.10432
B.860 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-1 | PARUSHAMPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248328 | 800/1 | 7.3158 | 0
B.861 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-2 | PARUSHAMPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248561 | 800/1 | 7.8086 | 0
B.862 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-1 | PD KOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248277 | 400/1 | 3.3948 | 0
B.863 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-1 | PD KOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248277 | 400/1 | 0 | -0.031
| CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | PD KOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009823 | 400/1 | 3.7916 | 0
| CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | PD KOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009823 | 400/1 | 0 | 0
B.864 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | BANK-1 | PUNABAGHATTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253213 | 800/1 | 4.6985 | 0
B.865 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | BANK-2 | PUNABAGHATTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258299 | 800/1 | 7.2882 | 0
B.866 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-1 | RAMAGIRI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248302 | 600/1 | 5.2766 | 0
B.867 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | Bank-2 | RAMAGIRI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248217 | 600/1 | 7.2622 | 0
B.868 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-1 | RAMPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248269 | 800/1 | 6.3462 | 0
B.869 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | BANK-2 | RAMPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248646 | 300/1 | 6.3986 | 0
B.870 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-1 | RANGANATHAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248544 | 400/1 | 5.045 | 0
B.871 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | RANGANATHAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248653 | 400/1 | 3.5303 | 0
B.872 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-1 | RANGENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0469744 | 600/1 | 2.2307 | 0
B.873 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | HIRIYUR | BANK-2 | RANGENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167041 | 400/1A | 3.1159 | 0
B.874 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-1 | SANIKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248542 | 400/1 | 3.478 | 0
B.875 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-2 | SANIKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248237 | 600/1 | 3.993 | 0
B.876 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | CHALLAKERE | BANK-2 | SANIKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248237 | 600/1 | 0 | -0.0117
B.877 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | SANTEBENNUR | BANK-1 | SANTHEBENNUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253551 | 800/1 | 4.8324 | 0
B.878 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | SANTEBENNUR | Bank 2 | SANTHEBENNUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253337 | 800/1 | 8.5291 | 0
B.879 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | Bank 1 | SASALUHALLA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248499 | 400/1 | 4.8058 | 0
B.880 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | HOLALKERE | Bank 2 | SASALUHALLA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248567 | 800/1 | 5.2618 | 0
B.881 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HONNALI | BANK-1 | SASUVEHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253115 | 800/1 | 4.3366 | 0
B.882 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | HONNALI | BANK-2 | SASUVEHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253546 | 600/1 | 7.94 | 0
B.883 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | NYAMATHI | BANK-1 | SAVALANGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253347 | 600/1 | 1.4165 | 0
B.884 | CTAZ | DAVANAGERE | 66/11 KV | HARIHARA | NYAMATHI | BANK-2 | SAVALANGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19001057 | 400./1 | 4.4253 | 0
B.885 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE RURAL | BANK-1 | SHYAGALE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253482 | 400/1 | 2.8363 | 0
B.886 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-1 | SIRIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248651 | 800/1 | 4.2916 | 0
B.887 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-2 | SIRIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248652 | 600/1 | 3.3774 | 0
| CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-3 | SIRIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20001173 | 800/1 | 2.018 | 0
B.888 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-1 | SOKKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253344 | 800/1 | 4.6392 | 0
| CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | JAGALURU | BANK-2 | SOKKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19007966 | 800/1 | 2.5552 | 0
B.889 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-1 | TAVAREKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253529 | 600/1 | 3.9205 | 0
B.890 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-2 | TAVAREKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253549 | 600/1 | 2.9533 | 0
B.891 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | BANK-1 | TELIGI(66KV MUSS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253313 | 800/1 | 2.7845 | 0
B.892 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | Bank - 2 | TELIGI(66KV MUSS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253309 | 400/1 | 3.4765 | 0
B.893 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | Bank - 3 | TELIGI(66KV MUSS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253309 | 400/1 | 4.3988 | 0
B.894 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | Bank - 3 | TELIGI(66KV MUSS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253172 | 600/1 | 0 | 0
B.895 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-1 | THALLAK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248597 | 800/1 | 4.9459 | 0
B.896 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-2 | THALLAK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248519 | 400/1 | 2.2447 | 0
B.897 | CTAZ | DAVANAGERE | 66/11 kV | HIRIYURU | TALAKU | BANK-2 | THALLAK | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248519 | 400/1 | 0 | -0.3096
B.898 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-1 | TURUVANUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248529 | 800/1 | 3.4103 | 0
B.899 | CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-2 | TURUVANUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248721 | 400/1 | 2.8942 | 0
B.900 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | SANTEBENNUR | BANK-1 | TYAVANAGI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO253062 | 800/1 | 7.3309 | 0
B.901 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | BANK-1 | UCHCHANGIDURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253179 | 800/1 | 3.5386 | 0
B.902 | CTAZ | DAVANAGERE | 66/11 kV | HARIHARA | TELAGI | Bank 2 | UCHCHANGIDURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253276 | 800/1 | 5.3037 | 0
| CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | BANK-1 | Vijapura | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245321 | 800/1 | 0 | -4.0412
| CTAZ | DAVANAGERE | 66/11 kV | CHITRADURGA | CHITRADURGA RURAL | Bank 2 | Vijapura | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0245197 | 1200/1 | 0 | 0
B.903 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-1 | VANI VILASPURA (BHARAMAGIRI) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248272 | 400/1 | 5.1872 | 0
B.904 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | Bank 2 | VANI VILASPURA (BHARAMAGIRI) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248654 | 400/1 | 5.3372 | 0
B.905 | CTAZ | DAVANAGERE | 66/11 KV | HIRIYURU | CHALLAKERE | BANK-1 | VISHVESWARAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19000031 | 400/1 | 2.7131 | 0
B.906 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-2_RA | BANK-1 | YARGUNTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253424 | 800/1 | 4.5371 | 0
B.907 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-2_RA | BANK-2 | YARGUNTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253369 | 200/1A | 5.6134 | 0
B.908 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-2_RA | BANK-3 | YARGUNTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253301 | 200/1A | 3.5138 | 0
| CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-2_RA | BANK-3 | YARGUNTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253301 | 200/1A | 0 | -8e-05
B.909 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | DAVANAGERE CSD-2_RA | BANK-4 | YARGUNTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253396 | 800/1 | 6.7784 | 0
B.910 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-1 | AMMASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247806 | 800/1 | 4.2854 | 0
B.911 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-2 | AMMASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247795 | 800/1 | 4.3018 | 0
B.912 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-3 | AMMASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247935 | 1200/1 | 4.8509 | 0
B.913 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | GUBBI | BANK-1 | ANKASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252902 | 400/1 | 5.3477 | 0
B.914 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | GUBBI | BANK-2 | ANKASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18128614 | 400/1 | 2.5208 | 0
| CTAZ | TUMKUR | 66/11 kV | TUMKUR | GUBBI | BANK-2 | ANKASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18128614 | 400/1 | 0 | -0.6923
B.915 | CTAZ | TUMKUR | 66/11 kV | Kunigal | YEDIYUR | BANK-1 | AMRUTHUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247676 | 600/1 | 5.3555 | 0
B.916 | CTAZ | TUMKUR | 66/11 kV | Kunigal | YEDIYUR | BANK-2 | AMRUTHUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247607 | 600/1 | 4.1665 | 0
B.917 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-1 | ANCHEPALYA(66KV) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247721 | 800/1 | 3.6089 | 0
B.918 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-2 | ANCHEPALYA(66KV) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KEB16703 | 800/1 | 6.5309 | 0
B.919 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-3 | ANCHEPALYA(66KV) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247713 | 400/1 | 7.4075 | 0
B.920 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR CSD-1_RA | BANK-1 | ANTHARASANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252912 | 1200/1 | 16.727 | 0
B.921 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR CSD-1_RA | BANK-2 | ANTHARASANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252925 | 1200/1 | 13.3559 | 0
B.922 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR CSD-1_RA | BANK-3 | ANTHARASANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252701 | 1200/1 | 21.6024 | 0
B.923 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR CSD-1_RA | BANK-3 | ANTHARASANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252701 | 1200/1 | 0 | 0
B.924 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | BANK-1 | BADAVANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248020 | 800/1 | 8.7641 | 0
B.925 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | BANK-2 | BADAVANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248103 | 800/1 | 6.623 | 0
B.926 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR CSD-2_RA | BANK-1 | BADDIHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252656 | 800/1 | 7.7178 | 0
B.927 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR CSD-2_RA | BANK-2 | BADDIHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252755 | 800/1 | 8.9068 | 0
B.928 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-1 | BANDIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247971 | 600/1 | 7.309 | 0
B.929 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-2 | BANDIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247755 | 600/1 | 7.7879 | 0
B.930 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK-1 | BELADARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252622 | 400/1 | 2.372 | 0
B.931 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK-2 | BELADARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252637 | 400/1 | 3.1302 | 0
B.932 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK-1 | BELLAVI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252704 | 800/1 | 4.0944 | 0
B.933 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK-2 | BELLAVI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Qo252773 | 800/1 | 5.5606 | 0
B.934 | CTAZ | TUMKUR | 66/11 KV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK-3 | BELLAVI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18093063 | 800/1 | 5.196 | 0
B.935 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | Bank-1 | BEVINAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252867 | 800/1 | 4.7367 | 0
B.936 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | Bank-2 | BEVINAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252909 | 800/1 | 6.4506 | 0
B.937 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | KUNIGAL | BANK-1 | BHAKTHARAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247673 | 800/1 | 5.0921 | 0
B.938 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | KUNIGAL | BANK-2 | BHAKTHARAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247736 | 800/1 | 4.1773 | 0
B.939 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | BANK-1 | BIDARE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253028 | 600/1 | 5.7124 | 0
| CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | BANK-2 | BIDARE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008090 | 800/1 | 4.4234 | 0
B.940 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-1 | BRAHMASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252889 | 1200/1 | 7.3595 | 0
B.941 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-2 | BRAHMASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252804 | 800/1 | 6.6249 | 0
B.942 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-1 | BUKKAPATNA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252615 | 1200/1 | 11.5603 | 0
B.943 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-2 | BUKKAPATNA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252810 | 600/1 | 4.7196 | 0
B.944 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-2 | BUKKAPATNA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252810 | 600/1 | 0 | -0.0384
B.945 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-1 | CHELUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252698 | 1200/1 | 9.1831 | 0
B.946 | BRAZ | KOLAR | 66/11 kV | CHIKKABALLAPURA | BAGEPALLI | BANK-2 | CHELUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252536 | 1200/1 | 9.8764 | 0
B.947 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK-1 | CHIKKABANAGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252803 | 800/1 | 6.9023 | 0
B.948 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK-2 | CHIKKABANAGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253685 | 600/1 | 3.4255 | 0
B.949 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK-2 | CHIKKABANAGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253685 | 600/1 | 0 | -0.03582
B.950 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | BANK-1 | CHIKKANAYAKANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247975 | 800/1 | 7.6106 | 0
B.951 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | BANK-2 | CHIKKANAYAKANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247886 | 800/1 | 5.753 | 0
| CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | BANK-3 | CHIKKANAYAKANAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18128638 | 1200/1 | 2.5716 | 0
B.952 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK 1 | CHIKKATHOTLUKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252957 | 400/1 | 3.8 | 0
B.953 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK 2 | CHIKKATHOTLUKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252824 | 800/1 | 4.8648 | 0
B.954 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK 2 | CHIKKATHOTLUKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252824 | 800/1 | 0 | -0.008
| CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK 1 | CHENGAVARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19005499 | 800/1 | 3.0852 | 0
B.955 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | HULIYURDURGA | BANK-1 | CHOWDANAKUPPE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247628 | 400/1 | 2.4328 | 0
B.956 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | HULIYURDURGA | BANK-2 | CHOWDANAKUPPE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247678 | 400/1 | 1.4928 | 0
B.957 | CTAZ | TUMKUR | 66/11 kV | TIPTUR | CN HALLY | BANK-1 | DASOODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247948 | 400/1 | 5.2258 | 0
B.958 | CTAZ | TUMKUR | 66/11 KV | TIPTUR | CN HALLY | BANK-1 | DASOODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247948 | 400/1 | 0 | -0.00768
B.959 | CTAZ | TUMKUR | 66/11 kV | TIPTUR | CN HALLY | BANK-2 | DASOODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247788 | 400/1 | 4.2942 | 0
B.960 | CTAZ | TUMKUR | 66/11 kV | TIPTUR | CN HALLY | BANK-2 | DASOODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247788 | 400/1 | 0 | 0
B.961 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | NITTUR | BANK-1 | DODDAGUNI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252783 | 600/1 | 6.3158 | 0
B.962 | CTAZ | TUMKUR | 110/11 KV | TUMKUR | NITTUR | BANK-2 | DODDAGUNI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252911 | 800/1 | 3.0085 | 0
B.963 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-1 | DODDASARANGI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO247573 | 600/1 | 5.101 | 0
| CTAZ | TUMKUR | 110/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-2 | DODDASARANGI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20005935 | 600/1 | 1.6008 | 0
B.964 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | BANK-1 | GUBBI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253044 | 1200/1 | 9.4834 | 0
B.965 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | BANK-2 | GUBBI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252754 | 800/1 | 6.5146 | 0
B.966 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | BANK-3 | GUBBI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252679 | 1200/1 | 13.5916 | 0
| CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | BANK-4 | GUBBI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18092766 | 1200/1 | 1.0765 | 0
B.967 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK 1 | GULIGENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252809 | 800/1 | 4.7849 | 0
B.968 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK 2 | GULIGENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252818 | 800/1 | 6.633 | 0
B.969 | CTAZ | TUMKUR | 110/11 kV | MADHUGIRI | SIRA URBAN | BANK-1 | GUNGURUMALE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247766 | 800/1 | 2.8582 | 0
B.970 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | NITTUR | BANK-1 | HAGALAVADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258926 | 600/1-1-1 | 4.4905 | 0
B.971 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-1 | HALKURKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248082 | 600/1 | 2.2607 | 0
B.972 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-2 | HALKURKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17167033 | 800/1 | 2.8684 | 0
B.973 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | BANK-1 | HANDANAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259924 | 800/1 | 4.2123 | 0
B.974 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | BANK-2 | HANDANAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259920 | 800/1 | 6.4067 | 0
B.975 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-1 | HEBBUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247641 | 800/1 | 6.5344 | 0
B.976 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-2 | HEBBUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247587 | 600/1 | 4.9517 | 0
B.977 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-3 | HEBBUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247627 | 800/1 | 5.6301 | 0
B.978 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-1 | HEGGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252610 | 400/1 | 3.7265 | 0
B.979 | CTAZ | TUMKUR | 66/11 KV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-2 | HEGGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18158282 | 800/1 | 2.5227 | 0
| CTAZ | TUMKUR | 66/11 KV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-2 | HEGGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18158282 | 800/1 | 0 | -0.1399
B.980 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | KYATSANDRA | BANK-1 | HIREHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252615 | 1200/1 | 14.0334 | 0
B.981 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | KYATSANDRA | BANK-2 | HIREHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252586 | 600/1 | 10.9487 | 0
B.982 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KORATAGERE | BANK-1 | HOLAVANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248031 | 600/1 | 4.9985 | 0
B.983 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KORATAGERE | BANK-2 | HOLAVANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248019 | 800/1 | 5.8304 | 0
| CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KORATAGERE | BANK-2 | HOLAVANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248019 | 800/1 | 0 | -0.01856
B.984 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KORATAGERE | BANK-2 | HOLAVANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248019 | 800/1 | 0 | 0
B.985 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | Bank 1 | HONNAVALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247951 | 800/1 | 4.2673 | 0
B.986 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | Bank 2 | HONNAVALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248029 | 800/1 | 4.5929 | 0
| CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | Bank 1 | HONNENAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19009829 | 400/1 | 3.2975 | 0
B.987 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | KYATSANDRA | BANK 1 | HONNUDIKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252762 | 600/1 | 4.8343 | 0
B.988 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | KYATSANDRA | BANK 2 | HONNUDIKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO247547 | 600/1 | 9.6972 | 0
B.989 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | KYATSANDRA | BANK 2 | HONNUDIKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO247547 | 600/1 | 0 | 0
B.990 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | NITTUR | BANK-1 | HOSAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253031 | 1200/1 | 8.9544 | 0
B.991 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | NITTUR | BANK-2 | HOSAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252993 | 800/1 | 7.9512 | 0
B.992 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | NITTUR | BANK-1 | HOSAKERE (Madhugiri) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248178 | 400/1 | 3.5155 | 0
B.993 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | NITTUR | BANK-1 | HOSAKERE (Madhugiri) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248178 | 400/1 | 0 | 0
B.994 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | NITTUR | BANK-2 | HOSAKERE (Madhugiri) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248198 | 400/1 | 4.4 | 0
B.995 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | NITTUR | BANK-2 | HOSAKERE (Madhugiri) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248198 | 400/1 | 0 | -0.12552
B.996 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | BANK-1 | HULIYAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247880 | 800/1 | 5.8191 | 0
B.997 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | BANK-2 | HULIYAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247950 | 800/1 | 4.6916 | 0
B.998 | CTAZ | TUMKUR | 110/11 KV | TIPTUR | CN HALLY | BANK-3 | HULIYAR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19000167 | 800/1 | 3.6328 | 0
B.999 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | HULIYURDURGA | BANK-1 | HULIYURDURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247704 | 600/1 | 3.0609 | 0
B.1000 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | HULIYURDURGA | BANK-2 | HULIYURDURGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247675 | 800/1 | 5.7269 | 0
B.1001 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-1 | HUNASEGATTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247759 | 600/1 | 4.7878 | 0
B.1002 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-2 | HUNASEGATTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247763 | 600/1 | 2.7859 | 0
B.1003 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | BANK 1 | I.D.Hally | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248074 | 800/1 | 4.3704 | 0
B.1004 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | BANK 1 | I.D.Hally | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248074 | 800/1 | 0 | 0
B.1005 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | BANK 2 | I.D.Hally | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248100 | 400/1 | 3.313 | 0
B.1006 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | BANK 2 | I.D.Hally | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248100 | 400/1 | 0 | -0.08064
B.1007 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | YEDIYUR | BANK-1 | JIDDIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247665 | 400/1 | 3.546 | 0
| CTAZ | TUMKUR | 66/11 kV | KUNIGAL | YEDIYUR | BANK-2 | JIDDIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 21004840 | 400/1 | 1.4296 | 0
B.1008 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-1 | K.B.CROSS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247826 | 800/1 | 5.7919 | 0
B.1009 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-2 | K.B.CROSS | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247969 | 800/1 | 4.9886 | 0
B.1010 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | Bank 1 | K.G.Temple | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252712 | 1200/1 | 8.8332 | 0
B.1011 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | Bank 2 | K.G.Temple | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252584 | 800/1 | 5.9378 | 0
B.1012 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | NITTUR | BANK-1 | KADABA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252964 | 600/1 | 6.5716 | 0
B.1013 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | NITTUR | BANK-2 | KADABA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252848 | 1200/1 | 9.854 | 0
| CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-1 | KARADI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008273 | 800/1 | 3.1891 | 0
B.1014 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-1 | KADEHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247853 | 800/1 | 3.4263 | 0
B.1015 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-2 | KADEHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247962 | 800/1 | 4.3136 | 0
B.1016 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-1 | KALLAMBELLA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252805 | 1200/1 | 9.2447 | 0
B.1017 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-2 | KALLAMBELLA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252792 | 1200/1 | 13.4023 | 0
B.1018 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | BANK-1 | KALLUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247556 | 1200/1 | 13.2139 | 0
B.1019 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | Bank-2 | KALLUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247555 | 800/1 | 7.5043 | 0
B.1020 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | Bank-1 | KATHRIKEHAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247674 | 800/1 | 3.8814 | 0
| CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | Bank-1 | KATHRIKEHAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247674 | 800/1 | 0 | -0.5048
B.1021 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | BANK-1 | KEMPANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258495 | 400/1 | 3.6569 | 0
B.1022 | BRAZ | RAMANAGAR | 66/11 kV | RAMANAGAR | BIDADI | BANK-2 | KEMPANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258495 | 400/1 | 3.9215 | 0
B.1023 | CTAZ | TUMKUR | 66/11 kV | TIPTUR | TIPTUR | BANK-1 | KEREGODI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247794 | 800/1 | 4.1882 | 0
B.1024 | BRAZ | BANGALORE RURAL | 66/11 KV | NELAMANGALA | DODDABALAPURA (U) | BANK-1 | KIADB(Vasantha Narasapura) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | XE486637 | 1200/1-1-1A | 0.7141 | 0
| BRAZ | BANGALORE RURAL | 66/11 KV | NELAMANGALA | DODDABALAPURA (U) | BANK-1 | KIADB(Vasantha Narasapura) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | XE486637 | 1200/1-1-1A | 0 | -0.0069
B.1025 | BRAZ | BANGALORE RURAL | 66/11 KV | NELAMANGALA | DODDABALAPURA (U) | BANK-2 | KIADB(Vasantha Narasapura) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | XE486000 | 1200/1 | 11.7226 | 0
| BRAZ | BANGALORE RURAL | 66/11 KV | NELAMANGALA | DODDABALAPURA (U) | BANK-2 | KIADB(Vasantha Narasapura) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | XE486000 | 1200/1 | 0 | 0
B.1026 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KODIGENAHALLY | BANK-1 | KODIGENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248108 | 800/1 | 4.7773 | 0
B.1027 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KODIGENAHALLY | BANK-2 | KODIGENAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248145 | 800/1 | 5.5781 | 0
B.1028 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KORATAGERE | BANK-1 | KOLALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252974 | 800/1 | 4.986 | 0
B.1029 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KORATAGERE | BANK 2 | KOLALA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252829 | 800/1 | 7.8041 | 0
| BRAZ | BANGALORE RURAL | 66/11 kV | Hoskote | AVALAHALLY | BANK-1 | Konasagara | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 21001922 | 800/1 | 1.398 | 0
B.1030 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK-1 | KORA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253034 | 600/1 | 3.1697 | 0
B.1031 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK 2 | KORA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252982 | 1200/1 | 4.0766 | 0
B.1032 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK 3 | KORA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252844 | 1200/1 | 15.5436 | 0
B.1033 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KORATAGERE | BANK-1 | KORATAGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252743 | 1200/1 | 7.6912 | 0
B.1034 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KORATAGERE | BANK-2 | KORATAGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO253033 | 800/1 | 7.093 | 0
B.1035 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KORATAGERE | BANK-3 | KORATAGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO252765 | 1200/1 | 4.7417 | 0
| CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KORATAGERE | BANK-4 | KORATAGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18128559 | 800/1 | 3.2947 | 0
B.1036 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | KUNIGAL_RA | BANK-1 | KUNIGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247730 | 1200/1 | 8.1578 | 0
B.1037 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | KUNIGAL_RA | BANK-2 | KUNIGAL | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247733 | 1200/1 | 5.8453 | 0
B.1038 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-1 | LINGADAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248043 | 400/1 | 5.5355 | 0
B.1039 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | CHANNAGIRI | BANK-2 | LINGADAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248156 | 400/1 | 3.9726 | 0
B.1040 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | BANK-1 | MADHUGIRI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248158 | 800/1 | 5.7598 | 0
B.1041 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | BANK-2 | MADHUGIRI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247996 | 800/1 | 6.6983 | 0
B.1042 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | Bank-1 | MADHUGIRI(NEW) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248153 | 800/1 | 4.2168 | 0
B.1043 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | bank-2 | MADHUGIRI(NEW) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248014 | 800/1 | 2.4555 | 0
B.1044 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-1 | MALLASANDRA(TUMKUR) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252944 | 800/1 | 8.5705 | 0
B.1045 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | BANK-2 | MALLASANDRA(TUMKUR) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252949 | 800/1 | 5.928 | 0
B.1046 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-1 | MANGALAVADA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248003 | 800/1 | 5.5295 | 0
B.1047 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-2 | MANGALAVADA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247998 | 600/1 | 7.8478 | 0
B.1048 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-1 | MAYASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247879 | 800/1 | 3.3119 | 0
B.1049 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK 2 | MAYASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247894 | 800/1 | 7.6022 | 0
B.1050 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK 3 | MAYASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247854 | 800/1 | 6.6943 | 0
B.1051 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-1 | MELEKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO259936 | 1200/1 | 13.2966 | 0
B.1052 | CTAZ | DAVANAGERE | 66/11 kV | DAVANAGERE | ANAGODU | BANK-2 | MELEKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | QO259930 | 1200/1 | 15.2464 | 0
B.1053 | BRAZ | KOLAR | 66/11 kV | CHINTHAMANI | CHINTHAMANI RURAL | BANK - 1 | MIDIGESHI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247990 | 800/1 | 6.0483 | 0
| CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | BANK-1 | NANDIHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20001203 | 800/1 | 3.3698 | 0
B.1054 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-1 | NAGALAMADIKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248069 | 600/1 | 1.1327 | 0
B.1055 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-1 | NAGALAMADIKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248069 | 600/1 | 0 | -1.0025
B.1056 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-2 | NAGALAMADIKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247995 | 600/1 | 2.6951 | 0
B.1057 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-3 | NAGALAMADIKE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16195295 | 800/1 | 3.0706 | 0
B.1058 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | HULIYURDURGA | BANK-1 | NIDASALE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247749 | 400/1 | 2.999 | 0
B.1059 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KODIGENAHALLY | BANK-1 | NITRAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248005 | 600/1 | 4.3973 | 0
B.1060 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KODIGENAHALLY | BANK-2 | NITRAHALLI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248143 | 800/1 | 4.5458 | 0
B.1061 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | NITTUR | BANK-1 | NITTUR(220KV RS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252793 | 1200/1 | 10.91 | 0
B.1062 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | NITTUR | BANK-2 | NITTUR(220KV RS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252703 | 1200/1 | 7.7282 | 0
B.1063 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | NITTUR | BANK-3 | NITTUR(220KV RS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252834 | 1200/1 | 4.288 | 0
| CTAZ | TUMKUR | 110/11 kV | TUMKUR | NITTUR | BANK-4 | NITTUR(220KV RS) | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18093092 | 1200/1 | 1.2987 | 0
B.1064 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-1 | NONAVINAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247840 | 1200/1 | 4.5509 | 0
B.1065 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-2 | NONAVINAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247809 | 600/1 | 4.8293 | 0
B.1066 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK-1 | PATTANAYAKANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252564 | 800/1 | 4.4353 | 0
B.1067 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK-2 | PATTANAYAKANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252729 | 800/1 | 5.5226 | 0
B.1068 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-1 | PAVAGADA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248163 | 800/1 | 2.1542 | 0
B.1069 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-2 | PAVAGADA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248167 | 800/1 | 11.1011 | 0
B.1070 | CTAZ | TUMKUR | 220/66/11 kV | MADHUGIRI | PAVAGADA | BANK-1 | PAVAGADA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 14196207 | 800/1 | 2.9 | 0
B.1071 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | BANK-1 | PULAMAGHATTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248102 | 600/1 | 4.697 | 0
B.1072 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | MADHUGIRI | BANK-2 | PULAMAGHATTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248171 | 600/1 | 3.7221 | 0
B.1073 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KODIGENAHALLY | BANK-1 | PURAVARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17031101 | 400/1 | 2.9792 | 0
| CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KODIGENAHALLY |  | PURAVARA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 21003418 | 400/1 | 0.6792 | 0
B.1074 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-1 | SAMPIGE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252958 | 600/1 | 5.2632 | 0
B.1075 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-2 | SAMPIGE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252991 | 600/1 | 8.7916 | 0
| CTAZ | TUMKUR | 110/11 kV | KUNIGAL | HULIYURDURGA | BANK-1 | SANABHAGHATTTA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q047496 | 400/1 | 0.0138 | 0
B.1076 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | HULIYURDURGA | BANK 1 | SANTHEMAVATHURU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247741 | 800/1 | 4.5554 | 0
B.1077 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | HULIYURDURGA | BANK 2 | SANTHEMAVATHURU | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247726 | 400/1 | 3.9255 | 0
B.1078 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-1 | SHAILAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247681 | 800/1 | 5.4369 | 0
B.1079 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-2 | SHAILAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247688 | 800/1 | 5.4582 | 0
B.1080 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-3 | SHAILAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16083130 | 800/1 | 1.5011 | 0
B.1081 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-3 | SHAILAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16083130 | 800/1 | 0 | -0.044
B.1082 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | BANK-1 | SHETTYKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Qo247850 | 600/1 | 4.4011 | 0
B.1083 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | BANK-2 | SHETTYKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Qo248095 | 600/1 | 4.9748 | 0
B.1084 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK-1 | SIRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0259923 | 1200/1 | 6.3072 | 0
B.1085 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK-2 | SIRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253015 | 1200/1 | 8.5921 | 0
B.1086 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK-3 | SIRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252832 | 800/1 | 6.9762 | 0
B.1087 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA URBAN | BANK-3 | SIRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252832 | 800/1 | 0 | -0.00232
B.1088 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | NITTUR | BANK-1 | SOMALAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252775 | 600/1 | 5.9538 | 0
| CTAZ | TUMKUR | 110/11 kV | TUMKUR | NITTUR | BANK-2 | SOMALAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 20009735 | 1200/1 | 2.771 | 0
B.1089 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-1 | THALKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247842 | 600/1 | 3.6418 | 0
| CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-2 | THALKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479574 | 800/1 | 3.04 | 0
| CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-2 | THALKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0479574 | 800/1 | 0 | 0
B.1090 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-1 | TAVAREKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253529 | 600/1 | 7.5232 | 0
B.1091 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | SIRA RURAL | BANK-2 | TAVAREKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0253549 | 600/1 | 3.7891 | 0
B.1092 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | KODIGENAHALLY | BANK-1 | TERIYUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18088422 | 800/1 | 2.634 | 0
B.1093 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-1 | THANDAGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247756 | 800/1 | 3.9895 | 0
| CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-2 | THANDAGA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247756 | 800/1 | 1.0987 | 0
B.1094 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | Bank-1 | THIMMANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Qo247843 | 800/1 | 5.8338 | 0
B.1095 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | CN HALLY | Bank-2 | THIMMANAHALLY | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247802 | 800/1 | 5.2542 | 0
B.1096 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | Bank-1 | THIMMASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247591 | 800/1 | 4.4788 | 0
B.1097 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION2 | Bank-2 | THIMMASANDRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247703 | 800/1 | 3.914 | 0
B.1098 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | MAGADI | BANK-1 | THOVINAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252954 | 1200/1 | 7.1028 | 0
B.1099 | BRAZ | RAMANAGAR | 66/11 kV | MAGADI | MAGADI | BANK-2 | THOVINAKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252975 | 800/1 | 6.2564 | 0
B.1100 | CTAZ | TUMKUR | 66/11 kV | TIPTUR | TIPTUR | BANK-1 | TIPPUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 18053951 | 400/1 | 2.7771 | 0
B.1101 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-1 | TIPTUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247953 | 800/1 | 6.1057 | 0
B.1102 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-2 | TIPTUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247877 | 800/1 | 5.2035 | 0
B.1103 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TIPTUR | BANK-3 | TIPTUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | KAU04744 | 800/1 | 2.1244 | 0
| CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK-1 | TMTP | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19001111 | 2000-1200/1-1-1 | 0.02 | 0
| CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BANK-2 | TMTP | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 16110542 | 2000-1200/1-1-1 | 0.04 | 0
B.1104 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR URBAN SUB DIVISION1 | BANK-1 | TUMKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252715 | 800/1 | 12.8443 | 0
B.1105 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | TUMKUR URBAN SUB DIVISION1 | BANK-2 | TUMKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252655 | 800/1 | 14.4554 | 0
B.1106 | CTAZ | TUMKUR | 66/11 KV | TUMKUR | TUMKUR URBAN SUB DIVISION1 | BANK-3 | TUMKUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 19008199 | 1200/1 | 0 | 0
B.1107 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-1 | TURUVEKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247786 | 800/1 | 3.8078 | 0
B.1108 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-2 | TURUVEKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247873 | 800/1 | 3.4334 | 0
B.1109 | CTAZ | TUMKUR | 110/11 kV | TIPTUR | TURUVEKERE | BANK-3 | TURUVEKERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247863 | 800/1 | 6.9809 | 0
B.1110 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | Bank-1 | UNGRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258937 | 600/1 | 6.2362 | 0
B.1111 | CTAZ | TUMKUR | 110/11 kV | TUMKUR | GUBBI | Bank-2 | UNGRA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0258989 | 600/1 | 6.833 | 0
B.1112 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | KYATSANDRA | BANK-1 | URDIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252851 | 600/1 | 3.6315 | 0
B.1113 | CTAZ | TUMKUR | 66/11 kV | TUMKUR | KYATSANDRA | BANK-2 | URDIGERE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0252749 | 600/1 | 3.6211 | 0
B.1114 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-1 | VENKATAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248027 | 300/1 | 0.32784 | 0
B.1115 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-1 | VENKATAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248027 | 300/1 | 0 | -2.0709
B.1116 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-2 | VENKATAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248146 | 600/1 | 1.4232 | 0
B.1117 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-2 | VENKATAPURA | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248146 | 600/1 | 0 | -0.52386
B.1118 | CTAZ | TUMKUR | 110/11 kV | KUNIGAL | HULIYURDURGA | BANK-1 | YADAVANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247689 | 600/1 | 2.0453 | 0
B.1119 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | HULIYURDURGA | BANK-2 | YADAVANI | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | 17125650 | 800/1 | 3.2367 | 0
B.1120 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-1 | Y.N.HOSAKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q248129 | 800/1 | 3.5311 | 0
B.1121 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-1 | Y.N.HOSAKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q248129 | 800/1 | 0 | -0.46872
B.1122 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-2 | Y.N.HOSAKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248121 | 800/1 | 3.8961 | 0
B.1123 | CTAZ | TUMKUR | 66/11 kV | MADHUGIRI | PAVAGADA | BANK-2 | Y.N.HOSAKOTE | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0248121 | 800/1 | 0 | -0.22152
B.1124 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | YEDIYUR | BANK-1 | YEDIYUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247586 | 600/1 | 2.7205 | 0
B.1125 | CTAZ | TUMKUR | 66/11 kV | KUNIGAL | YEDIYUR | BANK-2 | YEDIYUR | Metered/DLMS | Functional | 1st of Every month | Bank |  |  |  | Q0247648 | 600/1 | 4.2091 | 0
b | Total (MU) | [15 empty] | 9315.2262 | -31.9293
c | EHT consumtion | [15 empty] | 750.4158
d | IPP at 11KV | [15 empty] | 88.707
e | IPP import energy from BESCOM ( 66KV & above | [15 empty] | 4.8648
f | Auxillary consumption | [15 empty] | 5.2744
g | Wheeled Energy | [15 empty] | 1155.7897
h | Open access consumption above 66 kV | [15 empty] | 7.326
i | Open access consumption above 11 kV | [15 empty] | 1.9386
J | SRTPV | [15 empty] | 13.8128
Input Energy=b+d+e-g-h-I +j | [16 empty] | 8970.7685 | Net input energy at DISCOM periphery (MU)
Color code | Parameter
Please enter voltage level or leave blank
Please enter feeder id and name or leave blank
Enter meter no or leave blank
Enter CT/PT ratio or leave blank
0 | Please enter numeric value or 0
Please select yes or no from list
Formula protected
I/we undertake that the information supplied in this document and pro-forma is accurate to the best of my knowledge and if any of the information supplied is found to be incorrect and such information result into loss to the Central Government or State Government or any of the authority under them or any other person affected,I/we undertake to indemnify such loss.
Authorised Signatory and Seal
Signature
Name Of the authorised signatory CGM (Operations)
Name of the Discom:BESCOM | [15 empty] | Name of the Energy Manager/Auditor : Sri Basavaraju .H .B
Full Address:- KR circle, Nrupathunga Rd, Nunegundlapalli, Ambedkar Veedhi, Bengaluru, Karnataka 560001 | [15 empty] | Registration Number : |  | 6827

## Detailed of received source
Details of Input Energy Sources
Period From….To.…
A. Generation at Transmission Periphery (Details)
S.No. | Name of Generation Station | Generation Capacity (In MW) | Type of Station Generation (Based- Solid ( Coal ,Lignite)/Liquid/Gas/Renewable ( biomass- bagasse)/Others) | Type of Contract (in years/months/days) | Type of Grid (Intra-state/Inter-state) | Point of Connection (POC) Loss MU | Voltage Level ( At input) | Remarks (Source of data)
1 | NTPC RSTPS | 174.6781 | Thermal | 25 Years | Inter state | Pertains to PGCIL. Details not availabe in BESCOM | NA | *NA-Not available
2 | NTPC TALCHER | 44.375 | Thermal | 25 Years | Inter state |  | NA
3 | NTPC SR - III | 164.7589 | Thermal | 25 Years | Inter state |  | NA
4 | NTPC SR - Simhadri | 87.0175 | Thermal | 25 Years | Inter state |  | NA
5 | NTPC Kudgi | 574.0576 | Thermal | 25 Years | Inter state |  | NA
6 | NLC TPS - I Expansion | 51.0166 | Thermal | 25 Years | Inter state |  | NA
7 | NLC TPS - II Expansion | 68.8587 | Thermal | 25 Years | Inter state |  | NA
8 | NLC TS II-Stage-I | 46.5872 | Thermal | 25 Years | Inter state |  | NA
9 | NLC TS II-Stage-II | 46.5872 | Thermal | 25 Years | Inter state |  | NA
10 | MAPS | 16.1337 | Atomic | 25 Years | Inter state |  | NA
11 | Kaiga-UNIT I & II, III & IV | 124.4462 | Atomic | 25 Years | Inter state |  | NA
12 | NTPL | 87.723 | Thermal | 25 Years | Inter state |  | NA
13 | Vallur | 72.669 | Thermal | 25 Years | Inter state |  | NA
14 | Kudankulam | 201.2398 | Atomic | 25 Years | Inter state |  | NA
15 | Damodar valley Corporation | 215.9483 | Thermal | 25 Years | Inter state |  | NA
16 | Jurala | 112.581 | HYDEL | 25 Years | Inter state |  | NA
17 | TBHE |  | HYDEL | 25 Years | Inter state |  | NA
18 | NTPC NVVN Bundled power | 33.5919 | Bundled power | 25 Years | Inter state |  | NA
19 | NTPC NSM Bundled power |  | Bundled power | 25 Years | Inter state |  | NA
20 | [5 empty] | NA | NA
21 | UPCL (Major IPP) | 716.16 | Thermal | 25 Years | Inter state | NA | NA
22 | KPCL |  |  |  |  | NA | NA
23 | MGHE JOGFALLS | 523.0747 | Hydel | 25 Years | Intra state | NA | NA
24 | SHIVASAMUDRAM | 20.1552 | Hydel | 25 Years | Intra state | NA | NA
25 | MUNIRABAD | 13.4368 | Hydel | 25 Years | Intra state | NA | NA
26 | SHIMSHA | 8.254 | Hydel | 25 Years | Intra state | NA | NA
27 | Sharavathi Valley Project | 14.6191 | Hydel | 25 Years | Intra state | NA | NA
28 | Kali Valley Project | 1.6464 | Hydel | 25 Years | Intra state | NA | NA
29 | Varahi Valley Project | 38.9571 | Hydel | 25 Years | Intra state | NA | NA
30 | Kadra Power House | 11.0374 | Hydel | 25 Years | Intra state | NA | NA
31 | Kodasalli Dam Power House | 1.5356 | Hydel | 25 Years | Intra state | NA | NA
32 | Gerusoppa Power House | 7.1983 | Hydel | 25 Years | Intra state | NA | NA
33 | Ghataprabha | 5.7586 | Hydel | 25 Years | Intra state | NA | NA
34 | Bhadra Power House | 11.5172 | Hydel | 25 Years | Intra state | NA | NA
35 | Almatti Dam power house | 8.6379 | Hydel | 25 Years | Intra state | NA | NA
36 | RTPS UNIT I to 7 | 768.3881 | Thermal | 25 Years | Intra state | NA | NA
37 | RTPS UNIT 8 | 119.9712 | Thermal | 25 Years | Intra state | NA | NA
38 | BTPS-Unit I | 239.9425 | Thermal | 25 Years | Intra state | NA | NA
39 | BTPS-Unit II | 239.9425 | Thermal | 25 Years | Intra state | NA | NA
40 | BTPS-Unit III | 335.9195 | Thermal | 25 Years | Intra state | NA | NA
41 | RPCL | 767.816 | Thermal | 25 Years | Intra state | NA | NA
42 | KPCL Solar | 3 | Solar | 25 Years | Intra state | NA | NA
43 | Kappadaguddu-Unit-I & II | 7.5 | Wind | 25 Years | Intra state | NA | NA
44 |  |  |  |  | Intra state | NA | NA
45 | NON CONVENTIONAL ENERGY |  |  |  | Intra state | NA | NA
46 |  |  | Biomass: |  | Intra state | NA | NA
47 | Konark Power Project | 7.5 |  | 20 years | Intra state | NA | NA
48 | R.K.Power Gen | 20 |  | 20 years | Intra state | NA | NA
49 | Samson Distallaries | 3 |  | 20 years | Intra state | NA | NA
50 | BERI-1 | 1.5 |  | 20 years | Intra state | NA | NA
51 | Haveri Bio Energy | 10 |  | 20 years | Intra state | NA | NA
52 | Dharwad Bio Energy | 10 |  | 20 years | Intra state | NA | NA
53 | Raichur Bio Energy | 10 |  | 20 years | Intra state | NA | NA
54 | Sai Spurthi Power Pvt Ltd. | 10.25 | MINI-HYDEL | 20 years | Intra state | NA | NA
55 | IPCL | 18 |  | 20 years | Intra state | NA | NA
56 | Atria-Shivasamudram | 6.6 |  | 20 years | Intra state | NA | NA
57 | Atria-Shimsha | 18 |  | 20 years | Intra state | NA | NA
58 | Atria-Shimsha addl unit | 6 |  | 20 years | Intra state | NA | NA
59 | POINEER GENCO LTD | 24.75 |  | 20 years | Intra state | NA | NA
60 | Poineer Power Corporation Ltd | 24.75 |  | 20 years | Intra state | NA | NA
61 | Paschim Hydro Energy Pvt Ltd | 9 |  | 20 years | Intra state | NA | NA
62 | Trinethra Energy Convertions ltd | 4.5 |  | 20 years | Intra state | NA | NA
63 | Prasanna Power Ltd | 6 |  | 20 years | Intra state | NA | NA
64 | Rithwik Energy Generation Pvt Ltd | 24 |  | 20 years | Intra state | NA | NA
65 | Dishaa Power Corpn Pvt Ltd | 4.8 |  | 20 years | Intra state | NA | NA
66 | Krishna hydro energy ltd | 24.75 |  | 20 years | Intra state | NA | NA
67 | Shilpa Medicare | 0.46 | WIND | 20 years | Intra state | NA | NA
68 | Kamal Trading | 0.23 |  | 20 years | Intra state | NA | NA
69 | VXL System - II | 0.23 |  | 20 years | Intra state | NA | NA
70 | VXL System - I | 0.23 |  | 20 years | Intra state | NA | NA
71 | Patel Shanti Steels | 0.23 |  | 20 years | Intra state | NA | NA
72 | Sharp Pumps | 0.23 |  | 20 years | Intra state | NA | NA
73 | Friend Associate | 0.23 |  | 20 years | Intra state | NA | NA
74 | RSM Autokast | 0.46 |  | 20 years | Intra state | NA | NA
75 | Rajanikanth Foundation | 0.23 |  | 20 years | Intra state | NA | NA
76 | Mayura Steels | 0.23 |  | 20 years | Intra state | NA | NA
77 | NuziveeduSeeds[NSL-5] | 1.9 |  | 20 years | Intra state | NA | NA
78 | NuziveeduSeeds[NSL-6,7,8&9] | 9 |  | 20 years | Intra state | NA | NA
79 | NuziveeduSeeds[NSL-2&3] | 10.5 |  | 20 years | Intra state | NA | NA
80 | NuziveeduSeeds[NSL-1-4] | 6.75 |  | 20 years | Intra state | NA | NA
81 | NuziveeduSeeds(3&4) | 24.75 |  | 20 years | Intra state | NA | NA
82 | NuziveeduSeeds (5&6)25.5 | 25.5 |  | 20 years | Intra state | NA | NA
83 | Texmo Precision | 1.2 |  | 20 years | Intra state | NA | NA
84 | Raja Magnetics | 0.6 |  | 20 years | Intra state | NA | NA
85 | Royal Energy | 0.6 |  | 20 years | Intra state | NA | NA
86 | Fiza Developers | 1.2 |  | 20 years | Intra state | NA | NA
87 | Panama Business | 0.6 |  | 20 years | Intra state | NA | NA
88 | Suttatti Enterprises | 1.2 |  | 20 years | Intra state | NA | NA
89 | Cepco Industries (1.2MW) | 0.6 |  | 20 years | Intra state | NA | NA
90 | Ghodawat Industries | 5.4 |  | 20 years | Intra state | NA | NA
91 | Siddaganga Oil Extractions(1.2MW) | 1.2 |  | 20 years | Intra state | NA | NA
92 | Supreme Power | 0.6 |  | 20 years | Intra state | NA | NA
93 | Relience Energy (1.8MW) | 1.8 |  | 20 years | Intra state | NA | NA
94 | Panama Credit & Capital | 0.6 |  | 20 years | Intra state | NA | NA
95 | Balasaheb.M.Ladkhant | 0.6 |  | 20 years | Intra state | NA | NA
96 | Shilpa Medicare (0.6MW) | 0.6 |  | 20 years | Intra state | NA | NA
97 | Texmo Industries | 1.8 |  | 20 years | Intra state | NA | NA
98 | Jindal Aluminium (6.6MW) | 6.6 |  | 20 years | Intra state | NA | NA
99 | Mohit & Mohit | 2.4 |  | 20 years | Intra state | NA | NA
100 | Shriram City Union | 1.8 |  | 20 years | Intra state | NA | NA
101 | Shriram Transport | 4.2 |  | 20 years | Intra state | NA | NA
102 | Shriram Investment | 4.2 |  | 20 years | Intra state | NA | NA
103 | Dee Dee Enterprises | 0.6 |  | 20 years | Intra state | NA | NA
104 | Topaz Investment (1.2MW) | 1.2 |  | 20 years | Intra state | NA | NA
105 | Enercon Wind (Ktk) | 21 |  | 20 years | Intra state | NA | NA
106 | Cepco Industries (8.4MW) | 8.4 |  | 20 years | Intra state | NA | NA
107 | Topaz Investment (0.6MW) | 0.6 |  | 20 years | Intra state | NA | NA
108 | Dee Dee enterprises (0.6MW) | 0.6 |  | 20 years | Intra state | NA | NA
109 | Enercon Wind | 8.4 |  | 20 years | Intra state | NA | NA
110 | JN Investment | 0.6 |  | 20 years | Intra state | NA | NA
111 | Lovelly Fragrances | 0.6 |  | 20 years | Intra state | NA | NA
112 | Ghodawat Industries(5.4MW) | 5.4 |  | 20 years | Intra state | NA | NA
113 | Sanjay D Ghodawat (HUF) | 0.6 |  | 20 years | Intra state | NA | NA
114 | Shraddha Constructions | 6.6 |  | 20 years | Intra state | NA | NA
115 | Sanjay D Ghodawat (Individual)(0.6MW) | 0.6 |  | 20 years | Intra state | NA | NA
116 | VXL System | 0.6 |  | 20 years | Intra state | NA | NA
117 | Cepco Industries (0.6MW) | 1.2 |  | 20 years | Intra state | NA | NA
118 | BSC Textiles - I | 0.6 |  | 20 years | Intra state | NA | NA
119 | Deffree Power | 0.6 |  | 20 years | Intra state | NA | NA
120 | Siddaganga Oil Extractions(VVS) | 1.2 |  | 20 years | Intra state | NA | NA
121 | BSC Textiles - II | 0.6 |  | 20 years | Intra state | NA | NA
122 | B.S.Channabasappa-2 | 0.6 |  | 20 years | Intra state | NA | NA
123 | Meghna Automotives | 0.6 |  | 20 years | Intra state | NA | NA
124 | Patel shanthi - I | 0.6 |  | 20 years | Intra state | NA | NA
125 | P.Vijay Kumar | 0.6 |  | 20 years | Intra state | NA | NA
126 | Mohan Lal | 0.6 |  | 20 years | Intra state | NA | NA
127 | Primetex Apparels | 0.6 |  | 20 years | Intra state | NA | NA
128 | Laxmi Organic | 1.2 |  | 20 years | Intra state | NA | NA
129 | Cooper Foundry Ltd | 2.4 |  | 20 years | Intra state | NA | NA
130 | Rohit Surfactants pvt Ltd | 6 |  | 20 years | Intra state | NA | NA
131 | Minerals Enterprises | 3 |  | 20 years | Intra state | NA | NA
132 | World Institute | 1.2 |  | 20 years | Intra state | NA | NA
133 | BS Channabasaapa-I | 0.6 |  | 20 years | Intra state | NA | NA
134 | Unnathi Projects - I | 0.6 |  | 20 years | Intra state | NA | NA
135 | Jitendra D Majethia | 0.6 |  | 20 years | Intra state | NA | NA
136 | Patel shanthi - II | 0.6 |  | 20 years | Intra state | NA | NA
137 | Brindavan Agro Industries | 1.2 |  | 20 years | Intra state | NA | NA
138 | Gem Crafts | 0.6 |  | 20 years | Intra state | NA | NA
139 | S.E.Investment Ltd | 2.4 |  | 20 years | Intra state | NA | NA
140 | Unnathi Projects - II | 1.8 |  | 20 years | Intra state | NA | NA
141 | Sanjana Power | 1.8 |  | 20 years | Intra state | NA | NA
142 | International Conveyors | 0.6 |  | 20 years | Intra state | NA | NA
143 | Swaraj PVC Pipes | 0.6 |  | 20 years | Intra state | NA | NA
144 | Sanjay D Ghodawat (HUF) (0.6MW) | 0.6 |  | 20 years | Intra state | NA | NA
145 | I.G.E India Ltd | 0.6 |  | 20 years | Intra state | NA | NA
146 | Shilpa Medicare (1.2MW) | 1.2 |  | 20 years | Intra state | NA | NA
147 | Amrit Bottlers | 1.2 |  | 20 years | Intra state | NA | NA
148 | M.K.Agrotech | 1.2 |  | 20 years | Intra state | NA | NA
149 | Associate Autotex | 1.2 |  | 20 years | Intra state | NA | NA
150 | Good Luck Syndicate | 0.6 |  | 20 years | Intra state | NA | NA
151 |  | 4.2 |  | 20 years | Intra state | NA | NA
152 | Star Flexi Pack | 0.6 |  | 20 years | Intra state | NA | NA
153 | Shreyalaxmi | 0.6 |  | 20 years | Intra state | NA | NA
154 | Abhishek Export | 1.25 |  | 20 years | Intra state | NA | NA
155 | Rajesh Constructions | 2.5 |  | 20 years | Intra state | NA | NA
156 | Sanjana Power | 1.25 |  | 20 years | Intra state | NA | NA
157 | Jivraj Tea | 1.25 |  | 20 years | Intra state | NA | NA
158 | Gangadhar | 2.5 |  | 20 years | Intra state | NA | NA
159 | Ferromar | 1.25 |  | 20 years | Intra state | NA | NA
160 | Kariganur | 2.5 |  | 20 years | Intra state | NA | NA
161 | Amitronics Pvt Ltd | 1.25 |  | 20 years | Intra state | NA | NA
162 | Mantri Developers | 3.75 |  | 20 years | Intra state | NA | NA
163 | Navalakha Translines | 1.25 |  | 20 years | Intra state | NA | NA
164 | MSPL - I(SUZLON) | 6.25 |  | 20 years | Intra state | NA | NA
165 | MSPL-II(SUZLON) | 1.25 |  | 20 years | Intra state | NA | NA
166 | MSPL-III(SUXLON) | 3.75 |  | 20 years | Intra state | NA | NA
167 | Vandana Ispat Ltd | 2.5 |  | 20 years | Intra state | NA | NA
168 | Lanco Infratech | 3 |  | 20 years | Intra state | NA | NA
169 | Prabhat Agri Biotech Ltd | 0.75 |  | 20 years | Intra state | NA | NA
170 | Savitha Chemicals | 0.75 |  | 20 years | Intra state | NA | NA
171 | Manipal Health Systems | 3.75 |  | 20 years | Intra state | NA | NA
172 | Prime Lables - I | 0.25 |  | 20 years | Intra state | NA | NA
173 | Prime Lables - II | 0.64 |  | 20 years | Intra state | NA | NA
174 | Fair deal | 3.25 |  | 20 years | Intra state | NA | NA
175 | MSPL - I | 0.95 |  | 20 years | Intra state | NA | NA
176 | MSPL - II | 4.75 |  | 20 years | Intra state | NA | NA
177 | MSPL-III | 3.8 |  | 20 years | Intra state | NA | NA
178 | MSPL - IV | 5.3 |  | 20 years | Intra state | NA | NA
179 | MSPL - V | 3.75 |  | 20 years | Intra state | NA | NA
180 | MSPL - VI | 3.8 |  | 20 years | Intra state | NA | NA
181 | MSPL - VII | 2.85 |  | 20 years | Intra state | NA | NA
182 | MSPL - VIII | 1.9 |  | 20 years | Intra state | NA | NA
183 | Ramgad Minerals - I | 1.9 |  | 20 years | Intra state | NA | NA
184 | Ramgad Minerals - II | 0.75 |  | 20 years | Intra state | NA | NA
185 | Sanghvi Movers | 0.75 |  | 20 years | Intra state | NA | NA
186 | Suresh Production | 0.75 |  | 20 years | Intra state | NA | NA
187 | Eshwari Knitting | 3 |  | 20 years | Intra state | NA | NA
188 | Eshwari Textiles | 3 |  | 20 years | Intra state | NA | NA
189 | Eshwari Garments | 3 |  | 20 years | Intra state | NA | NA
190 | Victus Associate | 1.5 |  | 20 years | Intra state | NA | NA
191 | Bellary Iron Ores PVT Ltd-Gonur-II(GRHP-17) | 0.95 |  | 20 years | Intra state | NA | NA
192 | Shanmuga Compact. | 0.75 |  | 20 years | Intra state | NA | NA
193 | Indan Energy | 0.75 |  | 20 years | Intra state | NA | NA
194 | Elveety Industries | 0.5 |  | 20 years | Intra state | NA | NA
195 | Kariganur (0.75MW) | 0.75 |  | 20 years | Intra state | NA | NA
196 | Pallavi Green Power | 0.75 |  | 20 years | Intra state | NA | NA
197 | Jindal Aluminium (1.9MW) | 1.9 |  | 20 years | Intra state | NA | NA
198 | Mansukhmal | 0.95 |  | 20 years | Intra state | NA | NA
199 | Savitha Chemicals(9.8MW) | 3.8 |  | 20 years | Intra state | NA | NA
200 | Bellary Iron Ores PVT Ltd-Gonur-III(GRHP-24) | 0.95 |  | 20 years | Intra state | NA | NA
201 | Maris Power Supply-I (4.5MW) | 4.5 |  | 20 years | Intra state | NA | NA
202 | Maris Power Supply-II(0.75MW) | 0.75 |  | 20 years | Intra state | NA | NA
203 | S.Kumar | 0.95 |  | 20 years | Intra state | NA | NA
204 | Savitha Chemicals | 1.9 |  | 20 years | Intra state | NA | NA
205 | Bellad & Company | 0.95 |  | 20 years | Intra state | NA | NA
206 | Indan Energy Private Ltd | 0.95 |  | 20 years | Intra state | NA | NA
207 | Bhoruka Power Corpn Ltd | 2 |  | 20 years | Intra state | NA | NA
208 | Bellary Iron Ores PVT Ltd-I(2 MW)(PDR-02) | 2.5 |  | 20 years | Intra state | NA | NA
209 | Sanmati power Co. | 0.5 |  | 20 years | Intra state | NA | NA
210 | Mineral Enterpriese | 2.4 |  | 20 years | Intra state | NA | NA
211 | CBM CORPORATION | 0.8 |  | 20 years | Intra state | NA | NA
212 | Abletech Electro Engineers Pvt. Ltd. | 1.6 |  | 20 years | Intra state | NA | NA
213 | Mysore Mercantile | 4.8 |  | 20 years | Intra state | NA | NA
214 | MSPL-VI | 5 |  | 20 years | Intra state | NA | NA
215 | MSPL-VII | 16.25 |  | 20 years | Intra state | NA | NA
216 | Ramgad Minerals & Mining-III | 3.75 |  | 20 years | Intra state | NA | NA
217 | Ramgad Minerals & Mining-IV | 17.5 |  | 20 years | Intra state | NA | NA
218 | MSPL-IV(SUZLON) | 13.75 |  | 20 years | Intra state | NA | NA
219 | MSPL-V(SUZLON) | 11.25 |  | 20 years | Intra state | NA | NA
220 | Ramgad Minerals & Mining-I(SUZLON) | 10 |  | 20 years | Intra state | NA | NA
221 | Ramgad Minerals & Mining-II(SUZLON) | 7.5 |  | 20 years | Intra state | NA | NA
222 | Venganna Setty & Bros(suzlon) | 7.5 |  | 20 years | Intra state | NA | NA
223 | KRDEL SOGI | 2.5 |  | 20 years | Intra state | NA | NA
224 | Mavinahonda | 2 |  | 20 years | Intra state | NA | NA
225 | VSL Mining Company 1 | 6.25 |  | 20 years | Intra state | NA | NA
226 | VSL Mining Company 2 | 2.5 |  | 20 years | Intra state | NA | NA
227 | VS Lad and Sons | 3.75 |  | 20 years | Intra state | NA | NA
228 | Mahalaxmi Commercial Services | 1.25 |  | 20 years | Intra state | NA | NA
229 | Siddayu Ayurvedic Research Foundation | 2.5 |  | 20 years | Intra state | NA | NA
230 | Mark data Power & Energy (P) Ltd | 1.25 |  | 20 years | Intra state | NA | NA
231 | Allegro Venture | 1.25 |  | 20 years | Intra state | NA | NA
232 | Enercon Wind Farms( Krishna) | 17.4 |  | 20 years | Intra state | NA | NA
233 | EnerconWindFarms(Krishna) | 2.4 |  | 20 years | Intra state | NA | NA
234 | Enercon Wind Farms( KARNATAKA) | 3.2 |  | 20 years | Intra state | NA | NA
235 | R.D.S.Construction | 0.8 |  | 20 years | Intra state | NA | NA
236 | Neharaj Energy | 0.8 |  | 20 years | Intra state | NA | NA
237 | Jubliee Textile Mills | 0.8 |  | 20 years | Intra state | NA | NA
238 | Avanti Feeds Ltd | 3.2 |  | 20 years | Intra state | NA | NA
239 | Srinivasa Cystine | 1.6 |  | 20 years | Intra state | NA | NA
240 | B.V.Finance & Leasing | 1.6 |  | 20 years | Intra state | NA | NA
241 | Brindavan Agro Industries Ltd | 3.2 |  | 20 years | Intra state | NA | NA
242 | Vandana Rolling Mills Ltd | 0.8 |  | 20 years | Intra state | NA | NA
243 | R.S.Suriya | 0.8 |  | 20 years | Intra state | NA | NA
244 | Vandana Global Ltd | 0.8 |  | 20 years | Intra state | NA | NA
245 | Vivek Trading | 0.8 |  | 20 years | Intra state | NA | NA
246 | Mahalaxmi Construction Corpn Ltd | 0.8 |  | 20 years | Intra state | NA | NA
247 | Amrit Bottlers Pvt Ltd | 0.8 |  | 20 years | Intra state | NA | NA
248 | Vivek Pharmachem (India ) Ltd | 0.8 |  | 20 years | Intra state | NA | NA
249 | M/s Indian Power Corporation-1 | 2.4 |  | 20 years | Intra state | NA | NA
250 | M/s Indian Power Corporation-2 | 4.8 |  | 20 years | Intra state | NA | NA
251 | M/s Prasad Technology Park Ltd | 1.6 |  | 20 years | Intra state | NA | NA
252 | M/s Unnathi Projects | 0.8 |  | 20 years | Intra state | NA | NA
253 | M/s Mumbai Stock Brokers Pvt Ltd | 0.8 |  | 20 years | Intra state | NA | NA
254 | M/s D.R. Container Terminal | 1.6 |  | 20 years | Intra state | NA | NA
255 | M/s Panama Infrastructure | 1.6 |  | 20 years | Intra state | NA | NA
256 | M/s Sameer Ladkat | 0.8 |  | 20 years | Intra state | NA | NA
257 | M/s Indian Power Corporation-3 | 3.2 |  | 20 years | Intra state | NA | NA
258 | M/s Ramco Industries Ltd | 1.6 |  | 20 years | Intra state | NA | NA
259 | M/s Elpro International Ltd | 0.8 |  | 20 years | Intra state | NA | NA
260 | M/s Cauvery Coffee Traders | 0.8 |  | 20 years | Intra state | NA | NA
261 | M/s M.K.Agrotech Pvt Ltd | 1.6 |  | 20 years | Intra state | NA | NA
262 | M/s Siddaganga Oil Extractions | 1.6 |  | 20 years | Intra state | NA | NA
263 | M/s Panama Business Centre | 1.6 |  | 20 years | Intra state | NA | NA
264 | M/s Balasaheb M Ladkat | 1.6 |  | 20 years | Intra state | NA | NA
265 | M/s Goutam Ladkat | 0.8 |  | 20 years | Intra state | NA | NA
266 | Gem Crafts-1 | 0.8 |  | 20 years | Intra state | NA | NA
267 | Gem Crafts-2 | 0.8 |  | 20 years | Intra state | NA | NA
268 | Enercon Wind Farms(Chitradurga) | 8.8 |  | 20 years | Intra state | NA | NA
269 | Globe Transports Company | 1.25 |  | 20 years | Intra state | NA | NA
270 | V.M.Salgaocar & Brothers Pvt Ltd | 3.75 |  | 20 years | Intra state | NA | NA
271 | Vandana Global Ltd | 1.25 |  | 20 years | Intra state | NA | NA
272 | Indian Wind Energy Association | 1.25 |  | 20 years | Intra state | NA | NA
273 | Triveni Enterprises | 1.25 |  | 20 years | Intra state | NA | NA
274 | Research Developers & MFG Corporation | 1.25 |  | 20 years | Intra state | NA | NA
275 | BSK Trading INK | 1.25 |  | 20 years | Intra state | NA | NA
276 | Shakambari Enterprises | 1.25 |  | 20 years | Intra state | NA | NA
277 | Praveen Chandra | 1.25 |  | 20 years | Intra state | NA | NA
278 | Ensemble Infrastructure | 1.25 |  | 20 years | Intra state | NA | NA
279 | Visva Visal Engineering Ltd | 1.25 |  | 20 years | Intra state | NA | NA
280 | Nava Bharat International Ltd | 1.25 |  | 20 years | Intra state | NA | NA
281 | Ramesh Kumar Hanjarimal Rathod | 1.25 |  | 20 years | Intra state | NA | NA
282 | PraveenChandra(K245) | 1.25 |  | 20 years | Intra state | NA | NA
283 | Hutti Gold Mines | 10.8 |  | 20 years | Intra state | NA | NA
284 | Enercon Wind Farms(Hindustan) | 56.8 |  | 20 years | Intra state | NA | NA
285 | Enercon Wind Farms(Hindustan) | 12 |  | 20 years | Intra state | NA | NA
286 | Rangamma Steel & Malleables | 0.8 |  | 20 years | Intra state | NA | NA
287 | Sree Devi Chemicals | 0.8 |  | 20 years | Intra state | NA | NA
288 | Triveni Enterprises | 0.8 |  | 20 years | Intra state | NA | NA
289 | Texmo Precision Casting | 1.6 |  | 20 years | Intra state | NA | NA
290 | Happy Valley Developers | 0.8 |  | 20 years | Intra state | NA | NA
291 | U.D.Foundation | 0.8 |  | 20 years | Intra state | NA | NA
292 | Texonic Instruments | 0.8 |  | 20 years | Intra state | NA | NA
293 | Protectron Electromech(P) Ltd | 0.8 |  | 20 years | Intra state | NA | NA
294 | VXL Systems | 0.8 |  | 20 years | Intra state | NA | NA
295 | Ranka-N-Ranka | 5 |  | 20 years | Intra state | NA | NA
296 | AccionWindEnergyPvtLtd | 13.2 |  | 20 years | Intra state | NA | NA
297 | IndoWindEnergyLtd | 10.5 |  | 20 years | Intra state | NA | NA
298 | IndoWindEnergyLtd | 7.5 |  | 20 years | Intra state | NA | NA
299 | AllamVeerabhadrappa | 1.5 |  | 20 years | Intra state | NA | NA
300 | VSLadandSons | 3 |  | 20 years | Intra state | NA | NA
301 | VSLMiningCo.PVTLtd | 1.5 |  | 20 years | Intra state | NA | NA
302 | Sameera Trading Company | 1.5 |  | 20 years | Intra state | NA | NA
303 | Gangadhar Narasingdas | 10.5 |  | 20 years | Intra state | NA | NA
304 | Eastman International | 1.5 |  | 20 years | Intra state | NA | NA
305 | Ramesh Steels | 1.5 |  | 20 years | Intra state | NA | NA
306 | Rita International | 1.5 |  | 20 years | Intra state | NA | NA
307 | Belgaum Wind Farms Pvt Ltd | 24.8 |  | 20 years | Intra state | NA | NA
308 | Green infra energy Ltd | 36.3 |  | 20 years | Intra state | NA | NA
309 | Green infra energy Ltd | 23.1 |  | 20 years | Intra state | NA | NA
310 | Accion Wind Energy Pvt Ltd | 16.5 |  | 20 years | Intra state | NA | NA
311 | Tata power(25.6MW) | 25.6 |  | 20 years | Intra state | NA | NA
312 | Tata power(24.8MW) | 24.8 |  | 20 years | Intra state | NA | NA
313 | ICSA | 1.5 |  | 20 years | Intra state | NA | NA
314 | ICSA | 1.5 |  | 20 years | Intra state | NA | NA
315 | Leo fasteners | 3 |  | 20 years | Intra state | NA | NA
316 | Leo fasteners | 3 |  | 20 years | Intra state | NA | NA
317 | Sargam Retails Pvt Ltd | 6.25 |  | 20 years | Intra state | NA | NA
318 | Sargam Retails Pvt Ltd | 7.5 |  | 20 years | Intra state | NA | NA
319 | D.J.Malpani | 3 |  | 20 years | Intra state | NA | NA
320 | Gangadhar Narsingdas Agarwal | 3 |  | 20 years | Intra state | NA | NA
321 | Ferromar Shipping Pvt.Ltd | 1.5 |  | 20 years | Intra state | NA | NA
322 | Gangadhar Narsingdas Agarwal | 1.5 |  | 20 years | Intra state | NA | NA
323 | Sriram EPC | 1.35 |  | 20 years | Intra state | NA | NA
324 | NMDC | 9 |  | 20 years | Intra state | NA | NA
325 | P.Venganna Shetty | 1.25 |  | 20 years | Intra state | NA | NA
326 | Ramgad Minerals & Mining Ltd-III | 5 |  | 20 years | Intra state | NA | NA
327 | Super Wind Project(P) Ltd-Phase 6 | 1.5 |  | 20 years | Intra state | NA | NA
328 | Super Wind Project(P) Ltd-Phase 7 | 1.5 |  | 20 years | Intra state | NA | NA
329 | Super Wind Project(P) Ltd-Phase 8 | 1.5 |  | 20 years | Intra state | NA | NA
330 | Simran Wind Project(P)Ltd-Phase 3 | 1.5 |  | 20 years | Intra state | NA | NA
331 | Simran Wind Project(P)Ltd-Phase 4 | 1.5 |  | 20 years | Intra state | NA | NA
332 | Energy Developement Company Ltd | 1.5 |  | 20 years | Intra state | NA | NA
333 | Deepak Cables | 2.5 |  | 20 years | Intra state | NA | NA
334 | CLP Wind Farms(India)Pvt Ltd | 1.25 |  | 20 years | Intra state | NA | NA
335 | Sree Minerals | 1.5 |  | 20 years | Intra state | NA | NA
336 | Gautham Freight | 4.5 |  | 20 years | Intra state | NA | NA
337 | Hira Ferro Alloys Ltd | 1.5 |  | 20 years | Intra state | NA | NA
338 | Abhishek Export(India) Pvt Ltd | 2.5 |  | 20 years | Intra state | NA | NA
339 | H.G.Rangan Goud | 1.25 |  | 20 years | Intra state | NA | NA
340 | Sunvik Steels Pvt Ltd | 10 |  | 20 years | Intra state | NA | NA
341 | NMDC | 1.5 |  | 20 years | Intra state | NA | NA
342 | PTC India Financial Services Ltd(Phase-1) | 1.5 |  | 20 years | Intra state | NA | NA
343 | PTC India Financial Services Ltd(Phase-2) | 4.5 |  | 20 years | Intra state | NA | NA
344 | Vish Wind Infrastructure LLP | 6.4 |  | 20 years | Intra state | NA | NA
345 | SRB Consultancy Pvt Ltd | 1.5 |  | 20 years | Intra state | NA | NA
346 | SRB Consultancy Pvt Ltd | 1.5 |  | 20 years | Intra state | NA | NA
347 | CLP Wind Farms (India) Pvt Ltd | 39.6 |  | 20 years | Intra state | NA | NA
348 | EN Renewable Energy Ltd | 11.2 |  | 20 years | Intra state | NA | NA
349 | EN Renewable Energy Ltd | 39.2 |  | 20 years | Intra state | NA | NA
350 | Protectron | 1.6 |  | 20 years | Intra state | NA | NA
351 | Ramgad Minerals & Mining Ltd-III | 1.25 |  | 20 years | Intra state | NA | NA
352 | Ramgad Minerals & Mining Ltd-III | 2.5 |  | 20 years | Intra state | NA | NA
353 | M/s Vikram Traders | 2.1 |  | 20 years | Intra state | NA | NA
354 | M/s Vikram Traders | 2.1 |  | 20 years | Intra state | NA | NA
355 | Sterling Agro industries | 2.5 |  | 20 years | Intra state | NA | NA
356 | Srinivasa Hatcheries | 2.5 |  | 20 years | Intra state | NA | NA
357 | Vish Wind Infrastructure LLP 1.6 | 1.6 |  | 20 years | Intra state | NA | NA
358 | Mytrah Vayu (Krishna) Phase-5 IDIPP-12) | 15.3 |  | 20 years | Intra state | NA | NA
359 | Mytrah Vayu (Krishna) Phase-4 IDIPP-11) | 17.85 |  | 20 years | Intra state | NA | NA
360 | Mytrah Vayu (Krishna) Phase-3 IDIPP-10) | 16.15 |  | 20 years | Intra state | NA | NA
361 | Mytrah Vayu (Krishna) Phase-2 IDIPP-09) | 17 |  | 20 years | Intra state | NA | NA
362 | Mytrah Vayu (Krishna) Phase-1 IDIPP-08) | 11.05 |  | 20 years | Intra state | NA | NA
363 | Mytrah Vayu (Krishna) Phase-6 IDIPP-13) | 17.85 |  | 20 years | Intra state | NA | NA
364 | Bharat Petroleum Corporation Ltd (HTPBP-13) | 2.1 | Wnd | 20 years | Intra state | NA | NA
365 | Bharat Petroleum Corporation Ltd (HTPBP-18) | 4.2 | Wnd | 20 years | Intra state | NA | NA
366 | Green infrawind energy AssociationSemb corp | 44 | Wnd | 20 years | Intra state | NA | NA
367 | Sunphoto volataic | 60 | Wnd | 20 years | Intra state | NA | NA
368 | Atri Power Wind Bijapur 2 Pvt ltd | 23.3 | Wnd | 20 years | Intra state | NA | NA
369 | Aikyam holdings | 8 | Wnd | 20 years | Intra state | NA | NA
370 | Poonavala HTP 10 | 8.4 | Wnd | 20 years | Intra state | NA | NA
371 | Poonavala HTP 28 | 8.4 | Wnd | 20 years | Intra state | NA | NA
372 | Poonavala HTP 55 | 6.3 | Wnd | 20 years | Intra state | NA | NA
373 | Serum Institute of India | 2.1 | Wnd | 20 years | Intra state | NA | NA
374 | Sanchore Renewabls | 40 | Wnd | 20 years | Intra state | NA | NA
375 | Renewwind varekarwadi | 40 | Wnd | 20 years | Intra state | NA | NA
376 | Ananthara Enterprises | 2 | Wnd | 20 years | Intra state | NA | NA
377 | Protectron Electromech(P) Ltd | 2 | Wnd | 20 years | Intra state | NA | NA
378 | Serum Institute of India | 4.2 | Wnd | 20 years | Intra state | NA | NA
379 | Serum Institute of India | 2.1 | Wnd | 20 years | Intra state | NA | NA
380 | Serum Institute of India | 2.1 | Wnd | 20 years | Intra state | NA | NA
381 | [5 empty] | NA | NA
382 | Jindal Aluminium Ltd Solar | 10 | Solar | 25 years | Intra state | NA | NA
383 | United Telecoms Limited | 3 | Solar | 25 years | Intra state | NA | NA
384 | United Surya Energy | 3 | Solar | 25 years | Intra state | NA | NA
385 | BhorukaPowerCorporation (Solar) | 10 | Solar | 25 years | Intra state | NA | NA
386 | Azure Power Karnataka | 10 | Solar | 25 years | Intra state | NA | NA
387 | Azure Power India | 10 | Solar | 25 years | Intra state | NA | NA
388 | SECI | 10 | Solar | 25 years | Intra state | NA | NA
389 | SECI | 480 | Solar | 25 years | Intra state | NA | NA
390 | Welspun 34 Mw | 34 | Solar | 25 years | Intra state | NA | NA
391 | Welspun 16 Mw | 16 | Solar | 25 years | Intra state | NA | NA
392 | Welspun 50 Mw | 50 | Solar | 25 years | Intra state | NA | NA
393 | Photo Surka kiran | 10 | Solar | 25 years | Intra state | NA | NA
394 | Asian Fab Tech | 10 | Solar | 25 years | Intra state | NA | NA
395 | Asian Fab tech Sira, | 15 | Solar | 25 years | Intra state | NA | NA
396 | Sei Aditi | 30 | Solar | 25 years | Intra state | NA | NA
397 | Sei Bheem | 30 | Solar | 25 years | Intra state | NA | NA
398 | Sei Diamond | 30 | Solar | 25 years | Intra state | NA | NA
399 | Suryashakthi | 30 | Solar | 25 years | Intra state | NA | NA
400 | Mallagi Education 1.00 Mw | 1 | Solar | 25 years | Intra state | NA | NA
401 | VR Patil vidyut Nirman Ltd | 3 | Solar | 25 years | Intra state | NA | NA
402 | Samyama Jyothi Solar | 3 | Solar | 25 years | Intra state | NA | NA
403 | SGTRS Solar | 3 | Solar | 25 years | Intra state | NA | NA
404 | Sharanagowda Solar | 1 | Solar | 25 years | Intra state | NA | NA
405 | Skylet Power | 1 | Solar | 25 years | Intra state | NA | NA
406 | Sri Sai Shivanagere Solar | 1 | Solar | 25 years | Intra state | NA | NA
407 | Suragi Power | 2 | Solar | 25 years | Intra state | NA | NA
408 | Ramavari Power | 1 | Solar | 25 years | Intra state | NA | NA
409 | Prathiba Solar | 1 | Solar | 25 years | Intra state | NA | NA
410 | Chandragiri Power & Infra | 1 | Solar | 25 years | Intra state | NA | NA
411 | Guttur Solar Power | 1 | Solar | 25 years | Intra state | NA | NA
412 | HaLO energy MHHECL 51 | 2 | Solar | 25 years | Intra state | NA | NA
413 | HaLO energy MHHECL 50 | 2 | Solar | 25 years | Intra state | NA | NA
414 | HaLO energy MHHECL 52 | 2 | Solar | 25 years | Intra state | NA | NA
415 | Janakshi renewable Energy | 2 | Solar | 25 years | Intra state | NA | NA
416 | PV Power | 1 | Solar | 25 years | Intra state | NA | NA
417 | Ramapriya Solar | 1 | Solar | 25 years | Intra state | NA | NA
418 | Prema vijayendra | 1 | Solar | 25 years | Intra state | NA | NA
419 | P somachandra Consol energy | 3 | Solar | 25 years | Intra state | NA | NA
420 | ADC power | 3 | Solar | 25 years | Intra state | NA | NA
421 | Niketan Solar | 3 | Solar | 25 years | Intra state | NA | NA
422 | Ahaskar Arya Solar | 1 | Solar | 25 years | Intra state | NA | NA
423 | Rangadhol Solar Power | 1 | Solar | 25 years | Intra state | NA | NA
424 | Rayappa poojari | 1 | Solar | 25 years | Intra state | NA | NA
425 | Burnish Solar | 1 | Solar | 25 years | Intra state | NA | NA
426 | Scald Energy Pvt ltd | 1 | Solar | 25 years | Intra state | NA | NA
427 | BLDE Association | 3 | Solar | 25 years | Intra state | NA | NA
428 | BLDE University | 3 | Solar | 25 years | Intra state | NA | NA
429 | Kumars Energy | 3 | Solar | 25 years | Intra state | NA | NA
430 | Saleems Enegy | 3 | Solar | 25 years | Intra state | NA | NA
431 | Mulgund Energy | 3 | Solar | 25 years | Intra state | NA | NA
432 | Arete Elena | 2 | Solar | 25 years | Intra state | NA | NA
433 | Venkat energy | 2 | Solar | 25 years | Intra state | NA | NA
434 | Mepgen solar | 2 | Solar | 25 years | Intra state | NA | NA
435 | Sunishka Solar | 1 | Solar | 25 years | Intra state | NA | NA
436 | Rajpet Energy | 1 | Solar | 25 years | Intra state | NA | NA
437 | Sowhil Energy | 3 | Solar | 25 years | Intra state | NA | NA
438 | Panchakshari Power | 1 | Solar | 25 years | Intra state | NA | NA
439 | LRK Solar | 2 | Solar | 25 years | Intra state | NA | NA
440 | LPD Solar | 2 | Solar | 25 years | Intra state | NA | NA
441 | V carve | 1 | Solar | 25 years | Intra state | NA | NA
442 | Blister Solar (Krishna naik) | 2 | Solar | 25 years | Intra state | NA | NA
443 | Scorch Solar (Kamalabai) | 3 | Solar | 25 years | Intra state | NA | NA
444 | tacholine renewable (A Savitha) | 3 | Solar | 25 years | Intra state | NA | NA
445 | T. Vijayakumar | 1 | Solar | 25 years | Intra state | NA | NA
446 | Flaunt Solar Energy (Lakkshmamma) | 3 | Solar | 25 years | Intra state | NA | NA
447 | Cambria solar (gangaraju) | 3 | Solar | 25 years | Intra state | NA | NA
448 | Torrid Solar | 2 | Solar | 25 years | Intra state | NA | NA
449 | Alles Solar Pvt Ltd | 1 | Solar | 25 years | Intra state | NA | NA
450 | Spangle (shashidhara) | 2 | Solar | 25 years | Intra state | NA | NA
451 | R Gayathri Solar | 2 | Solar | 25 years | Intra state | NA | NA
452 | Poorvaj Solar | 3 | Solar | 25 years | Intra state | NA | NA
453 | T Gowranna | 1 | Solar | 25 years | Intra state | NA | NA
454 | Chowdeshwari Solar | 1 | Solar | 25 years | Intra state | NA | NA
455 | Aadyaarush Power | 2 | Solar | 25 years | Intra state | NA | NA
456 | Sri Ugrappa | 2 | Solar | 25 years | Intra state | NA | NA
457 | hunsakodihalli (pallavi S) | 3 | Solar | 25 years | Intra state | NA | NA
458 | Saakesha solar | 1 | Solar | 25 years | Intra state | NA | NA
459 | MNR solar (manjunatha k.t) | 2 | Solar | 25 years | Intra state | NA | NA
460 | Chennamanagathihalli Solar | 3 | Solar | 25 years | Intra state | NA | NA
461 | Hirehalli Solar (vyaramudi) | 3 | Solar | 25 years | Intra state | NA | NA
462 | Chikkahalli Solar H V Chaudary | 3 | Solar | 25 years | Intra state | NA | NA
463 | Vatsala Bellary | 2 | Solar | 25 years | Intra state | NA | NA
464 | Swelter energy (Anjinamma) | 1 | Solar | 25 years | Intra state | NA | NA
465 | Insolexo pvt ltd | 3 | Solar | 25 years | Intra state | NA | NA
466 | manjunath R kabadi | 1 | Solar | 25 years | Intra state | NA | NA
467 | Jayamal Energy | 2 | Solar | 25 years | Intra state | NA | NA
468 | Murali M Baladev | 3 | Solar | 25 years | Intra state | NA | NA
469 | Lakshmamma | 1 | Solar | 25 years | Intra state | NA | NA
470 | Shuun Solar | 3 | Solar | 25 years | Intra state | NA | NA
471 | H Ramanjaneya | 3 | Solar | 25 years | Intra state | NA | NA
472 | RJR Solar | 3 | Solar | 25 years | Intra state | NA | NA
473 | Mandidurgappa | 1 | Solar | 25 years | Intra state | NA | NA
474 | Renew Wind Energy - GIPP-13 | 20 | Solar | 25 years | Intra state | NA | NA
475 | Renew Wind Energy - GIPP-17 | 20 | Solar | 25 years | Intra state | NA | NA
476 | Tarun Kiran Bhoomi | 20 | Solar | 25 years | Intra state | NA | NA
477 | Jindal Aluminium Ltd Solar | 10 | Solar | 25 years | Intra state | NA | NA
478 | GRT Jewellers | 20 | Solar | 25 years | Intra state | NA | NA
479 | Clean Solar madhugiri | 20 | Solar | 25 years | Intra state | NA | NA
480 | Clean Solar Tumkur | 20 | Solar | 25 years | Intra state | NA | NA
481 | ES Sun power Pvt ltd | 20 | Solar | 25 years | Intra state | NA | NA
482 | ES Solar Pvt ltd | 10 | Solar | 25 years | Intra state | NA | NA
483 | Chirasthayi Saurya | 20 | Solar | 25 years | Intra state | NA | NA
484 | Chirasthayi Saurya | 10 | Solar | 25 years | Intra state | NA | NA
485 | Adani green enegy holenarasipura | 20 | Solar | 25 years | Intra state | NA | NA
486 | Adani green enegy K R pet | 20 | Solar | 25 years | Intra state | NA | NA
487 | Growth Street solar | 4 | Solar | 25 years | Intra state | NA | NA
488 | Renew Wind Rajasthan Four | 20 | Solar | 25 years | Intra state | NA | NA
489 | Renew Wind MP Three | 20 | Solar | 25 years | Intra state | NA | NA
490 | Adani green enegy Tiptur | 20 | Solar | 25 years | Intra state | NA | NA
491 | Mytrah Advaith | 15 | Solar | 25 years | Intra state | NA | NA
492 | Asian Fab tech Alakapur, gowribidnur | 20 | Solar | 25 years | Intra state | NA | NA
493 | Asian Fab tech kavalahalli, Doddaballapur | 10 | Solar | 25 years | Intra state | NA | NA
494 | Asian Fab tech thirumalapur, nagamangala | 15 | Solar | 25 years | Intra state | NA | NA
495 | Renew wind energy Maharashtra | 20 | Solar | 25 years | Intra state | NA | NA
496 | Kodangal Solar park | 20 | Solar | 25 years | Intra state | NA | NA
497 | KN Bijapura Solar energy | 20 | Solar | 25 years | Intra state | NA | NA
498 | KN Indi Vijayapura Solar energy | 20 | Solar | 25 years | Intra state | NA | NA
499 | Adani Green energy Gubbi tq | 20 | Solar | 25 years | Intra state | NA | NA
500 | Aditya birla solar ltd | 20 | Solar | 25 years | Intra state | NA | NA
501 | Brics renewable energy pvt ltd | 2 | Solar | 25 years | Intra state | NA | NA
502 | Adani Green energy Ramanagara tq | 20 | Solar | 25 years | Intra state | NA | NA
503 | Avanthi renewable energy pvt ltd | 20 | Solar | 25 years | Intra state | NA | NA
504 | NVR Renew Pvt Ltd | 20 | Solar | 25 years | Intra state | NA | NA
505 | Azure power Earth | 50 | Solar | 25 years | Intra state | NA | NA
506 | Aadya solar Block 1 | 50 | Solar | 25 years | Intra state | NA | NA
507 | Aadya solar Block 2 | 50 | Solar | 25 years | Intra state | NA | NA
508 | Aadya solar Block 3 | 50 | Solar | 25 years | Intra state | NA | NA
509 | Aadya solar Block 6 | 50 | Solar | 25 years | Intra state | NA | NA
510 | Tata power 15 | 50 | Solar | 25 years | Intra state | NA | NA
511 | Tata power 17 | 50 | Solar | 25 years | Intra state | NA | NA
512 | Tata power 18 | 50 | Solar | 25 years | Intra state | NA | NA
513 | Fortum b5 | 50 | Solar | 25 years | Intra state | NA | NA
514 | Fortum B9 | 50 | Solar | 25 years | Intra state | NA | NA
515 | Taletuttayi | 20 | Solar | 25 years | Intra state | NA | NA
516 | Asia fab tech , Arasikere | 10 | Solar | 25 years | Intra state | NA | NA
517 | ACME Kittur Solar Energy Pvt ltd | 15 | Solar | 25 years | Intra state | NA | NA
518 | ACME Sidlaghatta Solar Energy Pvt ltd | 15 | Solar | 25 years | Intra state | NA | NA
519 | ACME Guledagudda Solar Energy Pvt ltd | 20 | Solar | 25 years | Intra state | NA | NA
520 | radiance Solar Pvt ltd | 20 | Solar | 25 years | Intra state | NA | NA
521 | Asia fab tech , Doddaballapur | 20 | Solar | 25 years | Intra state | NA | NA
522 | Asian fab tec Chintamani | 5 | Solar | 25 years | Intra state | NA | NA
523 | Nokar Renew power Bailahongal | 20 | Solar | 25 years | Intra state | NA | NA
524 | Asian fab tec KGF Taluk | 20 | Solar | 25 years | Intra state | NA | NA
525 | Asian fab tec Gudibande | 20 | Solar | 25 years | Intra state | NA | NA
526 | Asian Fab tec Bangarpete | 20 | Solar | 25 years | Intra state | NA | NA
527 | Akilagya | 20 | Solar | 25 years | Intra state | NA | NA
528 | Acme Kudligi | 20 | Solar | 25 years | Intra state | NA | NA
B. Embedded Generation in DISCOM Area
| S.No | Name of Generation Station | Generation Capacity (In MW) | Tytpe of Station (Generation Based-Solid/Liquid/Gas/Renewable/Others) | Type of Contract | Type of Grid | Voltage Level (KVA) | Circle Load (MW) | Received at Circle (KVA) | Received at Circle (In MU) | Division Level Load (MW) | Received at Division Level (KVA) | Received at Division Level (In MU) | Sub-Division Level Load (MW) | Received at Sub-Division Level (KVA) | Received at Sub-Division Level (In MU) | Remarks (Source of data)
| 1 | NTPC RSTPS | 174.6781 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA | *NA-Not Available
| 2 | NTPC TALCHER | 44.375 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 3 | NTPC SR - III | 164.7589 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 4 | NTPC SR - Simhadri | 87.0175 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 5 | NTPC Kudgi | 574.0576 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 6 | NLC TPS - I Expansion | 51.0166 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 7 | NLC TPS - II Expansion | 68.8587 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 8 | NLC TS II-Stage-I | 46.5872 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 9 | NLC TS II-Stage-II | 46.5872 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 10 | MAPS | 16.1337 | Atomic | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 11 | Kaiga-UNIT I & II, III & IV | 124.4462 | Atomic | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 12 | NTPL | 87.723 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 13 | Vallur | 72.669 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 14 | Kudankulam | 201.2398 | Atomic | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 15 | Damodar valley Corporation | 215.9483 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 16 | Jurala | 112.581 | HYDEL | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 17 | TBHE |  | HYDEL | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 18 | NTPC NVVN Bundled power | 33.5919 | Bundled power | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 19 | NTPC NSM Bundled power |  | Bundled power | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 20 | UPCL (Major IPP) | 716.16 | Thermal | 25 Years | Inter state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 21 | KPCL |  |  |  |  | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 22 | MGHE JOGFALLS | 523.0747 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 23 | SHIVASAMUDRAM | 20.1552 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 24 | MUNIRABAD | 13.4368 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 25 | SHIMSHA | 8.254 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 26 | Sharavathi Valley Project | 14.6191 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 27 | Kali Valley Project | 1.6464 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 28 | Varahi Valley Project | 38.9571 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 29 | Kadra Power House | 11.0374 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 30 | Kodasalli Dam Power House | 1.5356 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 31 | Gerusoppa Power House | 7.1983 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 32 | Ghataprabha | 5.7586 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 33 | Bhadra Power House | 11.5172 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 34 | Almatti Dam power house | 8.6379 | Hydel | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 35 | RTPS UNIT I to 7 | 768.3881 | Thermal | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 36 | RTPS UNIT 8 | 119.9712 | Thermal | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 37 | BTPS-Unit I | 239.9425 | Thermal | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 38 | BTPS-Unit II | 239.9425 | Thermal | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 39 | BTPS-Unit III | 335.9195 | Thermal | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 40 | RPCL | 767.816 | Thermal | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 41 | KPCL Solar | 3 | Solar | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 42 | Kappadaguddu-Unit-I & II | 7.5 | Wind | 25 Years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 43 | NON CONVENTIONAL ENERGY |  |  |  | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 44 | Konark Power Project | 7.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 45 | R.K.Power Gen | 20 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 46 | Samson Distallaries | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 47 | BERI-1 | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 48 | Haveri Bio Energy | 10 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 49 | Dharwad Bio Energy | 10 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 50 | Raichur Bio Energy | 10 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 51 | Sai Spurthi Power Pvt Ltd. | 10.25 | MINI-HYDEL | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 52 | IPCL | 18 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 53 | Atria-Shivasamudram | 6.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 54 | Atria-Shimsha | 18 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 55 | Atria-Shimsha addl unit | 6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 56 | POINEER GENCO LTD | 24.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 57 | Poineer Power Corporation Ltd | 24.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 58 | Paschim Hydro Energy Pvt Ltd | 9 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 59 | Trinethra Energy Convertions ltd | 4.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 60 | Prasanna Power Ltd | 6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 61 | Rithwik Energy Generation Pvt Ltd | 24 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 62 | Dishaa Power Corpn Pvt Ltd | 4.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 63 | Krishna hydro energy ltd | 24.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 64 | Shilpa Medicare | 0.46 | WIND | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 65 | Kamal Trading | 0.23 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 66 | VXL System - II | 0.23 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 67 | VXL System - I | 0.23 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 68 | Patel Shanti Steels | 0.23 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 69 | Sharp Pumps | 0.23 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 70 | Friend Associate | 0.23 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 71 | RSM Autokast | 0.46 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 72 | Rajanikanth Foundation | 0.23 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 73 | Mayura Steels | 0.23 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 74 | NuziveeduSeeds[NSL-5] | 1.9 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 75 | NuziveeduSeeds[NSL-6,7,8&9] | 9 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 76 | NuziveeduSeeds[NSL-2&3] | 10.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 77 | NuziveeduSeeds[NSL-1-4] | 6.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 78 | NuziveeduSeeds(3&4) | 24.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 79 | NuziveeduSeeds (5&6)25.5 | 25.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 80 | Texmo Precision | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 81 | Raja Magnetics | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 82 | Royal Energy | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 83 | Fiza Developers | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 84 | Panama Business | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 85 | Suttatti Enterprises | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 86 | Cepco Industries (1.2MW) | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 87 | Ghodawat Industries | 5.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 88 | Siddaganga Oil Extractions(1.2MW) | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 89 | Supreme Power | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 90 | Relience Energy (1.8MW) | 1.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 91 | Panama Credit & Capital | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 92 | Balasaheb.M.Ladkhant | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 93 | Shilpa Medicare (0.6MW) | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 94 | Texmo Industries | 1.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 95 | Jindal Aluminium (6.6MW) | 6.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 96 | Mohit & Mohit | 2.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 97 | Shriram City Union | 1.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 98 | Shriram Transport | 4.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 99 | Shriram Investment | 4.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 100 | Dee Dee Enterprises | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 101 | Topaz Investment (1.2MW) | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 102 | Enercon Wind (Ktk) | 21 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 103 | Cepco Industries (8.4MW) | 8.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 104 | Topaz Investment (0.6MW) | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 105 | Dee Dee enterprises (0.6MW) | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 106 | Enercon Wind | 8.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 107 | JN Investment | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 108 | Lovelly Fragrances | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 109 | Ghodawat Industries(5.4MW) | 5.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 110 | Sanjay D Ghodawat (HUF) | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 111 | Shraddha Constructions | 6.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 112 | Sanjay D Ghodawat (Individual)(0.6MW) | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 113 | VXL System | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 114 | Cepco Industries (0.6MW) | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 115 | BSC Textiles - I | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 116 | Deffree Power | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 117 | Siddaganga Oil Extractions(VVS) | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 118 | BSC Textiles - II | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 119 | B.S.Channabasappa-2 | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 120 | Meghna Automotives | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 121 | Patel shanthi - I | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 122 | P.Vijay Kumar | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 123 | Mohan Lal | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 124 | Primetex Apparels | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 125 | Laxmi Organic | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 126 | Cooper Foundry Ltd | 2.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 127 | Rohit Surfactants pvt Ltd | 6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 128 | Minerals Enterprises | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 129 | World Institute | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 130 | BS Channabasaapa-I | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 131 | Unnathi Projects - I | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 132 | Jitendra D Majethia | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 133 | Patel shanthi - II | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 134 | Brindavan Agro Industries | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 135 | Gem Crafts | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 136 | S.E.Investment Ltd | 2.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 137 | Unnathi Projects - II | 1.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 138 | Sanjana Power | 1.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 139 | International Conveyors | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 140 | Swaraj PVC Pipes | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 141 | Sanjay D Ghodawat (HUF) (0.6MW) | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 142 | I.G.E India Ltd | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 143 | Shilpa Medicare (1.2MW) | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 144 | Amrit Bottlers | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 145 | M.K.Agrotech | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 146 | Associate Autotex | 1.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 147 | Good Luck Syndicate | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 148 |  | 4.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 149 | Star Flexi Pack | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 150 | Shreyalaxmi | 0.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 151 | Abhishek Export | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 152 | Rajesh Constructions | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 153 | Sanjana Power | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 154 | Jivraj Tea | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 155 | Gangadhar | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 156 | Ferromar | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 157 | Kariganur | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 158 | Amitronics Pvt Ltd | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 159 | Mantri Developers | 3.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 160 | Navalakha Translines | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 161 | MSPL - I(SUZLON) | 6.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 162 | MSPL-II(SUZLON) | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 163 | MSPL-III(SUXLON) | 3.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 164 | Vandana Ispat Ltd | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 165 | Lanco Infratech | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 166 | Prabhat Agri Biotech Ltd | 0.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 167 | Savitha Chemicals | 0.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 168 | Manipal Health Systems | 3.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 169 | Prime Lables - I | 0.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 170 | Prime Lables - II | 0.64 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 171 | Fair deal | 3.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 172 | MSPL - I | 0.95 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 173 | MSPL - II | 4.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 174 | MSPL-III | 3.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 175 | MSPL - IV | 5.3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 176 | MSPL - V | 3.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 177 | MSPL - VI | 3.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 178 | MSPL - VII | 2.85 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 179 | MSPL - VIII | 1.9 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 180 | Ramgad Minerals - I | 1.9 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 181 | Ramgad Minerals - II | 0.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 182 | Sanghvi Movers | 0.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 183 | Suresh Production | 0.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 184 | Eshwari Knitting | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 185 | Eshwari Textiles | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 186 | Eshwari Garments | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 187 | Victus Associate | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 188 | Bellary Iron Ores PVT Ltd-Gonur-II(GRHP-17) | 0.95 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 189 | Shanmuga Compact. | 0.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 190 | Indan Energy | 0.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 191 | Elveety Industries | 0.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 192 | Kariganur (0.75MW) | 0.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 193 | Pallavi Green Power | 0.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 194 | Jindal Aluminium (1.9MW) | 1.9 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 195 | Mansukhmal | 0.95 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 196 | Savitha Chemicals(9.8MW) | 3.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 197 | Bellary Iron Ores PVT Ltd-Gonur-III(GRHP-24) | 0.95 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 198 | Maris Power Supply-I (4.5MW) | 4.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 199 | Maris Power Supply-II(0.75MW) | 0.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 200 | S.Kumar | 0.95 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 201 | Savitha Chemicals | 1.9 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 202 | Bellad & Company | 0.95 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 203 | Indan Energy Private Ltd | 0.95 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 204 | Bhoruka Power Corpn Ltd | 2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 205 | Bellary Iron Ores PVT Ltd-I(2 MW)(PDR-02) | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 206 | Sanmati power Co. | 0.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 207 | Mineral Enterpriese | 2.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 208 | CBM CORPORATION | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 209 | Abletech Electro Engineers Pvt. Ltd. | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 210 | Mysore Mercantile | 4.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 211 | MSPL-VI | 5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 212 | MSPL-VII | 16.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 213 | Ramgad Minerals & Mining-III | 3.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 214 | Ramgad Minerals & Mining-IV | 17.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 215 | MSPL-IV(SUZLON) | 13.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 216 | MSPL-V(SUZLON) | 11.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 217 | Ramgad Minerals & Mining-I(SUZLON) | 10 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 218 | Ramgad Minerals & Mining-II(SUZLON) | 7.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 219 | Venganna Setty & Bros(suzlon) | 7.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 220 | KRDEL SOGI | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 221 | Mavinahonda | 2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 222 | VSL Mining Company 1 | 6.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 223 | VSL Mining Company 2 | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 224 | VS Lad and Sons | 3.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 225 | Mahalaxmi Commercial Services | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 226 | Siddayu Ayurvedic Research Foundation | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 227 | Mark data Power & Energy (P) Ltd | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 228 | Allegro Venture | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 229 | Enercon Wind Farms( Krishna) | 17.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 230 | EnerconWindFarms(Krishna) | 2.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 231 | Enercon Wind Farms( KARNATAKA) | 3.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 232 | R.D.S.Construction | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 233 | Neharaj Energy | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 234 | Jubliee Textile Mills | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 235 | Avanti Feeds Ltd | 3.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 236 | Srinivasa Cystine | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 237 | B.V.Finance & Leasing | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 238 | Brindavan Agro Industries Ltd | 3.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 239 | Vandana Rolling Mills Ltd | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 240 | R.S.Suriya | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 241 | Vandana Global Ltd | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 242 | Vivek Trading | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 243 | Mahalaxmi Construction Corpn Ltd | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 244 | Amrit Bottlers Pvt Ltd | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 245 | Vivek Pharmachem (India ) Ltd | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 246 | M/s Indian Power Corporation-1 | 2.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 247 | M/s Indian Power Corporation-2 | 4.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 248 | M/s Prasad Technology Park Ltd | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 249 | M/s Unnathi Projects | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 250 | M/s Mumbai Stock Brokers Pvt Ltd | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 251 | M/s D.R. Container Terminal | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 252 | M/s Panama Infrastructure | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 253 | M/s Sameer Ladkat | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 254 | M/s Indian Power Corporation-3 | 3.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 255 | M/s Ramco Industries Ltd | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 256 | M/s Elpro International Ltd | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 257 | M/s Cauvery Coffee Traders | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 258 | M/s M.K.Agrotech Pvt Ltd | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 259 | M/s Siddaganga Oil Extractions | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 260 | M/s Panama Business Centre | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 261 | M/s Balasaheb M Ladkat | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 262 | M/s Goutam Ladkat | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 263 | Gem Crafts-1 | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 264 | Gem Crafts-2 | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 265 | Enercon Wind Farms(Chitradurga) | 8.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 266 | Globe Transports Company | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 267 | V.M.Salgaocar & Brothers Pvt Ltd | 3.75 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 268 | Vandana Global Ltd | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 269 | Indian Wind Energy Association | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 270 | Triveni Enterprises | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 271 | Research Developers & MFG Corporation | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 272 | BSK Trading INK | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 273 | Shakambari Enterprises | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 274 | Praveen Chandra | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 275 | Ensemble Infrastructure | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 276 | Visva Visal Engineering Ltd | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 277 | Nava Bharat International Ltd | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 278 | Ramesh Kumar Hanjarimal Rathod | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 279 | PraveenChandra(K245) | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 280 | Hutti Gold Mines | 10.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 281 | Enercon Wind Farms(Hindustan) | 56.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 282 | Enercon Wind Farms(Hindustan) | 12 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 283 | Rangamma Steel & Malleables | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 284 | Sree Devi Chemicals | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 285 | Triveni Enterprises | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 286 | Texmo Precision Casting | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 287 | Happy Valley Developers | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 288 | U.D.Foundation | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 289 | Texonic Instruments | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 290 | Protectron Electromech(P) Ltd | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 291 | VXL Systems | 0.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 292 | Ranka-N-Ranka | 5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 293 | AccionWindEnergyPvtLtd | 13.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 294 | IndoWindEnergyLtd | 10.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 295 | IndoWindEnergyLtd | 7.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 296 | AllamVeerabhadrappa | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 297 | VSLadandSons | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 298 | VSLMiningCo.PVTLtd | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 299 | Sameera Trading Company | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 300 | Gangadhar Narasingdas | 10.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 301 | Eastman International | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 302 | Ramesh Steels | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 303 | Rita International | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 304 | Belgaum Wind Farms Pvt Ltd | 24.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 305 | Green infra energy Ltd | 36.3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 306 | Green infra energy Ltd | 23.1 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 307 | Accion Wind Energy Pvt Ltd | 16.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 308 | Tata power(25.6MW) | 25.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 309 | Tata power(24.8MW) | 24.8 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 310 | ICSA | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 311 | ICSA | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 312 | Leo fasteners | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 313 | Leo fasteners | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 314 | Sargam Retails Pvt Ltd | 6.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 315 | Sargam Retails Pvt Ltd | 7.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 316 | D.J.Malpani | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 317 | Gangadhar Narsingdas Agarwal | 3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 318 | Ferromar Shipping Pvt.Ltd | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 319 | Gangadhar Narsingdas Agarwal | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 320 | Sriram EPC | 1.35 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 321 | NMDC | 9 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 322 | P.Venganna Shetty | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 323 | Ramgad Minerals & Mining Ltd-III | 5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 324 | Super Wind Project(P) Ltd-Phase 6 | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 325 | Super Wind Project(P) Ltd-Phase 7 | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 326 | Super Wind Project(P) Ltd-Phase 8 | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 327 | Simran Wind Project(P)Ltd-Phase 3 | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 328 | Simran Wind Project(P)Ltd-Phase 4 | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 329 | Energy Developement Company Ltd | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 330 | Deepak Cables | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 331 | CLP Wind Farms(India)Pvt Ltd | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 332 | Sree Minerals | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 333 | Gautham Freight | 4.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 334 | Hira Ferro Alloys Ltd | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 335 | Abhishek Export(India) Pvt Ltd | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 336 | H.G.Rangan Goud | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 337 | Sunvik Steels Pvt Ltd | 10 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 338 | NMDC | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 339 | PTC India Financial Services Ltd(Phase-1) | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 340 | PTC India Financial Services Ltd(Phase-2) | 4.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 341 | Vish Wind Infrastructure LLP | 6.4 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 342 | SRB Consultancy Pvt Ltd | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 343 | SRB Consultancy Pvt Ltd | 1.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 344 | CLP Wind Farms (India) Pvt Ltd | 39.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 345 | EN Renewable Energy Ltd | 11.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 346 | EN Renewable Energy Ltd | 39.2 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 347 | Protectron | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 348 | Ramgad Minerals & Mining Ltd-III | 1.25 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 349 | Ramgad Minerals & Mining Ltd-III | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 350 | M/s Vikram Traders | 2.1 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 351 | M/s Vikram Traders | 2.1 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 352 | Sterling Agro industries | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 353 | Srinivasa Hatcheries | 2.5 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 354 | Vish Wind Infrastructure LLP 1.6 | 1.6 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 355 | Mytrah Vayu (Krishna) Phase-5 IDIPP-12) | 15.3 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 356 | Mytrah Vayu (Krishna) Phase-4 IDIPP-11) | 17.85 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 357 | Mytrah Vayu (Krishna) Phase-3 IDIPP-10) | 16.15 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 358 | Mytrah Vayu (Krishna) Phase-2 IDIPP-09) | 17 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 359 | Mytrah Vayu (Krishna) Phase-1 IDIPP-08) | 11.05 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 360 | Mytrah Vayu (Krishna) Phase-6 IDIPP-13) | 17.85 |  | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 361 | Bharat Petroleum Corporation Ltd (HTPBP-13) | 2.1 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 362 | Bharat Petroleum Corporation Ltd (HTPBP-18) | 4.2 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 363 | Green infrawind energy AssociationSemb corp | 44 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 364 | Sunphoto volataic | 60 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 365 | Atri Power Wind Bijapur 2 Pvt ltd | 23.3 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 366 | Aikyam holdings | 8 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 367 | Poonavala HTP 10 | 8.4 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 368 | Poonavala HTP 28 | 8.4 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 369 | Poonavala HTP 55 | 6.3 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 370 | Serum Institute of India | 2.1 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 371 | Sanchore Renewabls | 40 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 372 | Renewwind varekarwadi | 40 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 373 | Ananthara Enterprises | 2 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 374 | Protectron Electromech(P) Ltd | 2 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 375 | Serum Institute of India | 4.2 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 376 | Serum Institute of India | 2.1 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 377 | Serum Institute of India | 2.1 | Wnd | 20 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 378 | [5 empty] | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 379 | Jindal Aluminium Ltd Solar | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 380 | United Telecoms Limited | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 381 | United Surya Energy | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 382 | BhorukaPowerCorporation (Solar) | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 383 | Azure Power Karnataka | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 384 | Azure Power India | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 385 | SECI | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 386 | SECI | 480 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 387 | Welspun 34 Mw | 34 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 388 | Welspun 16 Mw | 16 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 389 | Welspun 50 Mw | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 390 | Photo Surka kiran | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 391 | Asian Fab Tech | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 392 | Asian Fab tech Sira, | 15 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 393 | Sei Aditi | 30 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 394 | Sei Bheem | 30 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 395 | Sei Diamond | 30 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 396 | Suryashakthi | 30 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 397 | Mallagi Education 1.00 Mw | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 398 | VR Patil vidyut Nirman Ltd | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 399 | Samyama Jyothi Solar | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 400 | SGTRS Solar | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 401 | Sharanagowda Solar | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 402 | Skylet Power | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 403 | Sri Sai Shivanagere Solar | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 404 | Suragi Power | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 405 | Ramavari Power | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 406 | Prathiba Solar | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 407 | Chandragiri Power & Infra | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 408 | Guttur Solar Power | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 409 | HaLO energy MHHECL 51 | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 410 | HaLO energy MHHECL 50 | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 411 | HaLO energy MHHECL 52 | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 412 | Janakshi renewable Energy | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 413 | PV Power | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 414 | Ramapriya Solar | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 415 | Prema vijayendra | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 416 | P somachandra Consol energy | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 417 | ADC power | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 418 | Niketan Solar | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 419 | Ahaskar Arya Solar | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 420 | Rangadhol Solar Power | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 421 | Rayappa poojari | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 422 | Burnish Solar | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 423 | Scald Energy Pvt ltd | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 424 | BLDE Association | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 425 | BLDE University | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 426 | Kumars Energy | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 427 | Saleems Enegy | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 428 | Mulgund Energy | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 429 | Arete Elena | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 430 | Venkat energy | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 431 | Mepgen solar | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 432 | Sunishka Solar | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 433 | Rajpet Energy | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 434 | Sowhil Energy | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 435 | Panchakshari Power | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 436 | LRK Solar | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 437 | LPD Solar | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 438 | V carve | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 439 | Blister Solar (Krishna naik) | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 440 | Scorch Solar (Kamalabai) | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 441 | tacholine renewable (A Savitha) | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 442 | T. Vijayakumar | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 443 | Flaunt Solar Energy (Lakkshmamma) | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 444 | Cambria solar (gangaraju) | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 445 | Torrid Solar | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 446 | Alles Solar Pvt Ltd | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 447 | Spangle (shashidhara) | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 448 | R Gayathri Solar | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 449 | Poorvaj Solar | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 450 | T Gowranna | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 451 | Chowdeshwari Solar | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 452 | Aadyaarush Power | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 453 | Sri Ugrappa | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 454 | hunsakodihalli (pallavi S) | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 455 | Saakesha solar | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 456 | MNR solar (manjunatha k.t) | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 457 | Chennamanagathihalli Solar | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 458 | Hirehalli Solar (vyaramudi) | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 459 | Chikkahalli Solar H V Chaudary | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 460 | Vatsala Bellary | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 461 | Swelter energy (Anjinamma) | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 462 | Insolexo pvt ltd | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 463 | manjunath R kabadi | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 464 | Jayamal Energy | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 465 | Murali M Baladev | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 466 | Lakshmamma | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 467 | Shuun Solar | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 468 | H Ramanjaneya | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 469 | RJR Solar | 3 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 470 | Mandidurgappa | 1 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 471 | Renew Wind Energy - GIPP-13 | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 472 | Renew Wind Energy - GIPP-17 | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 473 | Tarun Kiran Bhoomi | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 474 | Jindal Aluminium Ltd Solar | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 475 | GRT Jewellers | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 476 | Clean Solar madhugiri | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 477 | Clean Solar Tumkur | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 478 | ES Sun power Pvt ltd | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 479 | ES Solar Pvt ltd | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 480 | Chirasthayi Saurya | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 481 | Chirasthayi Saurya | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 482 | Adani green enegy holenarasipura | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 483 | Adani green enegy K R pet | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 484 | Growth Street solar | 4 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 485 | Renew Wind Rajasthan Four | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 486 | Renew Wind MP Three | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 487 | Adani green enegy Tiptur | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 488 | Mytrah Advaith | 15 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 489 | Asian Fab tech Alakapur, gowribidnur | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 490 | Asian Fab tech kavalahalli, Doddaballapur | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 491 | Asian Fab tech thirumalapur, nagamangala | 15 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 492 | Renew wind energy Maharashtra | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 493 | Kodangal Solar park | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 494 | KN Bijapura Solar energy | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 495 | KN Indi Vijayapura Solar energy | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 496 | Adani Green energy Gubbi tq | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 497 | Aditya birla solar ltd | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 498 | Brics renewable energy pvt ltd | 2 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 499 | Adani Green energy Ramanagara tq | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 500 | Avanthi renewable energy pvt ltd | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 501 | NVR Renew Pvt Ltd | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 502 | Azure power Earth | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 503 | Aadya solar Block 1 | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 504 | Aadya solar Block 2 | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 505 | Aadya solar Block 3 | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 506 | Aadya solar Block 6 | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 507 | Tata power 15 | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 508 | Tata power 17 | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 509 | Tata power 18 | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 510 | Fortum b5 | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 511 | Fortum B9 | 50 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 512 | Taletuttayi | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 513 | Asia fab tech , Arasikere | 10 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 514 | ACME Kittur Solar Energy Pvt ltd | 15 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 515 | ACME Sidlaghatta Solar Energy Pvt ltd | 15 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 516 | ACME Guledagudda Solar Energy Pvt ltd | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 517 | radiance Solar Pvt ltd | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 518 | Asia fab tech , Doddaballapur | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 519 | Asian fab tec Chintamani | 5 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 520 | Nokar Renew power Bailahongal | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 521 | Asian fab tec KGF Taluk | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 522 | Asian fab tec Gudibande | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 523 | Asian Fab tec Bangarpete | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 524 | Akilagya | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA
| 525 | Acme Kudligi | 20 | Solar | 25 years | Intra state | NA | NA | NA | NA | NA | NA | NA | NA | NA | NA

## CONSUMERS & CONSUMPTION DATA
Period From 01.04.2022 To 30.06.2022
S.No | Type of Consumers | Category of Consumers (EHT/HT/LT/Others) | Voltage Level (In Voltage) | No of Consumers | Total Consumption (In MU) | Remarks (Source of data)
1 | Domestic | LT |  | 9878585 | 2145.3982 | LT1, LT2
2 | Commercial | LT |  | 1236119 | 584.1629 | LT3, LT6C
3 | IP Sets | LT |  | 996714 | 2088.511 | LT4A, LT4B
4 | Hor. & Nur. & Coffee/Tea & Rubber (Metered) | LT |  | 1979 | 1.7602 | LT4C
5 | Hor. & Nur. & Coffee/Tea & Rubber (Flat)
6 | Heating and Motive Power
7 | Water Supply | LT |  | 91491 | 381.874 | LT6A
8 | Public Lighting | LT |  | 79745 | 155.8666 | LT6B
9 | HT Water Supply | HT |  | 294 | 218.1513 | HT1
10 | HT Industrial | HT |  | 8060 | 1278.8317 | HT2A
11 | Industrial (Small) | LT |  | 235699 | 336.6228 | LT5
12 | Industrial (Medium)
13 | HT Commercial | HT |  | 8155 | 581.3739 | HT2B, HT EV
14 | Applicable to Government Hospitals & Hospitals | HT |  | 990 | 93.6428 | HT2C
15 | Lift Irrigation Schemes/Lift Irrigation Societies | HT |  | 74 | 27.1854 | HT3
16 | HT Res. Apartments Applicable to all areas | HT |  | 484 | 24.4449 | HT4
17 | Mixed Load
18 | Government offices and department
19 | Others-1 (if any , specify in remarks) | HT |  | 2024 | 45.0803 | HT5
20 | Others-2 (if any , specify in remarks) | LT |  | 930790 | 70.2893 | LT7
| Total |  |  | 13471203 | 8033.1953

## Division Wise Losses
Division wise Losses
S.No | Name of circle | Circle code | Name of the Division | Period from 01.04.2022 to 30.06.2022
|  |  |  | Consumer profile | [8 empty] | Energy parameters |  |  |  |  | Losses |  | Commercial Parameter |  |  | AT & C loss (%)
|  |  |  | Consumer category | No of connection metered (Nos) | No of connection Un-metered (Nos) | Total Number of connections (Nos) | % of number of connections | Connected Load metered (MW) | Connected Load Un-metered (MW) | Total Connected Load (MW) | % of connected load |  | Billed energy (MU) |  |  | % of energy consumption | T&D loss (MU) | T&D loss (%) | Billed Amount in Rs. Crore | Collected Amount in Rs. Crore | Collection Efficiency
[13 empty] | Input energy (MU) | Metered energy | Unmetered/assessment energy | Total energy
1 | SOUTH | 251 | JAYANAGAR | Residential | 625172 |  | 625172 | 77.75% | 1400.7258 |  | 1400.7258 | 59.54% | 411.5719 | 203.4575 |  | 203.4575 | 52.64% | 25.0402 | 6.084% | 165.9411 | 164.2061 | 98.95%
|  |  |  | Agricultural | 142 | 159 | 301 | 0.03744% | 0.43957 | 0.55577 | 0.99534 | 0.04231% |  | 0.051865 | 0.000227 | 0.052092 | 0.01348% |  |  | 0.029131 | 0.031459 | 108%
|  |  |  | Commercial/Industrial-LT | 96388 |  | 96388 | 11.99% | 415.2613 |  | 415.2613 | 17.65% |  | 68.8329 |  | 68.8329 | 17.81% |  |  | 75.5474 | 74.4753 | 98.58%
|  |  |  | Commercial/Industrial-HT | 1160 |  | 1160 | 0.1443% | 244.3625 |  | 244.3625 | 10.39% |  | 72.1815 |  | 72.1815 | 18.67% |  |  | 83.5715 | 82.1855 | 98.34%
|  |  |  | Others | 81030 |  | 81030 | 10.08% | 291.1521 |  | 291.1521 | 12.38% |  | 42.0077 |  | 42.0077 | 10.87% |  |  | 45.7646 | 38.3427 | 83.78%
Sub-total |  |  |  |  | 803892 | 159 | 804051 | 100% | 2351.9413 | 0.55577 | 2352.4971 | 100% | 411.5719 | 386.5315 | 0.000227 | 386.5317 | 100% | 25.0402 | 6.084% | 370.8536 | 359.2411 | 96.87% | 9.025%
2 | SOUTH | 251 | KORAMANGALA | Residential | 452608 |  | 452608 | 82.07% | 928.3387 |  | 928.3387 | 44.66% | 420.6703 | 145.2897 |  | 145.2897 | 36.78% | 25.6937 | 6.108% | 119.1312 | 117.4915 | 98.62%
|  |  |  | Agricultural | 30 | 642 | 672 | 0.1218% | 0.0904 | 1.9859 | 2.0763 | 0.0999% |  | 5.8787 | 0.24513 | 6.1238 | 1.55% |  |  | 1.9726 | 3.0007 | 152.1%
|  |  |  | Commercial/Industrial-LT | 60261 |  | 60261 | 10.93% | 251.5492 |  | 251.5492 | 12.1% |  | 46.0957 |  | 46.0957 | 11.67% |  |  | 50.9807 | 50.3761 | 98.81%
|  |  |  | Commercial/Industrial-HT | 1154 |  | 1154 | 0.2092% | 678.7785 |  | 678.7785 | 32.66% |  | 164.5537 |  | 164.5537 | 41.66% |  |  | 221.3756 | 224.5687 | 101.4%
|  |  |  | Others | 36817 |  | 36817 | 6.676% | 217.744 |  | 217.744 | 10.48% |  | 32.9137 |  | 32.9137 | 8.333% |  |  | 33.5162 | 31.1969 | 93.08%
Sub-total |  |  |  |  | 550870 | 642 | 551512 | 100% | 2076.5009 | 1.9859 | 2078.4868 | 100% | 420.6703 | 394.7314 | 0.24513 | 394.9766 | 100% | 25.6937 | 6.108% | 426.9763 | 426.6339 | 99.92% | 6.183%
3 | SOUTH | 251 | HSR LAYOUT | Residential | 724390 |  | 724390 | 81.17% | 1559.4001 |  | 1559.4001 | 57.25% | 508.8397 | 235.1701 |  | 235.1701 | 50.19% | 40.2808 | 7.916% | 197.5329 | 193.697 | 98.06%
|  |  |  | Agricultural | 140 | 2193 | 2333 | 0.2614% | 0.62428 | 7.354 | 7.9783 | 0.2929% |  | 0.1028 | 0.72958 | 0.83238 | 0.1776% |  |  | 0.40376 | 0.35987 | 89.13%
|  |  |  | Commercial/Industrial-LT | 84022 |  | 84022 | 9.415% | 367.3348 |  | 367.3348 | 13.49% |  | 71.1388 |  | 71.1388 | 15.18% |  |  | 75.9142 | 74.6005 | 98.27%
|  |  |  | Commercial/Industrial-HT | 1366 |  | 1366 | 0.1531% | 443.6857 |  | 443.6857 | 16.29% |  | 129.2008 |  | 129.2008 | 27.57% |  |  | 152.1109 | 151.5027 | 99.6%
|  |  |  | Others | 80298 |  | 80298 | 8.998% | 345.5221 |  | 345.5221 | 12.68% |  | 32.2166 |  | 32.2166 | 6.876% |  |  | 41.4889 | 38.1474 | 91.95%
Sub-total |  |  |  |  | 890216 | 2193 | 892409 | 100% | 2716.5669 | 7.354 | 2723.9209 | 100% | 508.8397 | 467.8293 | 0.72958 | 468.5588 | 100% | 40.2808 | 7.916% | 467.4508 | 458.3075 | 98.04% | 9.717%
4 | NORTH | 260 | PEENNYA | Residential | 325599 |  | 325599 | 77.88% | 402.3605 |  | 402.3605 | 35.87% | 272.0183 | 65.6736 |  | 65.6736 | 25.47% | 14.2132 | 5.225% | 50.9921 | 49.9135 | 97.88%
|  |  |  | Agricultural | 7 | 241 | 248 | 0.05932% | 0.020115 | 0.79027 | 0.81039 | 0.07225% |  | 0 | 0.063986 | 0.063986 | 0.02482% |  |  | 0.028401 | 0.028891 | 101.7%
|  |  |  | Commercial/Industrial-LT | 53096 |  | 53096 | 12.7% | 344.8932 |  | 344.8932 | 30.75% |  | 58.3942 |  | 58.3942 | 22.65% |  |  | 58.0416 | 57.2387 | 98.62%
|  |  |  | Commercial/Industrial-HT | 1118 |  | 1118 | 0.2674% | 268.4189 |  | 268.4189 | 23.93% |  | 122.5603 |  | 122.5603 | 47.54% |  |  | 114.2543 | 112.6012 | 98.55%
|  |  |  | Others | 38029 |  | 38029 | 9.096% | 105.1855 |  | 105.1855 | 9.378% |  | 11.1131 |  | 11.1131 | 4.311% |  |  | 12.7909 | 8.4792 | 66.29%
Sub-total |  |  |  |  | 417849 | 241 | 418090 | 100% | 1120.8783 | 0.79027 | 1121.6685 | 100% | 272.0183 | 257.7411 | 0.063986 | 257.8051 | 100% | 14.2132 | 5.225% | 236.1073 | 228.2615 | 96.68% | 8.374%
5 | NORTH | 260 | MALLESHWARAM | Residential | 226022 |  | 226022 | 76.83% | 434.5802 |  | 434.5802 | 58.11% | 137.2611 | 60.7913 |  | 60.7913 | 46.52% | 6.5693 | 4.786% | 48.8398 | 48.3131 | 98.92%
|  |  |  | Agricultural | 1 | 2 | 3 | 0.00102% | 0.00745 | 0.011685 | 0.019135 | 0.002559% |  | 0 | 0 | 0 | 0% |  |  | 0.00028 | 0.00028 | 100%
|  |  |  | Commercial/Industrial-LT | 45896 |  | 45896 | 15.6% | 164.2264 |  | 164.2264 | 21.96% |  | 25.7038 |  | 25.7038 | 19.67% |  |  | 28.009 | 27.6105 | 98.58%
|  |  |  | Commercial/Industrial-HT | 312 |  | 312 | 0.1061% | 72.6988 |  | 72.6988 | 9.722% |  | 35.009 |  | 35.009 | 26.79% |  |  | 36.0094 | 35.5912 | 98.84%
|  |  |  | Others | 21963 |  | 21963 | 7.465% | 76.2752 |  | 76.2752 | 10.2% |  | 9.1876 |  | 9.1876 | 7.03% |  |  | 9.7678 | 7.4173 | 75.94%
Sub-total |  |  |  |  | 294194 | 2 | 294196 | 100% | 747.788 | 0.011685 | 747.7997 | 100% | 137.2611 | 130.6918 | 0 | 130.6918 | 100% | 6.5693 | 4.786% | 122.6262 | 118.9324 | 96.99% | 7.654%
6 | NORTH | 260 | HEBBALA | Residential | 433799 |  | 433799 | 78.91% | 837.2067 |  | 837.2067 | 59.94% | 281.5507 | 132.7553 |  | 132.7553 | 50.36% | 17.9467 | 6.374% | 107.6933 | 105.0504 | 97.55%
|  |  |  | Agricultural | 44 | 3525 | 3569 | 0.6492% | 0.3658 | 12.8055 | 13.1713 | 0.943% |  | 0.24403 | 18.0245 | 18.2685 | 6.93% |  |  | 8.2237 | 9.3782 | 114%
|  |  |  | Commercial/Industrial-LT | 59098 |  | 59098 | 10.75% | 184.0932 |  | 184.0932 | 13.18% |  | 36.8329 |  | 36.8329 | 13.97% |  |  | 39.0192 | 38.1372 | 97.74%
|  |  |  | Commercial/Industrial-HT | 431 |  | 431 | 0.0784% | 151.693 |  | 151.693 | 10.86% |  | 45.7411 |  | 45.7411 | 17.35% |  |  | 50.5161 | 47.9266 | 94.87%
|  |  |  | Others | 52822 |  | 52822 | 9.609% | 210.6482 |  | 210.6482 | 15.08% |  | 30.0062 |  | 30.0062 | 11.38% |  |  | 34.5802 | 26.7442 | 77.34%
Sub-total |  |  |  |  | 546194 | 3525 | 549719 | 100% | 1384.0069 | 12.8055 | 1396.8124 | 100% | 281.5507 | 245.5795 | 18.0245 | 263.604 | 100% | 17.9467 | 6.374% | 240.0325 | 227.2365 | 94.67% | 11.37%
7 | NORTH | 260 | JALAHALLI | Residential | 286261 |  | 286261 | 75.75% | 462.4246 |  | 462.4246 | 59.44% | 145.6141 | 71.3922 |  | 71.3922 | 53.03% | 10.9869 | 7.545% | 55.9176 | 54.9822 | 98.33%
|  |  |  | Agricultural | 52 | 2398 | 2450 | 0.6483% | 0.37698 | 11.9863 | 12.3633 | 1.589% |  | 0.059668 | 5.7963 | 5.8559 | 4.35% |  |  | 2.6339 | 2.6129 | 99.2%
|  |  |  | Commercial/Industrial-LT | 36812 |  | 36812 | 9.741% | 124.2577 |  | 124.2577 | 15.97% |  | 20.867 |  | 20.867 | 15.5% |  |  | 22.3034 | 21.7807 | 97.66%
|  |  |  | Commercial/Industrial-HT | 172 |  | 172 | 0.04551% | 44.9888 |  | 44.9888 | 5.783% |  | 20.5666 |  | 20.5666 | 15.28% |  |  | 21.009 | 19.9559 | 94.99%
|  |  |  | Others | 52226 |  | 52226 | 13.82% | 133.9318 |  | 133.9318 | 17.22% |  | 15.9455 |  | 15.9455 | 11.84% |  |  | 18.4863 | 16.1137 | 87.17%
Sub-total |  |  |  |  | 375523 | 2398 | 377921 | 100% | 765.98 | 11.9863 | 777.9663 | 100% | 145.6141 | 128.831 | 5.7963 | 134.6272 | 100% | 10.9869 | 7.545% | 120.3502 | 115.4454 | 95.92% | 11.31%
8 | EAST | 265 | VIDHANA SOUDHA | Residential | 157730 |  | 157730 | 57.56% | 226.2665 |  | 226.2665 | 37.22% | 129.4939 | 41.4512 |  | 41.4512 | 34.8% | 10.3871 | 8.021% | 32.4259 | 31.2072 | 96.24%
|  |  |  | Agricultural | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0% |  | 0 | 0 | 0 | 0% |  |  | 0 | 0 | 0%
|  |  |  | Commercial/Industrial-LT | 100266 |  | 100266 | 36.59% | 231.9424 |  | 231.9424 | 38.15% |  | 38.0446 |  | 38.0446 | 31.94% |  |  | 41.5006 | 40.7677 | 98.23%
|  |  |  | Commercial/Industrial-HT | 357 |  | 357 | 0.1303% | 84.9915 |  | 84.9915 | 13.98% |  | 29.1149 |  | 29.1149 | 24.44% |  |  | 35.0309 | 33.2316 | 94.86%
|  |  |  | Others | 15670 |  | 15670 | 5.718% | 64.7723 |  | 64.7723 | 10.65% |  | 10.4961 |  | 10.4961 | 8.812% |  |  | 10.1632 | 8.2504 | 81.18%
Sub-total |  |  |  |  | 274023 | 0 | 274023 | 100% | 607.9727 | 0 | 607.9727 | 100% | 129.4939 | 119.1068 | 0 | 119.1068 | 100% | 10.3871 | 8.021% | 119.1206 | 113.457 | 95.25% | 12.39%
9 | EAST | 265 | INDIRANAGAR | Residential | 321476 |  | 321476 | 78.28% | 674.5501 |  | 674.5501 | 52.69% | 254.2379 | 102.6015 |  | 102.6015 | 42.38% | 12.1266 | 4.77% | 83.6007 | 81.9797 | 98.06%
|  |  |  | Agricultural | 5 | 215 | 220 | 0.05357% | 0.02235 | 0.62171 | 0.64406 | 0.05031% |  | 0 | 0.16912 | 0.16912 | 0.06985% |  |  | 0.080219 | 0.080909 | 100.9%
|  |  |  | Commercial/Industrial-LT | 49694 |  | 49694 | 12.1% | 233.3317 |  | 233.3317 | 18.23% |  | 39.1014 |  | 39.1014 | 16.15% |  |  | 43.6773 | 42.9797 | 98.4%
|  |  |  | Commercial/Industrial-HT | 860 |  | 860 | 0.2094% | 247.0572 |  | 247.0572 | 19.3% |  | 85.3308 |  | 85.3308 | 35.24% |  |  | 94.9661 | 94.0403 | 99.03%
|  |  |  | Others | 38403 |  | 38403 | 9.352% | 124.5333 |  | 124.5333 | 9.728% |  | 14.9085 |  | 14.9085 | 6.158% |  |  | 15.902 | 12.4203 | 78.11%
Sub-total |  |  |  |  | 410438 | 215 | 410653 | 100% | 1279.4946 | 0.62171 | 1280.1163 | 100% | 254.2379 | 241.9422 | 0.16912 | 242.1113 | 100% | 12.1266 | 4.77% | 238.2262 | 231.5009 | 97.18% | 7.458%
10 | EAST | 265 | SHIVAJINAGAR | Residential | 503331 |  | 503331 | 76.01% | 1037.4857 |  | 1037.4857 | 57.04% | 359.1314 | 168.8242 |  | 168.8242 | 50.93% | 27.627 | 7.693% | 137.2717 | 133.1865 | 97.02%
|  |  |  | Agricultural | 29 | 853 | 882 | 0.1332% | 0.0904 | 2.7135 | 2.8039 | 0.1541% |  | 2.734 | 0.090213 | 2.8242 | 0.8519% |  |  | 0.90535 | 1.1464 | 126.6%
|  |  |  | Commercial/Industrial-LT | 84250 |  | 84250 | 12.72% | 277.7029 |  | 277.7029 | 15.27% |  | 52.9755 |  | 52.9755 | 15.98% |  |  | 58.2752 | 56.6732 | 97.25%
|  |  |  | Commercial/Industrial-HT | 723 |  | 723 | 0.1092% | 207.1258 |  | 207.1258 | 11.39% |  | 62.7708 |  | 62.7708 | 18.94% |  |  | 76.5013 | 75.7984 | 99.08%
|  |  |  | Others | 72985 |  | 72985 | 11.02% | 293.9041 |  | 293.9041 | 16.16% |  | 44.1097 |  | 44.1097 | 13.31% |  |  | 49.8525 | 41.5938 | 83.43%
Sub-total |  |  |  |  | 661318 | 853 | 662171 | 100% | 1816.3088 | 2.7135 | 1819.0223 | 100% | 359.1314 | 331.4142 | 0.090213 | 331.5044 | 100% | 27.627 | 7.693% | 322.8061 | 308.3984 | 95.54% | 11.81%
11 | EAST | 265 | WHITEFIELD | Residential | 305545 |  | 305545 | 81.71% | 657.4898 |  | 657.4898 | 44.02% | 259.1867 | 102.8634 |  | 102.8634 | 41.77% | 12.9318 | 4.989% | 86.1997 | 85.3669 | 99.03%
|  |  |  | Agricultural | 14 | 1674 | 1688 | 0.4514% | 0.06111 | 5.4228 | 5.4839 | 0.3671% |  | 0.014474 | 2.0207 | 2.0351 | 0.8264% |  |  | 0.92026 | 0.91766 | 99.72%
|  |  |  | Commercial/Industrial-LT | 32179 |  | 32179 | 8.605% | 119.5093 |  | 119.5093 | 8.001% |  | 22.7801 |  | 22.7801 | 9.251% |  |  | 24.411 | 23.9471 | 98.1%
|  |  |  | Commercial/Industrial-HT | 649 |  | 649 | 0.1736% | 442.8947 |  | 442.8947 | 29.65% |  | 94.9176 |  | 94.9176 | 38.54% |  |  | 127.112 | 126.0414 | 99.16%
|  |  |  | Others | 33894 |  | 33894 | 9.064% | 268.2725 |  | 268.2725 | 17.96% |  | 23.6586 |  | 23.6586 | 9.607% |  |  | 27.301 | 23.5527 | 86.27%
Sub-total |  |  |  |  | 372281 | 1674 | 373955 | 100% | 1488.2273 | 5.4228 | 1493.6502 | 100% | 259.1867 | 244.2342 | 2.0207 | 246.2549 | 100% | 12.9318 | 4.989% | 265.944 | 259.8258 | 97.7% | 7.175%
12 | WEST | 266 | RAJAJINAGAR | Residential | 443926 |  | 443926 | 75.71% | 763.619 |  | 763.619 | 56.17% | 230.5727 | 107.5079 |  | 107.5079 | 49.23% | 12.1824 | 5.284% | 84.8973 | 83.7068 | 98.6%
|  |  |  | Agricultural | 11 | 212 | 223 | 0.03803% | 0.042465 | 0.69115 | 0.73361 | 0.05396% |  | 0 | 0.036993 | 0.036993 | 0.01694% |  |  | 0.016304 | 0.018189 | 111.6%
|  |  |  | Commercial/Industrial-LT | 76539 |  | 76539 | 13.05% | 359.425 |  | 359.425 | 26.44% |  | 67.8578 |  | 67.8578 | 31.07% |  |  | 68.208 | 67.0094 | 98.24%
|  |  |  | Commercial/Industrial-HT | 485 |  | 485 | 0.08272% | 65.8024 |  | 65.8024 | 4.84% |  | 21.5325 |  | 21.5325 | 9.86% |  |  | 24.1681 | 23.6962 | 98.05%
|  |  |  | Others | 65174 |  | 65174 | 11.12% | 169.991 |  | 169.991 | 12.5% |  | 21.4551 |  | 21.4551 | 9.824% |  |  | 23.6616 | 17.0693 | 72.14%
Sub-total |  |  |  |  | 586135 | 212 | 586347 | 100% | 1358.8799 | 0.69115 | 1359.571 | 100% | 230.5727 | 218.3534 | 0.036993 | 218.3904 | 100% | 12.1824 | 5.284% | 200.9514 | 191.5 | 95.3% | 9.738%
13 | WEST | 266 | RAJARAJESHWARINAGARA | Residential | 276797 |  | 276797 | 76.39% | 571.5601 |  | 571.5601 | 59.6% | 171.6507 | 78.5859 |  | 78.5859 | 48.18% | 8.526 | 4.967% | 63.6801 | 62.9812 | 98.9%
|  |  |  | Agricultural | 49 | 60 | 109 | 0.03008% | 0.24468 | 0.25032 | 0.49499 | 0.05162% |  | 0.056782 | 0.014911 | 0.071693 | 0.04395% |  |  | 0.039583 | 0.035188 | 88.9%
|  |  |  | Commercial/Industrial-LT | 48614 |  | 48614 | 13.42% | 198.4481 |  | 198.4481 | 20.69% |  | 38.1116 |  | 38.1116 | 23.36% |  |  | 39.158 | 38.7119 | 98.86%
|  |  |  | Commercial/Industrial-HT | 372 |  | 372 | 0.1027% | 59.7142 |  | 59.7142 | 6.227% |  | 25.0552 |  | 25.0552 | 15.36% |  |  | 24.2766 | 24.2196 | 99.77%
|  |  |  | Others | 36441 |  | 36441 | 10.06% | 128.7302 |  | 128.7302 | 13.42% |  | 21.3003 |  | 21.3003 | 13.06% |  |  | 22.1739 | 18.9917 | 85.65%
Sub-total |  |  |  |  | 362273 | 60 | 362333 | 100% | 958.6973 | 0.25032 | 958.9476 | 100% | 171.6507 | 163.1098 | 0.014911 | 163.1247 | 100% | 8.526 | 4.967% | 149.3282 | 144.9396 | 97.06% | 7.76%
14 | WEST | 266 | KENGERI | Residential | 342621 |  | 342621 | 72.83% | 519.8061 |  | 519.8061 | 44.39% | 290.8485 | 75.7764 |  | 75.7764 | 27.01% | 10.3481 | 3.558% | 61.725 | 59.8177 | 96.91%
|  |  |  | Agricultural | 324 | 5944 | 6268 | 1.332% | 1.9538 | 22.9861 | 24.9399 | 2.13% |  | 0.23381 | 12.8028 | 13.0366 | 4.648% |  |  | 6.3398 | 6.73 | 106.2%
|  |  |  | Commercial/Industrial-LT | 46372 |  | 46372 | 9.857% | 245.0868 |  | 245.0868 | 20.93% |  | 48.5452 |  | 48.5452 | 17.31% |  |  | 47.8346 | 46.9752 | 98.2%
|  |  |  | Commercial/Industrial-HT | 547 |  | 547 | 0.1163% | 108.2552 |  | 108.2552 | 9.245% |  | 38.3047 |  | 38.3047 | 13.66% |  |  | 40.3495 | 39.8407 | 98.74%
|  |  |  | Others | 74627 |  | 74627 | 15.86% | 272.9325 |  | 272.9325 | 23.31% |  | 104.8375 |  | 104.8375 | 37.38% |  |  | 76.4536 | 65.7391 | 85.99%
Sub-total |  |  |  |  | 464491 | 5944 | 470435 | 100% | 1148.0343 | 22.9861 | 1171.0204 | 100% | 290.8485 | 267.6976 | 12.8028 | 280.5004 | 100% | 10.3481 | 3.558% | 232.7024 | 219.1027 | 94.16% | 9.194%
15 | BRC | 261 | NELAMANGALA | Residential | 309107 |  | 309107 | 71.75% | 204.7719 |  | 204.7719 | 19.87% | 340.9869 | 41.3887 |  | 41.3887 | 13.54% | 35.4217 | 10.39% | 30.731 | 29.1233 | 94.77%
|  |  |  | Agricultural | 117 | 30783 | 30900 | 7.173% | 0.93411 | 209.4343 | 210.3684 | 20.41% |  | 0.23927 | 75.0339 | 75.2732 | 24.63% |  |  | 33.3873 | 33.5584 | 100.5%
|  |  |  | Commercial/Industrial-LT | 50089 |  | 50089 | 11.63% | 176.4966 |  | 176.4966 | 17.13% |  | 29.7298 |  | 29.7298 | 9.729% |  |  | 29.1603 | 28.8712 | 99.01%
|  |  |  | Commercial/Industrial-HT | 878 |  | 878 | 0.2038% | 314.6292 |  | 314.6292 | 30.53% |  | 136.2392 |  | 136.2392 | 44.59% |  |  | 132.726 | 131.3526 | 98.97%
|  |  |  | Others | 39816 |  | 39816 | 9.243% | 124.3663 |  | 124.3663 | 12.07% |  | 22.9343 |  | 22.9343 | 7.506% |  |  | 24.4323 | 13.0879 | 53.57%
Sub-total |  |  |  |  | 400007 | 30783 | 430790 | 100% | 821.1982 | 209.4343 | 1030.6325 | 100% | 340.9869 | 230.5313 | 75.0339 | 305.5652 | 100% | 35.4217 | 10.39% | 250.4369 | 235.9933 | 94.23% | 15.56%
16 | BRC | 261 | Hoskote | Residential | 361160 |  | 361160 | 72.34% | 438.5377 |  | 438.5377 | 32.15% | 415.983 | 70.1445 |  | 70.1445 | 20.11% | 67.1874 | 16.15% | 54.2639 | 53.0036 | 97.68%
|  |  |  | Agricultural | 210 | 43949 | 44159 | 8.845% | 1.7697 | 274.7454 | 276.5151 | 20.27% |  | 4.227 | 98.3609 | 102.5879 | 29.41% |  |  | 45.1436 | 45.2201 | 100.2%
|  |  |  | Commercial/Industrial-LT | 49807 |  | 49807 | 9.976% | 178.8697 |  | 178.8697 | 13.12% |  | 29.4197 |  | 29.4197 | 8.435% |  |  | 29.8139 | 29.7709 | 99.86%
|  |  |  | Commercial/Industrial-HT | 898 |  | 898 | 0.1799% | 275.7808 |  | 275.7808 | 20.22% |  | 101.5934 |  | 101.5934 | 29.13% |  |  | 106.2629 | 107.5165 | 101.2%
|  |  |  | Others | 43231 |  | 43231 | 8.659% | 194.1475 |  | 194.1475 | 14.24% |  | 45.0501 |  | 45.0501 | 12.92% |  |  | 44.6 | 22.8072 | 51.14%
Sub-total |  |  |  |  | 455306 | 43949 | 499255 | 100% | 1089.1055 | 274.7454 | 1363.8508 | 100% | 415.983 | 250.4347 | 98.3609 | 348.7956 | 100% | 67.1874 | 16.15% | 280.0842 | 258.3183 | 92.23% | 22.67%
17 | RAMANAGARA | 267 | RAMANAGAR | Residential | 202589 |  | 202589 | 70.37% | 112.4418 |  | 112.4418 | 19.1% | 191.9136 | 27.6515 |  | 27.6515 | 15.88% | 17.8319 | 9.292% | 19.7108 | 19.1324 | 97.07%
|  |  |  | Agricultural | 67 | 37525 | 37592 | 13.06% | 0.39614 | 164.5754 | 164.9716 | 28.02% |  | 5.0628 | 69.7533 | 74.8161 | 42.98% |  |  | 33.8164 | 36.514 | 108%
|  |  |  | Commercial/Industrial-LT | 29372 |  | 29372 | 10.2% | 82.1666 |  | 82.1666 | 13.96% |  | 13.0697 |  | 13.0697 | 7.508% |  |  | 13.4155 | 13.2635 | 98.87%
|  |  |  | Commercial/Industrial-HT | 295 |  | 295 | 0.1025% | 156.5241 |  | 156.5241 | 26.59% |  | 45.0729 |  | 45.0729 | 25.89% |  |  | 51.5922 | 53.2054 | 103.1%
|  |  |  | Others | 18043 |  | 18043 | 6.267% | 72.5967 |  | 72.5967 | 12.33% |  | 13.4716 |  | 13.4716 | 7.739% |  |  | 12.4537 | 5.008 | 40.21%
Sub-total |  |  |  |  | 250366 | 37525 | 287891 | 100% | 424.1254 | 164.5754 | 588.7008 | 100% | 191.9136 | 104.3284 | 69.7533 | 174.0817 | 100% | 17.8319 | 9.292% | 130.9885 | 127.1233 | 97.05% | 11.97%
18 | RAMANAGARA | 267 | CHANDAPURA | Residential | 384900 |  | 384900 | 77.38% | 511.711 |  | 511.711 | 32.05% | 498.4671 | 83.7872 |  | 83.7872 | 17.97% | 32.3231 | 6.484% | 66.0248 | 65.2247 | 98.79%
|  |  |  | Agricultural | 174 | 14572 | 14746 | 2.964% | 0.95583 | 105.1019 | 106.0577 | 6.642% |  | 0.50904 | 31.0832 | 31.5922 | 6.777% |  |  | 14.0646 | 13.9936 | 99.5%
|  |  |  | Commercial/Industrial-LT | 50346 |  | 50346 | 10.12% | 246.1281 |  | 246.1281 | 15.42% |  | 42.9448 |  | 42.9448 | 9.213% |  |  | 42.7104 | 42.864 | 100.4%
|  |  |  | Commercial/Industrial-HT | 1714 |  | 1714 | 0.3446% | 554.5273 |  | 554.5273 | 34.73% |  | 276.3011 |  | 276.3011 | 59.27% |  |  | 260.7657 | 262.2605 | 100.6%
|  |  |  | Others | 45714 |  | 45714 | 9.19% | 178.236 |  | 178.236 | 11.16% |  | 31.5187 |  | 31.5187 | 6.762% |  |  | 34.2122 | 23.5282 | 68.77%
Sub-total |  |  |  |  | 482848 | 14572 | 497420 | 100% | 1491.5582 | 105.1019 | 1596.6601 | 100% | 498.4671 | 435.0608 | 31.0832 | 466.144 | 100% | 32.3231 | 6.484% | 417.7777 | 407.871 | 97.63% | 8.702%
19 | RAMANAGARA | 267 | KANAKAPUR | Residential | 134719 |  | 134719 | 71% | 48.9118 |  | 48.9118 | 11.79% | 226.5781 | 14.2383 |  | 14.2383 | 6.638% | 12.0852 | 5.334% | 10.51 | 10.2101 | 97.15%
|  |  |  | Agricultural | 49 | 30418 | 30467 | 16.06% | 0.46115 | 142.8554 | 143.3166 | 34.55% |  | 2.2171 | 62.6975 | 64.9146 | 30.26% |  |  | 28.8861 | 28.427 | 98.41%
|  |  |  | Commercial/Industrial-LT | 13922 |  | 13922 | 7.337% | 44.785 |  | 44.785 | 10.8% |  | 6.4885 |  | 6.4885 | 3.025% |  |  | 6.6308 | 6.5536 | 98.84%
|  |  |  | Commercial/Industrial-HT | 295 |  | 295 | 0.1555% | 89.7549 |  | 89.7549 | 21.64% |  | 39.9305 |  | 39.9305 | 18.62% |  |  | 37.755 | 37.5581 | 99.48%
|  |  |  | Others | 10336 |  | 10336 | 5.447% | 88.0472 |  | 88.0472 | 21.23% |  | 88.9211 |  | 88.9211 | 41.46% |  |  | 56.2619 | 49.2132 | 87.47%
Sub-total |  |  |  |  | 159321 | 30418 | 189739 | 100% | 271.9601 | 142.8554 | 414.8155 | 100% | 226.5781 | 151.7954 | 62.6975 | 214.4929 | 100% | 12.0852 | 5.334% | 140.0438 | 131.962 | 94.23% | 10.8%
20 | RAMANAGARA | 267 | MAGADI | Residential | 132109 |  | 132109 | 71.1% | 72.8433 |  | 72.8433 | 17.65% | 133.6332 | 13.3622 |  | 13.3622 | 11.17% | 14.0197 | 10.49% | 9.8522 | 9.7014 | 98.47%
|  |  |  | Agricultural | 235 | 18880 | 19115 | 10.29% | 1.2598 | 91.7869 | 93.0468 | 22.55% |  | 0.4936 | 43.8465 | 44.3401 | 37.07% |  |  | 19.6816 | 19.8811 | 101%
|  |  |  | Commercial/Industrial-LT | 19708 |  | 19708 | 10.61% | 113.6074 |  | 113.6074 | 27.53% |  | 23.855 |  | 23.855 | 19.94% |  |  | 21.3852 | 21.5176 | 100.6%
|  |  |  | Commercial/Industrial-HT | 296 |  | 296 | 0.1593% | 93.0333 |  | 93.0333 | 22.54% |  | 30.7384 |  | 30.7384 | 25.7% |  |  | 29.2465 | 29.2369 | 99.97%
|  |  |  | Others | 14568 |  | 14568 | 7.841% | 40.1807 |  | 40.1807 | 9.736% |  | 7.3178 |  | 7.3178 | 6.118% |  |  | 7.9757 | 3.8786 | 48.63%
Sub-total |  |  |  |  | 166916 | 18880 | 185796 | 100% | 320.9245 | 91.7869 | 412.7115 | 100% | 133.6332 | 75.767 | 43.8465 | 119.6135 | 100% | 14.0197 | 10.49% | 88.1411 | 84.2155 | 95.55% | 14.48%
21 | KOLAR | 264 | KOLAR | Residential | 200829 |  | 200829 | 72.3% | 93.2632 |  | 93.2632 | 15.65% | 247.1074 | 19.9055 |  | 19.9055 | 9.45% | 36.4748 | 14.76% | 15.1798 | 14.4441 | 95.15%
|  |  |  | Agricultural | 52 | 37889 | 37941 | 13.66% | 0.43992 | 280.9361 | 281.3761 | 47.21% |  | 4.5461 | 99.3458 | 103.8919 | 49.32% |  |  | 45.706 | 46.3334 | 101.4%
|  |  |  | Commercial/Industrial-LT | 28147 |  | 28147 | 10.13% | 71.1054 |  | 71.1054 | 11.93% |  | 11.1649 |  | 11.1649 | 5.301% |  |  | 11.5596 | 11.4858 | 99.36%
|  |  |  | Commercial/Industrial-HT | 173 |  | 173 | 0.06228% | 85.5423 |  | 85.5423 | 14.35% |  | 34.3543 |  | 34.3543 | 16.31% |  |  | 34.3908 | 34.0873 | 99.12%
|  |  |  | Others | 10678 |  | 10678 | 3.844% | 64.6763 |  | 64.6763 | 10.85% |  | 41.316 |  | 41.316 | 19.62% |  |  | 32.4157 | 3.2076 | 9.895%
Sub-total |  |  |  |  | 239879 | 37889 | 277768 | 100% | 315.0272 | 280.9361 | 595.9633 | 100% | 247.1074 | 111.2869 | 99.3458 | 210.6327 | 100% | 36.4748 | 14.76% | 139.2519 | 109.5582 | 78.68% | 32.94%
22 | KOLAR | 264 | KGF | Residential | 311559 |  | 311559 | 70.22% | 208.6081 |  | 208.6081 | 21.38% | 354.8749 | 35.3628 |  | 35.3628 | 11.41% | 45.0606 | 12.7% | 26.3813 | 25.2728 | 95.8%
|  |  |  | Agricultural | 172 | 66755 | 66927 | 15.08% | 1.6867 | 368.7368 | 370.4235 | 37.97% |  | 1.1884 | 133.7024 | 134.8908 | 43.54% |  |  | 60.0072 | 59.9968 | 99.98%
|  |  |  | Commercial/Industrial-LT | 44082 |  | 44082 | 9.936% | 129.7936 |  | 129.7936 | 13.31% |  | 18.2546 |  | 18.2546 | 5.892% |  |  | 17.7283 | 17.4521 | 98.44%
|  |  |  | Commercial/Industrial-HT | 382 |  | 382 | 0.0861% | 173.2497 |  | 173.2497 | 17.76% |  | 55.1743 |  | 55.1743 | 17.81% |  |  | 51.7975 | 51.8696 | 100.1%
|  |  |  | Others | 20721 |  | 20721 | 4.67% | 93.4262 |  | 93.4262 | 9.577% |  | 66.1318 |  | 66.1318 | 21.35% |  |  | 50.6092 | 8.8111 | 17.41%
Sub-total |  |  |  |  | 376916 | 66755 | 443671 | 100% | 606.7643 | 368.7368 | 975.5011 | 100% | 354.8749 | 176.1119 | 133.7024 | 309.8143 | 100% | 45.0606 | 12.7% | 206.5234 | 163.4025 | 79.12% | 30.93%
23 | KOLAR | 264 | CHIKKABALLAPURA | Residential | 239800 |  | 239800 | 67.99% | 96.9563 |  | 96.9563 | 14.17% | 285.217 | 26.4067 |  | 26.4067 | 10.6% | 36.2113 | 12.7% | 19.8223 | 19.4948 | 98.35%
|  |  |  | Agricultural | 144 | 61457 | 61601 | 17.47% | 1.1989 | 342.78 | 343.9789 | 50.26% |  | 1.2654 | 141.1706 | 142.436 | 57.2% |  |  | 63.4255 | 63.3383 | 99.86%
|  |  |  | Commercial/Industrial-LT | 32473 |  | 32473 | 9.207% | 74.0893 |  | 74.0893 | 10.83% |  | 10.694 |  | 10.694 | 4.295% |  |  | 11.2438 | 11.1859 | 99.49%
|  |  |  | Commercial/Industrial-HT | 210 |  | 210 | 0.05954% | 94.4299 |  | 94.4299 | 13.8% |  | 32.9844 |  | 32.9844 | 13.25% |  |  | 32.9009 | 32.8931 | 99.98%
|  |  |  | Others | 18617 |  | 18617 | 5.278% | 74.964 |  | 74.964 | 10.95% |  | 36.4846 |  | 36.4846 | 14.65% |  |  | 31.1253 | 12.3862 | 39.79%
Sub-total |  |  |  |  | 291244 | 61457 | 352701 | 100% | 341.6384 | 342.78 | 684.4184 | 100% | 285.217 | 107.8351 | 141.1706 | 249.0057 | 100% | 36.2113 | 12.7% | 158.5179 | 139.2983 | 87.88% | 23.28%
24 | KOLAR | 264 | CHINTHAMANI | Residential | 164557 |  | 164557 | 68.26% | 70.1487 |  | 70.1487 | 15.92% | 196.8036 | 16.4595 |  | 16.4595 | 9.712% | 27.3347 | 13.89% | 12.7322 | 12.39 | 97.31%
|  |  |  | Agricultural | 43 | 43027 | 43070 | 17.86% | 0.30173 | 260.7706 | 261.0723 | 59.23% |  | 0.041323 | 111.9356 | 111.9769 | 66.08% |  |  | 49.8315 | 50.1873 | 100.7%
|  |  |  | Commercial/Industrial-LT | 23878 |  | 23878 | 9.904% | 59.9967 |  | 59.9967 | 13.61% |  | 8.9978 |  | 8.9978 | 5.309% |  |  | 8.8992 | 8.9581 | 100.7%
|  |  |  | Commercial/Industrial-HT | 54 |  | 54 | 0.0224% | 6.8136 |  | 6.8136 | 1.546% |  | 2.2833 |  | 2.2833 | 1.347% |  |  | 2.2482 | 2.1439 | 95.36%
|  |  |  | Others | 9527 |  | 9527 | 3.952% | 42.7321 |  | 42.7321 | 9.695% |  | 29.7515 |  | 29.7515 | 17.56% |  |  | 25.5152 | 6.1472 | 24.09%
Sub-total |  |  |  |  | 198059 | 43027 | 241086 | 100% | 179.9928 | 260.7706 | 440.7634 | 100% | 196.8036 | 57.5334 | 111.9356 | 169.4689 | 100% | 27.3347 | 13.89% | 99.2264 | 79.8264 | 80.45% | 30.72%
25 | DAVANGERE | 263 | DAVANAGERE | Residential | 383898 |  | 383898 | 66.47% | 295.346 |  | 295.346 | 28.47% | 332.3136 | 58.7263 |  | 58.7263 | 20.09% | 40.0221 | 12.04% | 43.9775 | 40.2327 | 91.48%
|  |  |  | Agricultural | 24 | 91177 | 91201 | 15.79% | 0.21921 | 416.2358 | 416.455 | 40.15% |  | 0.011334 | 170.116 | 170.1273 | 58.2% |  |  | 75.1137 | 76.1304 | 101.4%
|  |  |  | Commercial/Industrial-LT | 55862 |  | 55862 | 9.672% | 164.1992 |  | 164.1992 | 15.83% |  | 21.4984 |  | 21.4984 | 7.355% |  |  | 23.5557 | 23.415 | 99.4%
|  |  |  | Commercial/Industrial-HT | 219 |  | 219 | 0.03792% | 45.8396 |  | 45.8396 | 4.419% |  | 15.4331 |  | 15.4331 | 5.28% |  |  | 16.2818 | 15.9697 | 98.08%
|  |  |  | Others | 46400 |  | 46400 | 8.034% | 115.4075 |  | 115.4075 | 11.13% |  | 26.5064 |  | 26.5064 | 9.068% |  |  | 23.7007 | 11.7435 | 49.55%
Sub-total |  |  |  |  | 486403 | 91177 | 577580 | 100% | 621.0115 | 416.2358 | 1037.2473 | 100% | 332.3136 | 122.1755 | 170.116 | 292.2915 | 100% | 40.0221 | 12.04% | 182.6294 | 167.4912 | 91.71% | 19.33%
26 | DAVANGERE | 263 | CHITRADURGA | Residential | 265937 |  | 265937 | 66.2% | 146.4265 |  | 146.4265 | 22.76% | 251.7088 | 31.516 |  | 31.516 | 15.06% | 42.409 | 16.85% | 24.3078 | 23.3533 | 96.07%
|  |  |  | Agricultural | 34 | 80630 | 80664 | 20.08% | 0.24177 | 310.1127 | 310.3544 | 48.25% |  | 0.016755 | 145.1623 | 145.1791 | 69.36% |  |  | 64.3103 | 64.9056 | 100.9%
|  |  |  | Commercial/Industrial-LT | 31370 |  | 31370 | 7.809% | 81.0265 |  | 81.0265 | 12.6% |  | 10.2504 |  | 10.2504 | 4.897% |  |  | 11.3437 | 11.2793 | 99.43%
|  |  |  | Commercial/Industrial-HT | 102 |  | 102 | 0.02539% | 24.8999 |  | 24.8999 | 3.871% |  | 6.274 |  | 6.274 | 2.998% |  |  | 6.6476 | 6.5415 | 98.4%
|  |  |  | Others | 23632 |  | 23632 | 5.883% | 80.5288 |  | 80.5288 | 12.52% |  | 16.0803 |  | 16.0803 | 7.683% |  |  | 14.6028 | 8.0119 | 54.87%
Sub-total |  |  |  |  | 321075 | 80630 | 401705 | 100% | 333.1235 | 310.1127 | 643.2362 | 100% | 251.7088 | 64.1375 | 145.1623 | 209.2998 | 100% | 42.409 | 16.85% | 121.2122 | 114.0915 | 94.13% | 21.73%
27 | DAVANGERE | 263 | HARIHARA | Residential | 226446 |  | 226446 | 68.16% | 86.9554 |  | 86.9554 | 15.68% | 205.7832 | 26.1584 |  | 26.1584 | 14.61% | 26.7626 | 13.01% | 19.8026 | 16.1738 | 81.68%
|  |  |  | Agricultural | 69 | 67606 | 67675 | 20.37% | 1.0465 | 264.4592 | 265.5057 | 47.87% |  | 0.090342 | 111.5727 | 111.663 | 62.37% |  |  | 49.3142 | 49.7691 | 100.9%
|  |  |  | Commercial/Industrial-LT | 23680 |  | 23680 | 7.128% | 67.0606 |  | 67.0606 | 12.09% |  | 7.8166 |  | 7.8166 | 4.366% |  |  | 8.5814 | 8.3855 | 97.72%
|  |  |  | Commercial/Industrial-HT | 113 |  | 113 | 0.03402% | 51.053 |  | 51.053 | 9.205% |  | 12.0943 |  | 12.0943 | 6.756% |  |  | 12.7557 | 12.4861 | 97.89%
|  |  |  | Others | 14291 |  | 14291 | 4.302% | 84.0592 |  | 84.0592 | 15.16% |  | 21.2884 |  | 21.2884 | 11.89% |  |  | 17.8469 | 14.2728 | 79.97%
Sub-total |  |  |  |  | 264599 | 67606 | 332205 | 100% | 290.1747 | 264.4592 | 554.6339 | 100% | 205.7832 | 67.4479 | 111.5727 | 179.0206 | 100% | 26.7626 | 13.01% | 108.3007 | 101.0873 | 93.34% | 18.8%
28 | DAVANGERE | 263 | HIRIYURU | Residential | 207913 |  | 207913 | 66.36% | 75.5466 |  | 75.5466 | 14.68% | 251.1852 | 20.3407 |  | 20.3407 | 10.19% | 51.6009 | 20.54% | 15.8307 | 14.5271 | 91.77%
|  |  |  | Agricultural | 66 | 65675 | 65741 | 20.98% | 0.5066 | 267.1327 | 267.6393 | 51.99% |  | 0.011825 | 123.2938 | 123.3056 | 61.78% |  |  | 54.8154 | 55.2215 | 100.7%
|  |  |  | Commercial/Industrial-LT | 23776 |  | 23776 | 7.589% | 72.9508 |  | 72.9508 | 14.17% |  | 9.5888 |  | 9.5888 | 4.804% |  |  | 10.1008 | 10.0212 | 99.21%
|  |  |  | Commercial/Industrial-HT | 71 |  | 71 | 0.02266% | 39.5865 |  | 39.5865 | 7.69% |  | 20.5756 |  | 20.5756 | 10.31% |  |  | 19.6002 | 19.3966 | 98.96%
|  |  |  | Others | 15808 |  | 15808 | 5.045% | 59.0243 |  | 59.0243 | 11.47% |  | 25.7736 |  | 25.7736 | 12.91% |  |  | 19.9825 | 3.688 | 18.46%
Sub-total |  |  |  |  | 247634 | 65675 | 313309 | 100% | 247.6149 | 267.1327 | 514.7476 | 100% | 251.1852 | 76.2905 | 123.2938 | 199.5843 | 100% | 51.6009 | 20.54% | 120.3296 | 102.8545 | 85.48% | 32.08%
29 | TUMKUR | 253 | TUMKUR | Residential | 334559 |  | 334559 | 65.48% | 250.7156 |  | 250.7156 | 23.24% | 465.5076 | 44.9874 |  | 44.9874 | 11.92% | 88.246 | 18.96% | 33.1132 | 32.1554 | 97.11%
|  |  |  | Agricultural | 59 | 83328 | 83387 | 16.32% | 0.47568 | 386.9242 | 387.3999 | 35.91% |  | 0.061379 | 207.2958 | 207.3572 | 54.96% |  |  | 91.8994 | 92.6519 | 100.8%
|  |  |  | Commercial/Industrial-LT | 54616 |  | 54616 | 10.69% | 161.8561 |  | 161.8561 | 15% |  | 20.3956 |  | 20.3956 | 5.406% |  |  | 22.1151 | 21.9565 | 99.28%
|  |  |  | Commercial/Industrial-HT | 622 |  | 622 | 0.1217% | 165.2641 |  | 165.2641 | 15.32% |  | 77.6482 |  | 77.6482 | 20.58% |  |  | 70.6092 | 68.2942 | 96.72%
|  |  |  | Others | 37738 |  | 37738 | 7.386% | 113.6814 |  | 113.6814 | 10.54% |  | 26.8732 |  | 26.8732 | 7.123% |  |  | 25.3587 | 9.6057 | 37.88%
Sub-total |  |  |  |  | 427594 | 83328 | 510922 | 100% | 691.993 | 386.9242 | 1078.9171 | 100% | 465.5076 | 169.9658 | 207.2958 | 377.2616 | 100% | 88.246 | 18.96% | 243.0956 | 224.6637 | 92.42% | 25.1%
30 | TUMKUR | 253 | TIPTUR | Residential | 204462 |  | 204462 | 61.33% | 82.6194 |  | 82.6194 | 13.64% | 241.6896 | 16.5316 |  | 16.5316 | 8.398% | 44.8389 | 18.55% | 12.9978 | 12.9079 | 99.31%
|  |  |  | Agricultural | 66 | 89871 | 89937 | 26.98% | 0.43732 | 383.6789 | 384.1163 | 63.41% |  | 0.026957 | 155.0311 | 155.058 | 78.77% |  |  | 68.6594 | 69.5756 | 101.3%
|  |  |  | Commercial/Industrial-LT | 26910 |  | 26910 | 8.071% | 73.1281 |  | 73.1281 | 12.07% |  | 8.5955 |  | 8.5955 | 4.367% |  |  | 9.0799 | 9.226 | 101.6%
|  |  |  | Commercial/Industrial-HT | 63 |  | 63 | 0.0189% | 18.2954 |  | 18.2954 | 3.02% |  | 4.0523 |  | 4.0523 | 2.059% |  |  | 4.2503 | 4.6513 | 109.4%
|  |  |  | Others | 12028 |  | 12028 | 3.608% | 47.631 |  | 47.631 | 7.863% |  | 12.6132 |  | 12.6132 | 6.408% |  |  | 11.3515 | 3.9168 | 34.5%
Sub-total |  |  |  |  | 243529 | 89871 | 333400 | 100% | 222.1112 | 383.6789 | 605.7902 | 100% | 241.6896 | 41.8196 | 155.0311 | 196.8507 | 100% | 44.8389 | 18.55% | 106.3388 | 100.2776 | 94.3% | 23.19%
31 | TUMKUR | 253 | MADHUGIRI | Residential | 305219 |  | 305219 | 69.63% | 113.3436 |  | 113.3436 | 15.94% | 362.7715 | 23.8529 |  | 23.8529 | 8.141% | 69.7752 | 19.23% | 18.6319 | 18.0312 | 96.78%
|  |  |  | Agricultural | 47 | 83995 | 84042 | 19.17% | 0.3925 | 425.1671 | 425.5596 | 59.83% |  | 0.027716 | 215.4391 | 215.4668 | 73.54% |  |  | 95.746 | 96.1893 | 100.5%
|  |  |  | Commercial/Industrial-LT | 30498 |  | 30498 | 6.957% | 73.7115 |  | 73.7115 | 10.36% |  | 9.3171 |  | 9.3171 | 3.18% |  |  | 9.9997 | 9.9697 | 99.7%
|  |  |  | Commercial/Industrial-HT | 60 |  | 60 | 0.01369% | 28.1729 |  | 28.1729 | 3.961% |  | 12.9385 |  | 12.9385 | 4.416% |  |  | 11.1764 | 11.2737 | 100.9%
|  |  |  | Others | 18544 |  | 18544 | 4.23% | 70.4865 |  | 70.4865 | 9.91% |  | 31.421 |  | 31.421 | 10.72% |  |  | 26.304 | 3.9146 | 14.88%
Sub-total |  |  |  |  | 354368 | 83995 | 438363 | 100% | 286.107 | 425.1671 | 711.2741 | 100% | 362.7715 | 77.5572 | 215.4391 | 292.9963 | 100% | 69.7752 | 19.23% | 161.8579 | 139.3786 | 86.11% | 30.45%
32 | TUMKUR | 253 | KUNIGAL | Residential | 84029 |  | 84029 | 64.74% | 34.1495 |  | 34.1495 | 12.75% | 95.5903 | 6.8825 |  | 6.8825 | 8.551% | 15.1027 | 15.8% | 5.229 | 5.0102 | 95.82%
|  |  |  | Agricultural | 59 | 30577 | 30636 | 23.6% | 0.54422 | 148.5385 | 149.0828 | 55.65% |  | 0.054031 | 53.1554 | 53.2094 | 66.11% |  |  | 23.4986 | 24.042 | 102.3%
|  |  |  | Commercial/Industrial-LT | 9795 |  | 9795 | 7.547% | 27.9108 |  | 27.9108 | 10.42% |  | 3.4229 |  | 3.4229 | 4.253% |  |  | 3.7586 | 3.6967 | 98.35%
|  |  |  | Commercial/Industrial-HT | 64 |  | 64 | 0.04931% | 39.2318 |  | 39.2318 | 14.64% |  | 9.6785 |  | 9.6785 | 12.02% |  |  | 10.5411 | 8.8209 | 83.68%
|  |  |  | Others | 5263 |  | 5263 | 4.055% | 17.5357 |  | 17.5357 | 6.545% |  | 7.2944 |  | 7.2944 | 9.063% |  |  | 6.9418 | 1.612 | 23.22%
Sub-total |  |  |  |  | 99210 | 30577 | 129787 | 100% | 119.372 | 148.5385 | 267.9106 | 100% | 95.5903 | 27.3322 | 53.1554 | 80.4876 | 100% | 15.1027 | 15.8% | 49.969 | 43.1818 | 86.42% | 27.24%
At Company Level |  |  | BESCOM | Residential | 9879069 |  | 9879069 | 73.33% | 13419.1101 |  | 13419.1101 | 40.17% | 8970.7625 | 2169.843 |  | 2169.843 | 27.01% | 937.5673 | 10.45% | 1734.9471 | 1692.2887 | 97.54%
|  |  |  | Agricultural | 2535 | 996232 | 998767 | 7.414% | 17.6073 | 4912.1471 | 4929.7544 | 14.76% |  | 29.4664 | 2087.9902 | 2117.4566 | 26.36% |  |  | 938.8999 | 950.276 | 101.2%
|  |  |  | Commercial/Industrial-LT | 1471818 |  | 1471818 | 10.93% | 5415.9441 |  | 5415.9441 | 16.21% |  | 920.7857 |  | 920.7857 | 11.46% |  |  | 963.9619 | 951.156 | 98.67%
|  |  |  | Commercial/Industrial-HT | 16215 |  | 16215 | 0.1204% | 5377.0957 |  | 5377.0957 | 16.1% |  | 1860.2056 |  | 1860.2056 | 23.16% |  |  | 1992.7993 | 1980.7578 | 99.4%
|  |  |  | Others | 1105334 |  | 1105334 | 8.205% | 4265.3222 |  | 4265.3222 | 12.77% |  | 964.9043 |  | 964.9043 | 12.01% |  |  | 887.5927 | 558.8993 | 62.97%
Grand Total |  |  |  |  | 12474971 | 996232 | 13471203 | 100% | 28495.0793 | 4912.1471 | 33407.2264 | 100% | 8970.7625 | 5945.205 | 2087.9902 | 8033.1953 | 100% | 937.5673 | 10.45% | 6518.2008 | 6133.3777 | 94.1% | 15.74%
Color code | Parameter
Please enter name of circle
Please enter circle code
0 | Please enter numeric value or 0
Formula protected
Notes:
1. Note: 996232 Consumers of LT4A (IP Sets below 10 HP) is treated as Unmetered , amounting to energy consumption of 2087.99022035 Units .
I/We undertake that the information supplied in this Document and Pro-forma is accurate to the best of my knowledge and if any of the information supplied is found to be incorrect and such information result into loss to the Central Government or State Government or any of the authority under them or any other person affected, I/We undertake to indemnify such loss.
Signature
Name of Authorised Signatory: CGM (Operations) | [15 empty] | Name of the Energy Manager/Auditor : Sri Basavaraju .H .B
Name of the DISCOM:BESCOM | [15 empty] | Registration Number : |  | 6827
Full Address:- KR circle, Nrupathunga Rd, Nunegundlapalli, Ambedkar Veedhi, Bengaluru, Karnataka 560001

## Annexure
Annexure -1: Proforma for Quarterly Consumer Category-wise Subsidy Billed/Received/Due for period 01.04.2022 to 30.06.2022 (Q1)
Consumer Category (Separate for each subsidized consumer category) | Billed Energy |  |  | Subsidized Billed Energy |  |  | Applicable rate of Subsidy as notified by State govt. |  | Subsidy Due from State Govt. |  |  | Subsidy Actually Billed / claimed from State Govt. (As against col.12) | Subsidy Received from State Govt. (As against col.13) | Balance Subsidy yet to be Received from State Govt.
| Metered | Un-metered* | Total | Metered (out of col.2) | Un-metered* | Total | Metered Energy** | Un-metered Energy** | Metered Energy | Un-metered Energy | Total
(out of col.3)
| (in kWh) |  |  | (in kWh) |  |  | (in Rs/kWh) |  | (in Rs. Cr.) |  |  | (in Rs. Cr.) | (in Rs. Cr.) | (in Rs. Cr.)
1 | 2 | 3 | 4=2+3 | 5 | 6 | 7=5+6 | 8 | 9 | 10=5X8 | 11=6x9 | 12=10+11 | 13 | 14 | 15=13-14
Residential | 2169843043.78 |  | 2169843043.78 | 45156796.7 |  | 45156796.7 | [5 empty] | 42.4723 | 42.4723 | 0
Agriculture | 29466408.22 | 2087990220.35 | 2117456628.57 |  | 2087990220.35 | 2087990220.35 | [5 empty] | 926.9477 | 706.6177 | 1211.16
Commercial/Industrial – LT | 920785708.07 |  | 920785708.07 |  |  | 0
Commercial/Industrial - HT | 1860205564.77 |  | 1860205564.77 |  |  | 0
Other (specify) | 964904323.37 |  | 964904323.37 |  |  | 0
Total | 5945205048.21 | 2087990220.35 | 8033195268.56 | 45156796.7 | 2087990220.35 | 2133147017.05 | [5 empty] | 969.42 | 749.09 | 1211.16

## Feeder Level Details
(Details of Feeder-wise losses)
Period from April 2022 to June 2022
SI No. | Zone | Received at Circle (In MU) | Received at Division (In MU) | Received at Sub-division (In MU) | Name of the Station | Feeder Code/ID | Feeder Name | Type of Feeder ( Urban/Mixed/Industrial/Agricultural/Rural) | Type of feeder meter ( AMI/AMR/Other) | Received at Feeder (Final in MU) (Import) | Feeder Consumption in MU | Export | NC in MU | %T&D loss | AT&C losses | % Data Received through Automatically (if feeder AMR/AMI) | Remarks
1 | BMANZ | NORTH | JALAHALLI | C3 | ABBIGERE_66 | 1120203902010101 | F02-RAGAVENDRA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.1518 | 2.0178 | 0 | 2.1518 | 6.2276 | 16.8461 | Note: Communication work is under process under the supervision of Scada KPTCL
2 | BMANZ | NORTH | JALAHALLI | C3 | ABBIGERE_66 | 1120203902010102 | F03-LAKSHMIPURA | URBAN MIXED LOAD | DLMS Meter | 2.0423 | 1.5587 | 0.395 | 1.6473 | 5.3808 | 6.8794
3 | BMANZ | NORTH | JALAHALLI | C3 | ABBIGERE_66 | 1120203902010104 | F04-ABBIGERE-INDL-AREA | URBAN MIXED LOAD | DLMS Meter | 3.4054 | 3.3471 | 0 | 3.4054 | 1.7112 | 3.1616
4 | BMANZ | NORTH | JALAHALLI | C3 | ABBIGERE_66 | 1120203902010103 | F05-SINGAPURA | URBAN MIXED LOAD | DLMS Meter | 4.817 | 4.5424 | 0 | 4.817 | 5.7011 | 15.7661
5 | BMANZ | NORTH | JALAHALLI | N9 | ABBIGERE_66 | 1120203902010105 | F06-ICTS KALENAHALLY | URBAN MIXED LOAD | DLMS Meter | 0.4791 | 0.47378 | 0 | 0.4791 | 1.1114 | 2.9262
6 | BMANZ | NORTH | JALAHALLI | C3 | ABBIGERE_66 | 1120203902020101 | F08-KALANAGAR | URBAN MIXED LOAD | DLMS Meter | 2.7547 | 2.5532 | 0 | 2.7547 | 7.3149 | 15.7049
7 | BMANZ | NORTH | JALAHALLI | C3 | ABBIGERE_66 | 1120203902020302 | F09-KUVEMPUNAGAR | URBAN MIXED LOAD | DLMS Meter | 2.1782 | 1.6609 | 0.41 | 1.7682 | 6.064 | 24.2751
8 | BMANZ | NORTH | JALAHALLI | C3 | ABBIGERE_66 | 1120203902020303 | F10-KANSHIRAMANAGAR | URBAN MIXED LOAD | DLMS Meter | 2.8435 | 2.6697 | 0 | 2.8435 | 6.1121 | 8.9849
9 | BMANZ | NORTH | JALAHALLI | C9 | ABBIGERE_66 | 1120203902020304 | F11-VARADRAJNAGR | URBAN MIXED LOAD | DLMS Meter | 3.835 | 3.2999 | 0.255 | 3.58 | 7.8243 | 13.4819
10 | BMANZ | NORTH | JALAHALLI | N9 | ABBIGERE_66 | 1120203902020301 | F12-MEDIAGRAHARA | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
11 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | ACHALU_66 | 1220303907010101 | F01-THOTAHALLI | AGRI | DLMS Meter | 0.71132 | 0.64032 | 0 | 0.71132 | 9.9817 | 9.9817
12 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | ACHALU_66 | 1220303907010102 | F02-GERAHALLI | AGRI | DLMS Meter | 1.0582 | 0.51035 | 0.491 | 0.5672 | 10.0227 | 10.0227
13 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | ACHALU_66 | 1220303907010103 | F03-ACCHALU | NJY | DLMS Meter | 0.6094 | 0.552 | 0 | 0.6094 | 9.4197 | 40.122
14 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | ACHALU_66 | 1220303907010104 | F04-LAGUNA | INDUSTRIAL | DLMS Meter | 0.2869 | 0.28333 | 0.0005 | 0.2864 | 1.0728 | 1.0728
15 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | ACHALU_66 | 1220303907020103 | F05-BS DODDI | AGRI | DLMS Meter | 0.8783 | 0.79027 | 0 | 0.8783 | 10.0231 | 10.0231
16 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | ACHALU_66 | 1220303907020101 | F06-MADESHWARA | NJY | DLMS Meter | 0.1254 | 0.11316 | 0 | 0.1254 | 9.76 | 95.799
17 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | ACHALU_66 | 1220303907020102 | F07-KALEGOWDANADODDI | AGRI | DLMS Meter | 0.0278 | 0.025018 | 0 | 0.0278 | 10.0072 | 10.0072
18 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905020101 | F01-GOWNIPALLI | AGRI | DLMS Meter | 1.208 | 0.55816 | 0.588 | 0.62001 | 9.9755 | 9.9755
19 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905020102 | F02-MUDIMADAGU | AGRI | DLMS Meter | 0.61256 | 0.036319 | 0.5722 | 0.04036 | 10.0124 | 10.0124
20 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905020103 | F03-ADDAGAL | AGRI | DLMS Meter | 0.90422 | 0.81393 | 0 | 0.90422 | 9.9856 | 9.9856
21 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905010301 | F04-BYRAGANAPALII NJY | NJY | DLMS Meter | 0.42843 | 0.39122 | 0 | 0.42843 | 8.6832 | 72.7062
22 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905010302 | F05-KOORIGEPALLI | AGRI | DLMS Meter | 0.76211 | 0.68599 | 0 | 0.76211 | 9.9879 | 9.9879
23 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905010303 | F06-MARASANAPALLI | AGRI | DLMS Meter | 0.66878 | 0.60189 | 0 | 0.66878 | 10.0024 | 10.0024
24 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905010304 | F07-CHILLORPALLI | AGRI | DLMS Meter | 0.82236 | 0.21156 | 0.58728 | 0.23508 | 10.0034 | 10.0441
25 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905020104 | F08-GANDHINAGAR NJY | NJY | DLMS Meter | 0.58418 | 0.33164 | 0.21908 | 0.3651 | 9.1652 | 87.2847
26 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905020105 | F09-ANEPALLI NJY | NJY | DLMS Meter | 0.2458 | 0.22669 | 0 | 0.2458 | 7.774 | 79.7847
27 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905010501 | F10-BALEVARIPALLI | AGRI | DLMS Meter | 0.7004 | 0 | 0.7004 | 0 | 0 | #DIV/0!
28 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905010502 | F11-KADIRAMAPALLI | AGRI | DLMS Meter | 0.68 | 0.61193 | 0 | 0.68 | 10.0106 | 10.0106
29 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905010503 | F12-SRIRAMPURA | AGRI | DLMS Meter | 0.708 | 0.6371 | 0 | 0.708 | 10.0147 | 10.0147
30 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905010504 | F13-G.BYAPALLI | AGRI | DLMS Meter | 0.4138 | 0.31854 | 0.06 | 0.3538 | 9.9666 | 9.9666
31 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905010505 | F14-MALLIMORAPALLI | NJY | DLMS Meter | 0.21908 | 0.19869 | 0 | 0.21908 | 9.3093 | 73.7334
32 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | ADDAGAL_66 | 1230103905020501 | F15-DIGAVACHINTHAPALLI | AGRI | DLMS Meter | 1.192 | 1.0726 | 0 | 1.192 | 10.0131 | 10.0131
33 | BMASZ | SOUTH | KORAMANGALA | S16 | ADUGODI_66 | 1110102902010301 | F01-BOMMANAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.1548 | 2.7036 | 0.25 | 2.9048 | 6.9252 | 16.7688
34 | BMASZ | SOUTH | JAYANAGAR | S2 | ADUGODI_66 | 1110102902020305 | F02-NEW-MICO-ROAD | URBAN MIXED LOAD | DLMS Meter | 2.3418 | 2.2376 | 0 | 2.3418 | 4.4486 | 7.2807
35 | BMASZ | SOUTH | KORAMANGALA | S16 | ADUGODI_66 | 1110102902020301 | F03-GURAPPAN-PALYA | URBAN MIXED LOAD | DLMS Meter | 0.50424 | 0.45712 | 0 | 0.50424 | 9.3445 | 15.2089
36 | BMASZ | SOUTH | JAYANAGAR | S2 | ADUGODI_66 | 1110102902020308 | F04-KMF | URBAN MIXED LOAD | DLMS Meter | 2.9926 | 2.8743 | 0.0043551 | 2.9883 | 3.8131 | 7.6311
37 | BMASZ | SOUTH | JAYANAGAR | S2 | ADUGODI_66 | 1110102902020302 | F05-WILSON-GARDEN | URBAN MIXED LOAD | DLMS Meter | 1.7754 | 1.2585 | 0.46644 | 1.309 | 3.8617 | 7.0338
38 | BMASZ | SOUTH | KORAMANGALA | S4 | ADUGODI_66 | 1110102902010101 | F06-FNDRI | URBAN MIXED LOAD | DLMS Meter | 3.7052 | 3.4234 | 0.118 | 3.5872 | 4.5666 | 7.7702
39 | BMASZ | SOUTH | JAYANAGAR | S2 | ADUGODI_66 | 1110102902010107 | F07-SALARPURIA-TOWERS | COMMERCIAL | DLMS Meter | 1.6037 | 1.5504 | 0 | 1.6037 | 3.3224 | 3.3234
40 | BMASZ | SOUTH | KORAMANGALA | S4 | ADUGODI_66 | 1110102902010102 | F08-KUDREMUKH | URBAN MIXED LOAD | DLMS Meter | 3.2005 | 3.134 | 0 | 3.2005 | 2.0788 | 2.2355
41 | BMASZ | SOUTH | KORAMANGALA | S16 | ADUGODI_66 | 1110102902010103 | F09-SJR | URBAN MIXED LOAD | DLMS Meter | 3.4054 | 2.5564 | 0.59605 | 2.8093 | 9.0038 | 14.7157
42 | BMASZ | SOUTH | KORAMANGALA | S4 | ADUGODI_66 | 1110102902030501 | F11-JYOTHI-NIVAS | COMMERCIAL | DLMS Meter | 2.2427 | 2.0989 | 0 | 2.2427 | 6.4121 | 6.4121
43 | BMASZ | SOUTH | JAYANAGAR | S2 | ADUGODI_66 | 1110102902030502 | F12-STAR-BAZAAR | COMMERCIAL | DLMS Meter | 0.90867 | 0.72372 | 0.15548 | 0.75319 | 3.9131 | 3.9131
44 | BMASZ | SOUTH | JAYANAGAR | S2 | ADUGODI_66 | 1110102902030503 | F13-ANSAL-KRISHNA-RMU | URBAN MIXED LOAD | DLMS Meter | 1.4373 | 1.0584 | 0.34035 | 1.0969 | 3.5111 | 3.6456
45 | BMASZ | SOUTH | KORAMANGALA | S4 | ADUGODI_66 | 1110102902030504 | F14-KALYANA-MANTAPA | URBAN MIXED LOAD | DLMS Meter | 3.2973 | 2.9834 | 0.103 | 3.1943 | 6.6006 | 7.7683
46 | BMASZ | SOUTH | KORAMANGALA | S4 | ADUGODI_66 | 1110102902030506 | F16-MICO-KML | COMMERCIAL | DLMS Meter | 0.89564 | 0.74175 | 0.12109 | 0.77455 | 4.2344 | 4.2344
47 | BMASZ | SOUTH | JAYANAGAR | S2 | ADUGODI_66 | 1110102902020303 | F17-FORUM | COMMERCIAL | DLMS Meter | 2.1255 | 0.079 | 2.0401 | 0.085384 | 7.4764 | 7.4764
48 | BMASZ | SOUTH | KORAMANGALA | S4 | ADUGODI_66 | 1110102902020304 | F18-MICO-INDUSTRIAL | COMMERCIAL | DLMS Meter | 0.45749 | 0.3408 | 0.072242 | 0.38525 | 11.5371 | 11.5371
49 | BMASZ | SOUTH | JAYANAGAR | S2 | ADUGODI_66 | 1110102902010108 | F19-VENKATAPURAIDLE | URBAN MIXED LOAD | DLMS Meter | 0.72013 | 0.5229 | 0.1763 | 0.54383 | 3.8482 | 3.8482
50 | BMASZ | SOUTH | JAYANAGAR | S2 | ADUGODI_66 | 1110102902010105 | F20-BLORE-DAIRY | COMMERCIAL | DLMS Meter | 3.2716 | 2.7839 | 0.36257 | 2.909 | 4.3026 | 4.3329
51 | BMASZ | SOUTH | KORAMANGALA | S16 | ADUGODI_66 | 1110102902010106 | F21-ORACLE-BG-ROAD | URBAN MIXED LOAD | DLMS Meter | 0.85752 | 0.8472 | 0 | 0.85752 | 1.203 | 1.203
52 | BMASZ | SOUTH | KORAMANGALA | S4 | ADUGODI_66 | 1110102902020306 | F22-STJOHNSWOOD-APPT | DOMESTIC | DLMS Meter | 2.8467 | 2.3511 | 0.322 | 2.5247 | 6.8781 | 6.8781
53 | BMASZ | SOUTH | KORAMANGALA | S4 | ADUGODI_66 | 1110102902030507 | F23-KORMANGALA-RD-BLOCK-RMU | URBAN MIXED LOAD | DLMS Meter | 4.2995 | 3.4952 | 0.551 | 3.7485 | 6.758 | 7.5947
54 | BMASZ | SOUTH | KORAMANGALA | S16 | ADUGODI_66 | 1110102902030508 | F24-UMAYAHOLDING | COMMERCIAL | DLMS Meter | 2.2734 | 2.1244 | 0 | 2.2734 | 6.5532 | 7.1197
55 | BMASZ | SOUTH | KORAMANGALA | S16 | ADUGODI_66 | 1110102902030509 | F25-DAVANAM-JEWELLERS-TOTAL | COMMERCIAL | DLMS Meter | 2.1495 | 1.6791 | 0.35 | 1.7995 | 6.6956 | 6.6956
56 | BMASZ | SOUTH | KORAMANGALA | S4 | ADUGODI_66 | 1110102902030510 | F26-ESSAE-TARRACO | COMMERCIAL | DLMS Meter | 1.486 | 1.4148 | 0 | 1.486 | 4.791 | 8.7163
57 | BMASZ | SOUTH | KORAMANGALA | S16 | ADUGODI_66 | 1110102902020307 | F27-EAST-LAND-HOLDING | COMMERCIAL | DLMS Meter | 3.0419 | 2.872 | 0 | 3.0419 | 5.5853 | 10.5051
58 | BRAZ | RAMANAGAR | MAGADI | MAGADI | AGALKOTE_66 | 1210102901020301 | F01-CHAKRABHAVI | AGRI | DLMS Meter | 0.71172 | 0.52432 | 0.129 | 0.58272 | 10.0216 | 13.3318
59 | BRAZ | RAMANAGAR | MAGADI | MAGADI | AGALKOTE_66 | 1210102901020302 | F02-AGALKOTTE-HAND-POST | AGRI | DLMS Meter | 0.48234 | 0.43418 | 0 | 0.48234 | 9.9847 | 9.9847
60 | BRAZ | RAMANAGAR | MAGADI | MAGADI | AGALKOTE_66 | 1210102901010101 | F03-DANDIGEPURA | AGRI | DLMS Meter | 0.39966 | 0.35968 | 0 | 0.39966 | 10.0025 | 13.6093
61 | BRAZ | RAMANAGAR | MAGADI | MAGADI | AGALKOTE_66 | 1210102901010102 | F04-HULLIKATTE | AGRI | DLMS Meter | 0.69966 | 0.53975 | 0.1 | 0.59966 | 9.9915 | 9.9915
62 | BRAZ | RAMANAGAR | MAGADI | MAGADI | AGALKOTE_66 | 1210102901010103 | F05-KALLUDEVANAHALLI | AGRI | DLMS Meter | 0.67102 | 0.51935 | 0.094 | 0.57702 | 9.9939 | 9.9939
63 | BRAZ | RAMANAGAR | MAGADI | MAGADI | AGALKOTE_66 | 1210102901020303 | F06-JODI HOSAHALLI | AGRI | DLMS Meter | 0.75222 | 0.19982 | 0.53 | 0.22222 | 10.081 | 10.081
64 | BRAZ | RAMANAGAR | MAGADI | MAGADI | AGALKOTE_66 | 1210102901010107 | F08-SEEGEKUPPE NJY | NJY | DLMS Meter | 0.37178 | 0.33623 | 0 | 0.37178 | 9.5625 | 54.3515
65 | BRAZ | RAMANAGAR | MAGADI | MAGADI | AGALKOTE_66 | 1210102901010108 | F09-BYRANHALLI NJY | NJY | DLMS Meter | 0.16616 | 0.12318 | 0.03 | 0.13616 | 9.5313 | 9.5313
66 | BRAZ | RAMANAGAR | MAGADI | MAGADI | AGALKOTE_66 | 1210102901010104 | F10-KORAMANGALA NJY | NJY | DLMS Meter | 0.28739 | 0.26086 | 0 | 0.28739 | 9.2323 | 38.3311
67 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010101 | F01-SULLERI | AGRI | DLMS Meter | 1.1424 | 0.86855 | 0.177 | 0.96536 | 10.0282 | 10.0282
68 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010102 | F02-GARKAHALLIC | AGRI | DLMS Meter | 1.7602 | 1.3663 | 0.242 | 1.5182 | 10.0065 | 10.0065
69 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902020301 | F03-KODAMBAHALLI | AGRI | DLMS Meter | 1.9146 | 1.7234 | 0 | 1.9146 | 9.9886 | 9.9886
70 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010103 | F04-SANTHEMOGENAHALLI | AGRI | DLMS Meter | 0.87791 | 0.79029 | 0 | 0.87791 | 9.9811 | 9.9811
71 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902020302 | F05-SINGARAJIPURA | AGRI | DLMS Meter | 1.0416 | 0.72134 | 0.24 | 0.80156 | 10.008 | 10.008
72 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902020303 | F06-BANAGALLY | AGRI | DLMS Meter | 1.3673 | 1.2307 | 0 | 1.3673 | 9.9883 | 9.9883
73 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902020304 | F07-HAROKOPPA | AGRI | DLMS Meter | 1.2718 | 0.78912 | 0.395 | 0.87685 | 10.0049 | 10.0049
74 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010201 | F08-AKKUR-NJY | NJY | DLMS Meter | 0.45651 | 0.41708 | 0 | 0.45651 | 8.6376 | 41.7628
75 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010202 | F09-JAGADAPURA-NJY | NJY | DLMS Meter | 0.99492 | 0.44526 | 0.506 | 0.48892 | 8.9297 | 41.4813
76 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010203 | F10-AMBADAHALLI NJY | NJY | DLMS Meter | 0.5584 | 0.29948 | 0.2295 | 0.3289 | 8.9447 | 43.2957
77 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010204 | F11-SOGALA | AGRI | DLMS Meter | 0.98128 | 0.70846 | 0.194 | 0.78728 | 10.0113 | 10.0113
78 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010205 | F12-AVHALLI | AGRI | DLMS Meter | 1.1701 | 1.0145 | 0.043 | 1.1271 | 9.9886 | 9.9886
79 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010206 | F13-KADANKANAHALLI | AGRI | DLMS Meter | 0.86772 | 0.71969 | 0.068 | 0.79972 | 10.007 | 10.007
80 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010207 | F14-SULLERI LIFT IRRIGATION | LIFT IRRIGATION | DLMS Meter | 0.01203 | 0.011573 | 0 | 0.01203 | 3.7994 | 99.7185
81 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010208 | F15-VYDYANATHESWARA NJY | NJY | DLMS Meter | 0.4369 | 0.30839 | 0.0985 | 0.3384 | 8.8683 | 35.9563
82 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010104 | F16-THUBINAKERE NJY | NJY | DLMS Meter | 0.57452 | 0.3007 | 0.244 | 0.33052 | 9.0228 | 32.4867
83 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010209 | F17-SADAHALLI | NJY | DLMS Meter | 0.79132 | 0.20225 | 0.5695 | 0.22182 | 8.8211 | 25.3213
84 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010210 | F18-SHANESWARA | AGRI | DLMS Meter | 0.64374 | 0.41105 | 0.187 | 0.45674 | 10.0042 | 10.0042
85 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | AKKURMOLE_66 | 1220105902010211 | F19-PALYA | AGRI | DLMS Meter | 0.86618 | 0.78572 | 0 | 0.86618 | 9.2896 | 9.2896
86 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | ALLIMARANAHALLI_66 | 1220301904010201 | F01- GANALU NJY | NJY | DLMS Meter | 1.1628 | 0.97479 | 0.1125 | 1.0503 | 7.1893 | 16.8727
87 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | ALLIMARANAHALLI_66 | 1220301904010202 | F02-HOSAKOTE | AGRI | DLMS Meter | 1.0757 | 0.96811 | 0 | 1.0757 | 10.0014 | 10.0014
88 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | ALLIMARANAHALLI_66 | 1220301904010203 | F03-SIDDAPURA | AGRI | DLMS Meter | 0.9607 | 0.86036 | 0.0049 | 0.9558 | 9.9856 | 9.9856
89 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | ALLIMARANAHALLI_66 | 1220301904010204 | F04-DIMBADALLI NJY | NJY | DLMS Meter | 0.4988 | 0.34235 | 0.129 | 0.3698 | 7.4234 | 53.6667
90 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | ALURU_66 | 1210104905010203 | F04-ALURU | URBAN MIXED LOAD | DLMS Meter | 2.2654 | 1.9202 | 0.1235 | 2.1419 | 10.3497 | 23.0536
91 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | ALURU_66 | 1210104905010201 | F05-TRIDENT | URBAN MIXED LOAD | DLMS Meter | 6.8698 | 6.3596 | 0 | 6.8698 | 7.4267 | 11.5693
92 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | ALURU_66 | 1210104905010202 | F06-MAKALI | URBAN MIXED LOAD | DLMS Meter | 2.9942 | 2.7492 | 0 | 2.9942 | 8.1822 | 14.5732
93 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | ALURU_66 | 1210104905020201 | F07-GOLDEN_PALMS | URBAN MIXED LOAD | DLMS Meter | 3.6872 | 3.4185 | 0 | 3.6872 | 7.2864 | 7.6029
94 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | ALURU_66 | 1210104905020202 | F08-APMC | URBAN MIXED LOAD | DLMS Meter | 4.1886 | 3.865 | 0 | 4.1886 | 7.7248 | 18.1214
95 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | ALURU_66 | 1210104905020204 | F09-RAJAJINAGAR HOUSING SOCIETY | URBAN MIXED LOAD | DLMS Meter | 0.873 | 0.79313 | 0 | 0.873 | 9.1488 | 18.8299
96 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | ALURU_66 | 1210104905020205 | F10-VASAVI | URBAN MIXED LOAD | DLMS Meter | 1.2572 | 0.31706 | 0.915 | 0.3422 | 7.3463 | 22.2459
97 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | ALURU_66 | 1210104905020203 | F13-HIMALAYA DRUG | INDUSTRIAL | DLMS Meter | 2.841 | 2.8451 | 0 | 2.841 | -0.14425 | -0.14425
98 | BMASZ | SOUTH | KORAMANGALA | S3 | AMARJYOTHI_66 | 1110201902010102 | F02-J-R-LAYOUT | DOMESTIC | DLMS Meter | 4.3879 | 4.1993 | 0.02 | 4.3679 | 3.8612 | 10.2957
99 | BMASZ | SOUTH | KORAMANGALA | S3 | AMARJYOTHI_66 | 1110201902010103 | F03-SASKEN | COMMERCIAL | DLMS Meter | 2.7244 | 2.4557 | 0.132 | 2.5924 | 5.2732 | 8.9371
100 | BMASZ | SOUTH | KORAMANGALA | S3 | AMARJYOTHI_66 | 1110201902020302 | F05-DD-I | URBAN MIXED LOAD | DLMS Meter | 1.182 | 1.1458 | 0.01 | 1.172 | 2.2329 | 2.2329
101 | BMASZ | SOUTH | KORAMANGALA | S3 | AMARJYOTHI_66 | 1110201902020303 | F06-FDDII | DOMESTIC | DLMS Meter | 1.0326 | 1.004 | 0.01 | 1.0226 | 1.8206 | 4.0235
102 | BMASZ | SOUTH | KORAMANGALA | S3 | AMARJYOTHI_66 | 1110201902020304 | F07-FK-R-LAYOUT | DOMESTIC | DLMS Meter | 2.4455 | 2.3187 | 0.1 | 2.3455 | 1.1408 | 3.0021
103 | BMASZ | SOUTH | KORAMANGALA | S3 | AMARJYOTHI_66 | 1110201902020305 | F08-GOLF-CLUB | DOMESTIC | DLMS Meter | 1.5341 | 1.4105 | 0.06 | 1.4741 | 4.3139 | 4.8474
104 | BMASZ | SOUTH | KORAMANGALA | S3 | AMARJYOTHI_66 | 1110201902020306 | F11-GLS-PHASE | COMMERCIAL | DLMS Meter | 1.5663 | 1.5326 | 0.02 | 1.5463 | 0.8819 | 0.8819
105 | BMASZ | SOUTH | KORAMANGALA | S3 | AMARJYOTHI_66 | 1110201902010105 | F12-DIVYASHREE | DOMESTIC | DLMS Meter | 2.9686 | 2.8612 | 0.032 | 2.9366 | 2.5701 | 6.6234
106 | BMASZ | SOUTH | KORAMANGALA | S3 | AMARJYOTHI_66 | 1110201902020404 | F18-24/7 | COMMERCIAL | DLMS Meter | 2.679 | 2.5535 | 0.001 | 2.678 | 4.6517 | 7.5478
107 | BMASZ | SOUTH | KORAMANGALA | S3 | AMARJYOTHI_66 | 1110201902020405 | F19-MYSIS | COMMERCIAL | DLMS Meter | 0.47303 | 0.35079 | 0.1005 | 0.37253 | 5.8362 | 5.8362
108 | BMASZ | SOUTH | KORAMANGALA | S4 | AMARJYOTHI_66 | 1110201902020308 | F21-SALARIPURIA | URBAN MIXED LOAD | DLMS Meter | 2.1806 | 1.9718 | 0.155 | 2.0256 | 2.6532 | 2.6532
109 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907010101 | F01 SIDDAPURA | AGRI | DLMS Meter | 1.3274 | 0.57354 | 0.69 | 0.6374 | 10.0193 | 10.0193
110 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907010102 | F02-HADAVANAHALLI | AGRI | DLMS Meter | 1.4289 | 1.2636 | 0 | 1.4289 | 11.5651 | 11.5651
111 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907010103 | F03-GIRENAHALLI | AGRI | DLMS Meter | 1.5378 | 1.3603 | 0 | 1.5378 | 11.5407 | 11.5407
112 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907010104 | F04-DUNDA | AGRI | DLMS Meter | 0.69 | 0.62106 | 0 | 0.69 | 9.991 | 9.991
113 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907020301 | F06-HARIDASANAHALLI | AGRI | DLMS Meter | 2.0732 | 1.8651 | 0 | 2.0732 | 10.0352 | 10.0352
114 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907020302 | F09-BANASANDRA | AGRI | DLMS Meter | 1.6921 | 1.5228 | 0 | 1.6921 | 10.0043 | 10.0043
115 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907030501 | F11-AMMASANDRA | NJY | DLMS Meter | 0.09084 | 0.047187 | 0.038 | 0.05284 | 10.6983 | 44.1773
116 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907030502 | F12-GUDDADAYANA PALYA | AGRI | DLMS Meter | 0.91274 | 0.82129 | 0 | 0.91274 | 10.0195 | 10.0195
117 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907030503 | F13-HONNENAHALLI | AGRI | DLMS Meter | 0.78786 | 0.70893 | 0 | 0.78786 | 10.0184 | 10.0184
118 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907030504 | F14-HEGGERE | AGRI | DLMS Meter | 0.80176 | 0.72155 | 0 | 0.80176 | 10.0037 | 10.0037
119 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907030505 | F15-BALLEKATTE | AGRI | DLMS Meter | 0.87866 | 0.7907 | 0 | 0.87866 | 10.0109 | 10.0109
120 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907030506 | F16-DANDINASHIVARA-NJY | NJY | DLMS Meter | 0.62254 | 0.5232 | 0.017 | 0.60554 | 13.5981 | 30.4581
121 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907030507 | F17-APPASANDRA-NJY | NJY | DLMS Meter | 0.23065 | 0.20225 | 0 | 0.23065 | 12.3126 | 23.7061
122 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907030508 | F18-MARASANDRA-NJY | NJY | DLMS Meter | 0.49454 | 0.099467 | 0.38 | 0.11454 | 13.1596 | 58.8318
123 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | AMMASANDRA_110 | 1320202907030509 | F19-KUNIKENAHLLI NJY | NJY | DLMS Meter | 0.495 | 0.42874 | 0 | 0.495 | 13.3864 | 33.8208
124 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903010106 | F01-SANABA | AGRI | DLMS Meter | 0.95731 | 0.84331 | 0 | 0.95731 | 11.9082 | 11.9082
125 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903010104 | F02-AMRUTHUR | RURAL MIXED LOAD | DLMS Meter | 0.91644 | 0.80301 | 0 | 0.91644 | 12.3777 | 40.6911
126 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903010105 | F03-MARKONAHALLI | AGRI | DLMS Meter | 0.59788 | 0.52642 | 0 | 0.59788 | 11.9526 | 11.9526
127 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903010103 | F04-NJY 2-PADUVAGARE | NJY | DLMS Meter | 0.21236 | 0.19149 | 0 | 0.21236 | 9.8262 | 52.1919
128 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903010109 | F05-KAGGALAPURA | AGRI | DLMS Meter | 0.89672 | 0.80699 | 0 | 0.89672 | 10.0069 | 10.0069
129 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903020301 | F06-NJY 3-KEELARA | NJY | DLMS Meter | 0.5054 | 0.45769 | 0 | 0.5054 | 9.4397 | 52.8569
130 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903020303 | F07-OLD-YEDIYUR | AGRI | DLMS Meter | 0.83942 | 0.75562 | 0 | 0.83942 | 9.9825 | 9.9825
131 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903020302 | F09-K.H.HALLI | AGRI | DLMS Meter | 1.2943 | 1.1563 | 0 | 1.2943 | 10.6609 | 10.6609
132 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903010102 | F10-KAGGERE | AGRI | DLMS Meter | 1.1186 | 0.98942 | 0 | 1.1186 | 11.5483 | 11.5483
133 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903010101 | F11-NJY 1-KODAGEHALLI | NJY | DLMS Meter | 0.8464 | 0.7595 | 0 | 0.8464 | 10.2665 | 38.2165
134 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903020306 | F12-MALLAPURA | AGRI | DLMS Meter | 0.6303 | 0.56085 | 0 | 0.6303 | 11.0194 | 11.0194
135 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | AMRUTHUR_66 | 1320109903010112 | F13-BASAVAMATTIKERE | AGRI | DLMS Meter | 0.58856 | 0.52773 | 0 | 0.58856 | 10.3357 | 10.3357
136 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903010101 | F01-KUDUR-EXPRESS | AGRI | DLMS Meter | 0.85126 | 0.74947 | 0 | 0.85126 | 11.9572 | 11.9572
137 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903010102 | F02-KUDUR-RURAL | AGRI | DLMS Meter | 0.98902 | 0.87821 | 0 | 0.98902 | 11.2038 | 11.2038
138 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903010103 | F03-YELIYUR | AGRI | DLMS Meter | 1.0158 | 0.91418 | 0 | 1.0158 | 10.0054 | 10.0054
139 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903010104 | F04-NEELATHAHALLI | AGRI | DLMS Meter | 0.78146 | 0.70321 | 0 | 0.78146 | 10.0131 | 10.0131
140 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903020301 | F07-SOMADEVARAPALYA | AGRI | DLMS Meter | 0.38102 | 0.34281 | 0 | 0.38102 | 10.0273 | 10.0273
141 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903020302 | F08-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 2.9223 | 2.6215 | 0 | 2.9223 | 10.2928 | 11.8251
142 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903010107 | F09-KEMPASAGARA | AGRI | DLMS Meter | 0.81288 | 0.73165 | 0 | 0.81288 | 9.993 | 9.993
143 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903020303 | F10-ALKERE | AGRI | DLMS Meter | 1.1719 | 1.0301 | 0 | 1.1719 | 12.0963 | 12.0963
144 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903010106 | F11-RASTHEPALYA NJY | NJY | DLMS Meter | 0.0994 | 0.074704 | 0.018032 | 0.081368 | 8.19 | 50.6563
145 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903010105 | F12-KAPANIPALYA | NJY | DLMS Meter | 0.3156 | 0.27939 | 0 | 0.3156 | 11.472 | 39.9259
146 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903010110 | F13-HOSAHALLI | NJY | DLMS Meter | 0.4736 | 0.42528 | 0 | 0.4736 | 10.2018 | 67.1006
147 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903020304 | F14-RITZEL-INDIA | INDUSTRIAL | DLMS Meter | 0.34056 | 0.34164 | 0 | 0.34056 | -0.31712 | -0.31712
148 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903030502 | F16-UNIVERSAL-GAS | INDUSTRIAL | DLMS Meter | 2.1062 | 2.1064 | 0 | 2.1062 | -0.010208 | -0.010208
149 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903030503 | F17-ECOVINOL | INDUSTRIAL | DLMS Meter | 0.66237 | 0.67155 | 0 | 0.66237 | -1.3859 | -1.3859
150 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903030504 | F18-WIENER-BERGER | INDUSTRIAL | DLMS Meter | 1.7039 | 1.7105 | 0 | 1.7039 | -0.38617 | -0.35481
151 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903010501 | F19-HELTHIUM MEDTECH | INDUSTRIAL | DLMS Meter | 0.44462 | 0.45547 | 0 | 0.44462 | -2.4403 | -2.2983
152 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903030505 | F20-JOHNSON | INDUSTRIAL | DLMS Meter | 1.0742 | 1.0769 | 0 | 1.0742 | -0.2467 | -0.048343
153 | BRAZ | KOLAR | KGF | KGF | ANDERSONPET_66 | 1230201901010101 | F01-BANAGIRI | AGRI | DLMS Meter | 0.71082 | 0.63949 | 0 | 0.71082 | 10.0355 | 10.0355
154 | BRAZ | KOLAR | KGF | KGF | ANDERSONPET_66 | 1230201901010102 | F02-KEMPAPURA | AGRI | DLMS Meter | 1.1146 | 1.0029 | 0 | 1.1146 | 10.0219 | 10.0219
155 | BRAZ | KOLAR | KGF | KGF | ANDERSONPET_66 | 1230201901020301 | F04-INDUSTRIAL-AREA | INDUSTRIAL | DLMS Meter | 0.95048 | 0.85736 | 0 | 0.95048 | 9.7966 | 9.7966
156 | BRAZ | KOLAR | KGF | KGF | ANDERSONPET_66 | 1230201901010104 | F06-SWARNANAGAR | URBAN MIXED LOAD | DLMS Meter | 4.573 | 2.7169 | 1.7258 | 2.8472 | 4.5779 | 29.3545
157 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902030501 | F01-ANDERSONPET | DOMESTIC | DLMS Meter | 3.0976 | 2.8297 | 0 | 3.0976 | 8.6471 | 8.6471
158 | BRAZ | KOLAR | KGF | KGF | ANDERSONPET_66 | 1230201901010105 | F10-ADAMPALLI NJY | NJY | DLMS Meter | 0.1762 | 0.1625 | 0 | 0.1762 | 7.7775 | 85.5713
159 | BRAZ | KOLAR | KGF | KGF | ANDERSONPET_66 | 1230201901020306 | F11-GATTAMADAMANGALA NJY | NJY | DLMS Meter | 0.83402 | 0.75675 | 0 | 0.83402 | 9.2644 | 68.0654
160 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902010105 | F12- MARIKUPPAM TOWN | NJY | DLMS Meter | 0.78056 | 0.69563 | 0 | 0.78056 | 10.8804 | 10.8804
161 | BRAZ | KOLAR | KGF | KGF | ANDERSONPET_66 | 1230201901020307 | F12-CHOKARABANDA(NJY) | NJY | DLMS Meter | 0.3576 | 0.32595 | 0 | 0.3576 | 8.8493 | 54.0824
162 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902020304 | F15-OORGAUMPET | URBAN MIXED LOAD | DLMS Meter | 5.6635 | 3.2631 | 2.0768 | 3.5867 | 9.0222 | 34.1062
163 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010101 | F01-BYAGADADENAHALLI | AGRI | DLMS Meter | 0.3758 | 0.33839 | 0 | 0.3758 | 9.954 | 9.954
164 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010102 | F02-CHANDAPURA | URBAN MIXED LOAD | DLMS Meter | 0.9618 | 0.91009 | 0 | 0.9618 | 5.3768 | 25.9883
165 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010103 | F03-SAMANDUR | AGRI | DLMS Meter | 0.68488 | 0.61647 | 0 | 0.68488 | 9.9883 | 9.9883
166 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010104 | F04-MUTHAKATTI | AGRI | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
167 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010105 | F05-THALY-ROAD | URBAN MIXED LOAD | DLMS Meter | 4.0966 | 2.3122 | 1.5745 | 2.5221 | 8.3229 | 20.7644
168 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902020301 | F06-IB-AKL | URBAN MIXED LOAD | DLMS Meter | 3.2604 | 2.2881 | 0.783 | 2.4774 | 7.6406 | 18.0421
169 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902020302 | F08-CHILLING-CENTRE | URBAN MIXED LOAD | DLMS Meter | 3.6585 | 3.2765 | 0.055 | 3.6035 | 9.0756 | 19.1514
170 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902020303 | F09-SOLUR | URBAN MIXED LOAD | DLMS Meter | 3.5159 | 2.0353 | 1.3083 | 2.2076 | 7.8048 | 30.9061
171 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902020304 | F10-CHUDENAHALLI | AGRI | DLMS Meter | 1.0918 | 0.98008 | 0 | 1.0918 | 10.233 | 11.4686
172 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010106 | F11-WATER-SUPPLY | WATER WORKS | DLMS Meter | 0.37044 | 0.3069 | 0.028 | 0.34244 | 10.3777 | 38.0054
173 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010107 | F12-SAINATH-EDUCATION | COMMERCIAL | DLMS Meter | 1.5377 | 1.4609 | 0 | 1.5377 | 4.9987 | 4.9987
174 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010108 | F14-BALAJI | INDUSTRIAL | DLMS Meter | 0.608 | 0.5565 | 0.0415 | 0.5665 | 1.7652 | 1.7652
175 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010109 | F15-NJY | NJY | DLMS Meter | 1.6143 | 1.4586 | 0 | 1.6143 | 9.6442 | 54.0441
176 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902020305 | F16-VBHC | DOMESTIC | DLMS Meter | 1.0382 | 0.70092 | 0.265 | 0.77318 | 9.346 | 12.9905
177 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010110 | F17-THIMMARAYASWAMY-TEMPLE-ROAD | URBAN MIXED LOAD | DLMS Meter | 2.7841 | 2.5395 | 0 | 2.7841 | 8.7849 | 8.7849
178 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902020308 | F18-NJY CHIKKA HOSAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.4008 | 0.44221 | 0.9205 | 0.48026 | 7.9228 | 40.4524
179 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902020309 | F19- KAVERI TELECOM | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
180 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010113 | F20-VANAKANAHALLY NJY | NJY | DLMS Meter | 1.4192 | 1.2696 | 0 | 1.4192 | 10.5426 | 65.9508
181 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010111 | F21-NJY-HONNAKALASAPURA | NJY | DLMS Meter | 1.0522 | 0.9716 | 0 | 1.0522 | 7.6599 | 33.3046
182 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | ANEKAL_66 | 1220201902010114 | F22-VAKIL LAYOUT | DOMESTIC | DLMS Meter | 0.0132 | 0.009008 | 0.00357 | 0.00963 | 6.459 | 7.0629
183 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902010101 | F01-HEBBALU | AGRI | DLMS Meter | 1.0756 | 0.96804 | 0 | 1.0756 | 10.0017 | 10.0017
184 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902010102 | F02-ARADHYA | INDUSTRIAL | DLMS Meter | 4.0157 | 3.8655 | 0 | 4.0157 | 3.7397 | 3.7397
185 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902010103 | F03-NEERTHADI | AGRI | DLMS Meter | 1.7324 | 1.5593 | 0 | 1.7324 | 9.9908 | 9.9908
186 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902010104 | F04-SHIVAPURA | AGRI | DLMS Meter | 0.78198 | 0.70364 | 0 | 0.78198 | 10.018 | 10.018
187 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902020301 | F05-HALUVARTHI | AGRI | DLMS Meter | 1.1418 | 1.0276 | 0 | 1.1418 | 10.0032 | 10.0032
188 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902020302 | F06-GANGANKATTE | AGRI | DLMS Meter | 0.75482 | 0.67904 | 0 | 0.75482 | 10.0389 | 10.0389
189 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902020303 | F07-NERLAGI | AGRI | DLMS Meter | 0.93882 | 0.84514 | 0 | 0.93882 | 9.9789 | 9.9789
190 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902020304 | F08-KOGGANURU | AGRI | DLMS Meter | 1.0835 | 0.97497 | 0 | 1.0835 | 10.02 | 10.02
191 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902020305 | F09-JACKWELL | WATER WORKS | DLMS Meter | 0.78711 | 0.005 | 0.78194 | 0.00517 | 3.2882 | 4.7744
192 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902010105 | F10-CHINNASAMUDRANJY | NJY | DLMS Meter | 2.2559 | 1.9428 | 0.071 | 2.1849 | 11.0826 | 16.9056
193 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ANGODU_66 | 1310104902010106 | F11-ANAGODU NJY | NJY | DLMS Meter | 1.5326 | 0.8538 | 0.572 | 0.9606 | 11.1176 | 22.8914
194 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010102 | F02-REAL-HOUSE-APPARTMENT | URBAN MIXED LOAD | DLMS Meter | 0.55311 | 0.43127 | 0.075 | 0.47811 | 9.7975 | 28.5848
195 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010103 | F03-KS-IT-COLLEGE | URBAN MIXED LOAD | DLMS Meter | 0.84934 | 0.71725 | 0.032 | 0.81734 | 12.2456 | 14.611
196 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010104 | F04-MALLASANDRA-ROAD | URBAN MIXED LOAD | DLMS Meter | 4.5338 | 3.3804 | 0.62 | 3.9138 | 13.6291 | 17.2066
197 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010110 | F05-WEAVERS COLONY | URBAN MIXED LOAD | DLMS Meter | 3.5496 | 2.2632 | 0.955 | 2.5946 | 12.7732 | 21.2825
198 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010105 | F06-PURAVANKARA | DOMESTIC | DLMS Meter | 0.83189 | 0.76451 | 0 | 0.83189 | 8.0998 | 9.9172
199 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010106 | F07-AMRUTH-NAGAR | URBAN MIXED LOAD | DLMS Meter | 0.92416 | 0.69537 | 0.12954 | 0.79462 | 12.4904 | 14.6681
200 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010107 | F08-YELETHOTADAPALYA | URBAN MIXED LOAD | DLMS Meter | 1.6704 | 1.2659 | 0.215 | 1.4554 | 13.0246 | 22.7309
201 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010108 | F09-ANJANADRI LAYOUT | DOMESTIC | DLMS Meter | 0.32085 | 0.22719 | 0.064 | 0.25685 | 11.5464 | 14.7199
202 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010101 | F10-VADDARAPALYA | URBAN MIXED LOAD | DLMS Meter | 2.7585 | 2.1776 | 0.281 | 2.4775 | 12.1048 | 14.9156
203 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010109 | F11-KEMBATHALLI | URBAN MIXED LOAD | DLMS Meter | 0.79275 | 0.68422 | 0.018 | 0.77475 | 11.6846 | 27.2089
204 | BMASZ | SOUTH | HSR | S12 | ANJANAPURA_66 | 1110304901010113 | F13-GODREJ ETERNITY | URBAN MIXED LOAD | DLMS Meter | 0.32629 | 0.29017 | 0 | 0.32629 | 11.0692 | 11.0692
205 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901010101 | F01-GANGAIAHNAPALYA | AGRI | DLMS Meter | 1.0765 | 0.95105 | 0 | 1.0765 | 11.6521 | 11.6521
206 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901010102 | F02-KUNTARAMANAHALLI | AGRI | DLMS Meter | 0.907 | 0.8161 | 0 | 0.907 | 10.0226 | 11.3882
207 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901010103 | F03-SHESHANAHALLY NJY | NJY | DLMS Meter | 0.3038 | 0.27752 | 0 | 0.3038 | 8.6504 | 51.7823
208 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901010107 | F04-DEVARAHALLI | AGRI | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
209 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901010104 | F05-KALLUGUDI | AGRI | DLMS Meter | 0.1929 | 0.17447 | 0 | 0.1929 | 9.553 | 9.553
210 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901010105 | F06-ANKASANDRA | AGRI | DLMS Meter | 0.4224 | 0.38006 | 0 | 0.4224 | 10.0244 | 10.0244
211 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901010106 | F07-RANGANA-HALLY | AGRI | DLMS Meter | 1.1963 | 0.76145 | 0.3438 | 0.85246 | 10.6767 | 10.6767
212 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901020301 | F08-BYADRAHALLY | AGRI | DLMS Meter | 1.0284 | 0.88919 | 0 | 1.0284 | 13.5361 | 13.5361
213 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901020302 | F09-DEVARAHALLI | AGRI | DLMS Meter | 0.9204 | 0.75454 | 0.072524 | 0.84788 | 11.0082 | 11.0082
214 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901020303 | F10-SARIGEPALYA | AGRI | DLMS Meter | 1.0598 | 0.7031 | 0.25987 | 0.79993 | 12.1044 | 12.1044
215 | CTAZ | TUMKUR | TUMKUR | GUBBI | ANKASANDRA_66 | 1320106901020304 | F11-YARABALLY | AGRI | DLMS Meter | 0.6858 | 0.24826 | 0.40891 | 0.27689 | 10.3375 | 10.3375
216 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901010101 | F02-SWANDENAHALLY | AGRI | DLMS Meter | 1.1724 | 1.0537 | 0 | 1.1724 | 10.1238 | 10.3111
217 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901010102 | F03-YELLAPURA | URBAN MIXED LOAD | DLMS Meter | 5.1128 | 1.8567 | 3.1459 | 1.9669 | 5.6024 | 19.9386
218 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901010103 | F04-HANDTOOL | INDUSTRIAL | DLMS Meter | 2.1544 | 1.8944 | 0.14527 | 2.0091 | 5.7106 | 9.9173
219 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901010107 | F05-NAVILAHALLI | AGRI | DLMS Meter | 0.84918 | 0.74963 | 0 | 0.84918 | 11.7228 | 11.8431
220 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901010104 | F06-URUKERE | URBAN MIXED LOAD | DLMS Meter | 3.3261 | 2.3793 | 0.77847 | 2.5476 | 6.6087 | 13.276
221 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901020301 | F07-MELEHALLY | AGRI | DLMS Meter | 1.1571 | 1.0206 | 0 | 1.1571 | 11.7981 | 11.7981
222 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901020302 | F08-HEBBAKA | AGRI | DLMS Meter | 1.21 | 1.0891 | 0 | 1.21 | 9.9921 | 9.9921
223 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901020303 | F09-BUGUDANAHALLI | WATER WORKS | DLMS Meter | 3.8968 | 2.3465 | 1.21 | 2.6868 | 12.6654 | 15.1544
224 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901020503 | F10-INDUSTRIAL-AREA | URBAN MIXED LOAD | DLMS Meter | 4.097 | 3.827 | 0 | 4.097 | 6.5916 | 13.9252
225 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901020304 | F11-DC-BUNGLOW | URBAN MIXED LOAD | DLMS Meter | 2.1728 | 1.5327 | 0.47578 | 1.6971 | 9.6866 | 11.0636
226 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901020305 | F12-KIADB | INDUSTRIAL | DLMS Meter | 5.5612 | 5.1924 | 0 | 5.5612 | 6.6321 | 6.6321
227 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901010105 | F13-KIADB-IND-AREA | INDUSTRIAL | DLMS Meter | 4.534 | 4.3083 | 0 | 4.534 | 4.9771 | 7.8434
228 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901020501 | F14-NARASAPURA | AGRI | DLMS Meter | 1.6278 | 1.3934 | 0 | 1.6278 | 14.4005 | 34.5816
229 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901010106 | F15-SATYAMANGALA | URBAN MIXED LOAD | DLMS Meter | 3.9335 | 2.9088 | 0.82383 | 3.1097 | 6.4609 | 6.4609
230 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901020504 | F16-FITWELL | INDUSTRIAL | DLMS Meter | 2.9591 | 2.6489 | 0.2 | 2.7591 | 3.9941 | 34.6994
231 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901020306 | F17-INDOAUTO | INDUSTRIAL | DLMS Meter | 5.8132 | 5.5061 | 0 | 5.8132 | 5.2833 | 6.7959
232 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901030701 | F20-KG PALYA | NJY | DLMS Meter | 0.33074 | 0.30124 | 0 | 0.33074 | 8.92 | 29.1212
233 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | ANTHRASANAHALLI_220 | 1320101901020502 | F21-TUDA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 5.5781 | 5.2083 | 0 | 5.5781 | 6.6296 | 15.208
234 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904020101 | F01-SPINNING-MILL | URBAN MIXED LOAD | DLMS Meter | 1.3932 | 1.3543 | 0 | 1.3932 | 2.7949 | 10.8484
235 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904020102 | F02-TULASIYANA | INDUSTRIAL | DLMS Meter | 2.9375 | 2.0363 | 0.78636 | 2.1512 | 5.3413 | 5.3413
236 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904010101 | F03-JK PAINTS | URBAN MIXED LOAD | DLMS Meter | 1.7158 | 1.668 | 0 | 1.7158 | 2.788 | 4.6816
237 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904010102 | F04-OBADENHALLI 3RD PHASE | INDUSTRIAL | DLMS Meter | 1.7554 | 0.88684 | 0.83412 | 0.92124 | 3.7339 | 3.7815
238 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904010103 | F05-WAD-PACK | INDUSTRIAL | DLMS Meter | 2.9096 | 2.8152 | 0 | 2.9096 | 3.2449 | 3.4382
239 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904010104 | F06-BRFL | INDUSTRIAL | DLMS Meter | 1.5625 | 1.4801 | 0 | 1.5625 | 5.2746 | 5.9941
240 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904020301 | F07-KEIHIN FIE | INDUSTRIAL | DLMS Meter | 3.7696 | 3.2271 | 0.34 | 3.4296 | 5.9037 | 6.8806
241 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904020302 | F08-VARADANAHALLI | AGRI | DLMS Meter | 0.59236 | 0.53302 | 0 | 0.59236 | 10.0177 | 10.0177
242 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904020303 | F09-JEANS-KNIT | INDUSTRIAL | DLMS Meter | 5.3197 | 3.7029 | 1.54 | 3.7797 | 2.0316 | 11.0194
243 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904010301 | F10-NAVODAYA | INDUSTRIAL | DLMS Meter | 3.4674 | 3.3416 | 0.0203 | 3.4471 | 3.06 | 3.5342
244 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904010302 | F11-RAILWAY-STATION | URBAN MIXED LOAD | DLMS Meter | 1.7132 | 1.5237 | 0 | 1.7132 | 11.0642 | 28.8594
245 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904020304 | F13-MUSASHI | INDUSTRIAL | DLMS Meter | 4.6838 | 4.5934 | 0 | 4.6838 | 1.9309 | 1.9309
246 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | APARELPARK_66 | 1210101904020305 | F14-STELIS BIO PHARMA | INDUSTRIAL | DLMS Meter | 3.7134 | 3.7139 | 0 | 3.7134 | -0.012253 | -0.012253
247 | BMASZ | SOUTH | JAYANAGAR | S15 | AREHALLI_66 | 1110103903010103 | F03-ITTUMADU | URBAN MIXED LOAD | DLMS Meter | 2.0986 | 1.9983 | 0 | 2.0986 | 4.7781 | 6.5711
248 | BMASZ | SOUTH | JAYANAGAR | S18 | AREHALLI_66 | 1110103903020101 | F04-CHIKKALASANDRA | URBAN MIXED LOAD | DLMS Meter | 3.5893 | 3.3079 | 0.03 | 3.5593 | 7.0637 | 10.895
249 | BMASZ | SOUTH | JAYANAGAR | S18 | AREHALLI_66 | 1110103903010104 | F05-KADIRENAHALLY | URBAN MIXED LOAD | DLMS Meter | 2.7216 | 2.4725 | 0.085 | 2.6366 | 6.2232 | 7.5607
250 | BMASZ | SOUTH | JAYANAGAR | S18 | AREHALLI_66 | 1110103903020102 | F06-F-KOMARLA-BRIGADE | URBAN MIXED LOAD | DLMS Meter | 2.8451 | 2.667 | 0 | 2.8451 | 6.2588 | 11.2054
251 | BMASZ | SOUTH | JAYANAGAR | S15 | AREHALLI_66 | 1110103903020103 | F07-BHUVANESHWARI-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.479 | 2.0363 | 0.33769 | 2.1413 | 4.9044 | 4.922
252 | BMASZ | SOUTH | JAYANAGAR | S18 | AREHALLI_66 | 1110103903010105 | F08-KOMRLA | URBAN MIXED LOAD | DLMS Meter | 2.026 | 1.5595 | 0.33513 | 1.6909 | 7.7689 | 11.2108
253 | BMASZ | SOUTH | JAYANAGAR | S15 | AREHALLI_66 | 1110103903020301 | F09-HOSAKEREHALLI | URBAN MIXED LOAD | DLMS Meter | 2.4392 | 1.8393 | 0.48261 | 1.9566 | 5.9975 | 10.1024
254 | BMASZ | SOUTH | JAYANAGAR | S18 | AREHALLI_66 | 1110103903020104 | F10-AGS-LAY-OUT | URBAN MIXED LOAD | DLMS Meter | 4.2081 | 3.8491 | 0.09 | 4.1181 | 6.5313 | 12.3275
255 | BMASZ | SOUTH | JAYANAGAR | S15 | AREHALLI_66 | 1110103903010107 | F11-TATA PERMOUNT | DOMESTIC | DLMS Meter | 0.43834 | 0.41893 | 0 | 0.43834 | 4.4274 | 4.4274
256 | BMASZ | SOUTH | JAYANAGAR | S15 | AREHALLI_66 | 1110103903010106 | F12-T.G LAYOUT | DOMESTIC | DLMS Meter | 3.2645 | 2.6331 | 0.46533 | 2.7992 | 5.9333 | 9.7348
257 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901040702 | F01-JAYADEVA-HOSTEL | COMMERCIAL | DLMS Meter | 0.58048 | 0.49578 | 0.065451 | 0.51503 | 3.7383 | 3.7383
258 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901010107 | F02-CRESCENT ROAD | URBAN MIXED LOAD | DLMS Meter | 2.2949 | 2.2038 | 0 | 2.2949 | 3.9705 | 10.1453
259 | BMANZ | EAST | VIDHANASOUDHA | W5 | ASTATION_66 | 1130102901010101 | F05-KAVERI-BHAVAN-AND-AUX | COMMERCIAL | DLMS Meter | 1.8603 | 1.7634 | 0.02852 | 1.8318 | 3.733 | 3.733
260 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901030508 | F06-CINEMA-FEEDER | COMMERCIAL | DLMS Meter | 4.498 | 4.3455 | 0 | 4.498 | 3.3903 | 6.5172
261 | BMANZ | NORTH | MALLESHWARA | C2 | ASTATION_66 | 1130102901030503 | F08-SHESHADRIPURAM | URBAN MIXED LOAD | DLMS Meter | 4.2963 | 3.247 | 0.925 | 3.3713 | 3.688 | 8.3588
262 | BMANZ | NORTH | MALLESHWARA | C2 | ASTATION_66 | 1130102901030504 | F09-MD-BLOCK | URBAN MIXED LOAD | DLMS Meter | 3.5282 | 3.3736 | 0.07 | 3.4582 | 2.4481 | 7.2161
263 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901040703 | F10-VASANTHNAGAR | URBAN MIXED LOAD | DLMS Meter | 2.43 | 2.2026 | 0.11052 | 2.3195 | 5.0371 | 5.0371
264 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901030101 | F11-BRIGADE-PLAZA | COMMERCIAL | DLMS Meter | 1.2688 | 1.124 | 0.088564 | 1.1802 | 4.7621 | 14.7892
265 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901020301 | F12-KHANIJA-BHAVANA | COMMERCIAL | DLMS Meter | 2.4899 | 2.3835 | 0 | 2.4899 | 4.274 | 7.9673
266 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901040704 | F13-RAJ-BHAVAN | COMMERCIAL | DLMS Meter | 2.4235 | 2.3152 | 0 | 2.4235 | 4.4686 | 4.4686
267 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901010102 | F14-UPPERPET-POLICE-STATION | URBAN MIXED LOAD | DLMS Meter | 2.9233 | 2.774 | 0 | 2.9233 | 5.1073 | 5.1073
268 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901040705 | F15-VIKASA-SOUDHA | COMMERCIAL | DLMS Meter | 0.80125 | 0.76577 | 0 | 0.80125 | 4.4284 | 4.4284
269 | BMANZ | EAST | VIDHANASOUDHA | W5 | ASTATION_66 | 1130102901010103 | F16-BANNAPPA-PARK | URBAN MIXED LOAD | DLMS Meter | 1.3421 | 1.1943 | 0.085895 | 1.2562 | 4.9226 | 5.923
270 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901010301 | F17-BVK IYAENGAR-ROAD | COMMERCIAL | DLMS Meter | 1.9488 | 1.8022 | 0.063992 | 1.8848 | 4.3829 | 5.337
271 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901010104 | F18-KR-CIRCLE | COMMERCIAL | DLMS Meter | 1.5024 | 1.4371 | 0 | 1.5024 | 4.3503 | 4.3503
272 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901010501 | F19-BALABROOIE | URBAN MIXED LOAD | DLMS Meter | 2.099 | 1.992 | 0 | 2.099 | 5.0987 | 8.5337
273 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901020303 | F21-TULASI-THOTA | URBAN MIXED LOAD | DLMS Meter | 3.1567 | 2.9703 | 0.02912 | 3.1276 | 5.0288 | 7.1368
274 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901020304 | F22-GANDHINAGAR | URBAN MIXED LOAD | DLMS Meter | 3.025 | 2.9003 | 0 | 3.025 | 4.1215 | 9.9985
275 | BMANZ | NORTH | MALLESHWARA | C1 | ASTATION_66 | 1130102901010105 | F23-PRAKASH-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.5248 | 1.4732 | 0.925 | 1.5998 | 7.9128 | 13.8716
276 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901010106 | F25-MADHAVANAGAR | URBAN MIXED LOAD | DLMS Meter | 5.8694 | 5.5388 | 0 | 5.8694 | 5.6314 | 10.2973
277 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901020306 | F26-KSRTC | COMMERCIAL | DLMS Meter | 2.6618 | 2.5167 | 0.045163 | 2.6166 | 3.8204 | 5.9337
278 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901040706 | F27-CHIKCPET | COMMERCIAL | DLMS Meter | 0.66848 | 0.62926 | 0 | 0.66848 | 5.8668 | 5.8668
279 | BMANZ | NORTH | MALLESHWARA | C2 | ASTATION_66 | 1130102901030505 | F28-MATRI-GREENS | URBAN MIXED LOAD | DLMS Meter | 2.6673 | 2.3422 | 0.26 | 2.4073 | 2.7019 | 2.7543
280 | BMANZ | EAST | VIDHANASOUDHA | W4 | ASTATION_66 | 1130102901030506 | F29-EMBASSY-HABITAT | DOMESTIC | DLMS Meter | 0.56419 | 0.53258 | 0 | 0.56419 | 5.6028 | 5.6028
281 | BMANZ | NORTH | MALLESHWARA | C2 | ASTATION_66 | 1130102901030507 | F30-MATRI-MALL | COMMERCIAL | DLMS Meter | 3.8414 | 3.8051 | 0 | 3.8414 | 0.94467 | 0.94467
282 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901010101 | F01-ICHANGUR | AGRI | DLMS Meter | 1.4889 | 1.3404 | 0 | 1.4889 | 9.9753 | 10.0433
283 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901010102 | F02-MEHER-CAPACITORS | INDUSTRIAL | DLMS Meter | 7.193 | 6.9669 | 0 | 7.193 | 3.1423 | 4.6872
284 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901010103 | F03-ADEEP-LOCKS | INDUSTRIAL | DLMS Meter | 5.5259 | 5.2403 | 0.015 | 5.5109 | 4.9104 | 5.2329
285 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901010104 | F04-YADAVANAHALLI | AGRI | DLMS Meter | 0.85248 | 0.5977 | 0.1896 | 0.66288 | 9.8334 | 12.4492
286 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020301 | F05-MAYASANDRA | AGRI | DLMS Meter | 0.89164 | 0.60565 | 0.2151 | 0.67654 | 10.479 | 11.2709
287 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020302 | F06-MIKEE-STEEL | INDUSTRIAL | DLMS Meter | 3.3613 | 2.7849 | 0.449 | 2.9123 | 4.373 | 4.373
288 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020303 | F07-ALPHA-GRANITES | INDUSTRIAL | DLMS Meter | 1.3986 | 1.3516 | 0 | 1.3986 | 3.36 | 3.36
289 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020304 | F09-LAXMI-FORGE | INDUSTRIAL | DLMS Meter | 4.474 | 4.4095 | 0 | 4.474 | 1.4412 | 1.5559
290 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901010105 | F10-JAIPURIA-SILK-MILLS | INDUSTRIAL | DLMS Meter | 2.6027 | 1.2452 | 1.327 | 1.2757 | 2.3926 | 2.6017
291 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020305 | F11-APPLICOM | INDUSTRIAL | DLMS Meter | 4.7473 | 5.8e-05 | 4.7473 | 6.01e-05 | 3.4942 | 3.4942
292 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020306 | F12-AASIRWAD-PIPES | INDUSTRIAL | DLMS Meter | 2.1945 | 2.1359 | 0.02468 | 2.1698 | 1.5658 | 1.6937
293 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020307 | F13-NIRANTHARA-JYOTHI | NJY | DLMS Meter | 1.8623 | 1.698 | 0 | 1.8623 | 8.823 | 22.9276
294 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901010106 | F14-BALLURU | URBAN MIXED LOAD | DLMS Meter | 3.4933 | 2.8556 | 0.418 | 3.0753 | 7.1442 | 16.1093
295 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901010107 | F15-ATTIBELE-URBAN | URBAN MIXED LOAD | DLMS Meter | 4.9501 | 4.3839 | 0.1952 | 4.7549 | 7.8029 | 11.5586
296 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020401 | F16-SRINIVASA FINANCE | INDUSTRIAL | DLMS Meter | 3.2786 | 3.2181 | 0 | 3.2786 | 1.8467 | 1.8664
297 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020402 | F17-BALAGARANAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.9342 | 2.6235 | 0.0615 | 2.8727 | 8.6732 | 8.898
298 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020403 | F18-COMATO/ALLOYTECH | INDUSTRIAL | DLMS Meter | 2.7013 | 2.3963 | 0.24 | 2.4613 | 2.6405 | 4.6787
299 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020404 | F19-JAYABHARATHI SCHOOL | URBAN MIXED LOAD | DLMS Meter | 2.7955 | 2.4945 | 0.1017 | 2.6938 | 7.3979 | 12.7296
300 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020405 | F20-NJY KAMBLIPURA | NJY | DLMS Meter | 1.7222 | 0.21154 | 1.4912 | 0.231 | 8.4238 | 35.8669
301 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020406 | F21-KHB | URBAN MIXED LOAD | DLMS Meter | 0.15502 | 0.14065 | 0.0026 | 0.15242 | 7.7197 | 7.7197
302 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020410 | F22-AGS | URBAN MIXED LOAD | DLMS Meter | 3.8582 | 3.5178 | 0 | 3.8582 | 8.8231 | 10.5011
303 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020408 | F23-ASHIRVAD PIPES | INDUSTRIAL | DLMS Meter | 4.7726 | 4.7492 | 0 | 4.7726 | 0.48925 | 0.48925
304 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020407 | F24-JANAADHAR | URBAN MIXED LOAD | DLMS Meter | 4.0106 | 3.6626 | 0 | 4.0106 | 8.6782 | 10.8168
305 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020409 | F25-MAHIDHARA | DOMESTIC | DLMS Meter | 0.0624 | 0.039149 | 0.0204 | 0.042 | 6.7874 | 13.9018
306 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | ATTIBELE_66 | 1220202901020308 | F26 -ASHIRVAD PIPES 6B | INDUSTRIAL | DLMS Meter | 3.1217 | 3.0372 | 0 | 3.1217 | 2.7053 | 2.7053
307 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901010101 | F01-THOLAHUNESE | AGRI | DLMS Meter | 0.70088 | 0.63068 | 0 | 0.70088 | 10.0166 | 10.0166
308 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901010102 | F02-KURKI | AGRI | DLMS Meter | 0.68706 | 0.61808 | 0 | 0.68706 | 10.0394 | 10.0394
309 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901020304 | F03-WATERSUPPLY | WATER WORKS | DLMS Meter | 0.1452 | 0.13551 | 0 | 0.1452 | 6.6756 | 52.4757
310 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901010103 | F04-KABBUR | AGRI | DLMS Meter | 1.5365 | 1.3828 | 0 | 1.5365 | 10.0027 | 10.0027
311 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901020301 | F05-GOPANALU | AGRI | DLMS Meter | 0.74134 | 0.66693 | 0 | 0.74134 | 10.0371 | 10.0371
312 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901010105 | F06-KANDAGALLU NJY | NJY | DLMS Meter | 1.1295 | 0.72896 | 0.303 | 0.82652 | 11.804 | 30.2025
313 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901020302 | F07-BADAATG | AGRI | DLMS Meter | 0.75766 | 0.68158 | 0 | 0.75766 | 10.042 | 10.042
314 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901020303 | F08-ATTIGERE | AGRI | DLMS Meter | 0.80732 | 0.72626 | 0 | 0.80732 | 10.041 | 10.041
315 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901010107 | F09-HANUMANAHALLI | AGRI | DLMS Meter | 0.62342 | 0.56099 | 0 | 0.62342 | 10.0135 | 10.0135
316 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901010104 | F10-HIRETHOGALERI NJY | NJY | DLMS Meter | 1.2853 | 1.049 | 0.122 | 1.1633 | 9.8267 | 23.9629
317 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901010301 | F11-R.G. HALLI NJY | NJY | DLMS Meter | 0.89367 | 0.55354 | 0.271 | 0.62267 | 11.1015 | 25.7969
318 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | ATTIGERE_66 | 1310104901010106 | F12-RANGANATHA FEEDER | AGRI | DLMS Meter | 0.4852 | 0.43651 | 0 | 0.4852 | 10.0359 | 10.0359
319 | BMASZ | SOUTH | JAYANAGAR | S2 | AUSTIN_TOWN_66 | 1110201904020301 | F01-TV--RMU | DOMESTIC | DLMS Meter | 1.3215 | 1.0983 | 0.17736 | 1.1442 | 4.0085 | 4.2962
320 | BMASZ | SOUTH | KORAMANGALA | S3 | AUSTIN_TOWN_66 | 1110201904010101 | F02-AIRFORCE-HOSPITAL | DOMESTIC | DLMS Meter | 3.2687 | 2.2849 | 0.8686 | 2.4001 | 4.7997 | 6.3438
321 | BMASZ | SOUTH | KORAMANGALA | S3 | AUSTIN_TOWN_66 | 1110201904010102 | F03-AUSTIN-TOWN | DOMESTIC | DLMS Meter | 4.1114 | 2.8487 | 1.168 | 2.9434 | 3.2162 | 5.1635
322 | BMANZ | EAST | INDIRA NAGAR | E3 | AUSTIN_TOWN_66 | 1110201904030501 | F05-ASHOK-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.444 | 2.3508 | 0 | 2.444 | 3.8132 | 5.372
323 | BMANZ | EAST | INDIRA NAGAR | E3 | AUSTIN_TOWN_66 | 1110201904020302 | F06-KSRP-RMU | URBAN MIXED LOAD | DLMS Meter | 1.5064 | 1.4471 | 0 | 1.5064 | 3.9378 | 5.7464
324 | BMASZ | SOUTH | KORAMANGALA | S3 | AUSTIN_TOWN_66 | 1110201904020303 | F07-FVANNERPET | DOMESTIC | DLMS Meter | 5.0188 | 4.4745 | 0.38 | 4.6388 | 3.5437 | 8.7115
325 | BMASZ | SOUTH | JAYANAGAR | S2 | AUSTIN_TOWN_66 | 1110201904020305 | F09-S.L-APARTMENT. | DOMESTIC | DLMS Meter | 1.5982 | 1.0969 | 0.44829 | 1.15 | 4.6102 | 5.754
326 | BMANZ | EAST | INDIRA NAGAR | E3 | AUSTIN_TOWN_66 | 1110201904030503 | F12-SHOPPER-STOP | URBAN MIXED LOAD | DLMS Meter | 1.7398 | 1.0861 | 0.61183 | 1.128 | 3.7081 | 9.1423
327 | BMASZ | SOUTH | KORAMANGALA | S3 | AUSTIN_TOWN_66 | 1110201904030504 | F13-NEELASANDRA | DOMESTIC | DLMS Meter | 4.8408 | 4.6927 | 0 | 4.8408 | 3.0599 | 6.8379
328 | BMANZ | EAST | INDIRA NAGAR | E3 | AUSTIN_TOWN_66 | 1110201904030505 | F14-SIDDAIAH-ROAD | URBAN MIXED LOAD | DLMS Meter | 2.5981 | 2.5094 | 0 | 2.5981 | 3.4135 | 3.4135
329 | BMANZ | EAST | INDIRA NAGAR | E3 | AUSTIN_TOWN_66 | 1110201904010104 | F15-SHOBHA-PEARL | URBAN MIXED LOAD | DLMS Meter | 0.97847 | 0.72467 | 0.2273 | 0.75117 | 3.5283 | 3.5283
330 | BMANZ | EAST | INDIRA NAGAR | E3 | AUSTIN_TOWN_66 | 1110201904010105 | F16-ING-VYSYA-BANK | URBAN MIXED LOAD | DLMS Meter | 0.56517 | 0.33251 | 0.22013 | 0.34505 | 3.6323 | 3.6323
331 | BMANZ | EAST | INDIRA NAGAR | E3 | AUSTIN_TOWN_66 | 1110201904010106 | F17-GARUDAMAL | URBAN MIXED LOAD | DLMS Meter | 2.2527 | 2.1551 | 0.029558 | 2.2231 | 3.0592 | 3.5898
332 | BMANZ | EAST | INDIRA NAGAR | E3 | AUSTIN_TOWN_66 | 1110201904020306 | F18-RADHIKAVARMA-RMU | URBAN MIXED LOAD | DLMS Meter | 0.67221 | 0.53636 | 0.11433 | 0.55788 | 3.8582 | 5.0794
333 | BRAZ | KOLAR | KGF | MULABAGILU | AVANI_66 | 1230202904010101 | F01-AVANI | AGRI | DLMS Meter | 0.76454 | 0.68836 | 0 | 0.76454 | 9.9647 | 12.6686
334 | BRAZ | KOLAR | KGF | MULABAGILU | AVANI_66 | 1230202904010102 | F02-DEVARAYASAMUDRA | AGRI | DLMS Meter | 0.7096 | 0.63836 | 0 | 0.7096 | 10.0397 | 10.0397
335 | BRAZ | KOLAR | KGF | MULABAGILU | AVANI_66 | 1230202904010103 | F03-KANTHARAJA CIRCLE | NJY | DLMS Meter | 1.3574 | 1.2296 | 0 | 1.3574 | 9.4128 | 43.5159
336 | BRAZ | KOLAR | KGF | MULABAGILU | AVANI_66 | 1230202904020301 | F04-OORKUNTEMITTUR | AGRI | DLMS Meter | 1.211 | 1.0901 | 0 | 1.211 | 9.984 | 9.984
337 | BRAZ | KOLAR | KGF | MULABAGILU | AVANI_66 | 1230202904020302 | F05-JAYAMANGALA | AGRI | DLMS Meter | 0.47416 | 0.42684 | 0 | 0.47416 | 9.9802 | 9.9802
338 | BRAZ | KOLAR | KGF | MULABAGILU | AVANI_66 | 1230202904020303 | F06-GOPASANDRA | AGRI | DLMS Meter | 0.64744 | 0.58274 | 0 | 0.64744 | 9.9932 | 9.9932
339 | BRAZ | KOLAR | KGF | MULABAGILU | AVANI_66 | 1230202904020304 | F07-YALAGANDAHALLI-NJY | NJY | DLMS Meter | 0.97856 | 0.88267 | 0 | 0.97856 | 9.7992 | 41.7427
340 | BRAZ | KOLAR | KGF | MULABAGILU | AVANI_66 | 1230202904010104 | F08-NAGASANDRA | NJY | DLMS Meter | 0.60626 | 0.54743 | 0 | 0.60626 | 9.7043 | 75.6138
341 | BRAZ | KOLAR | KGF | MULABAGILU | AVANI_66 | 1230202904010107 | F11-BADAMAKANAHALLI | NJY | DLMS Meter | 0.5088 | 0.46826 | 0 | 0.5088 | 7.9674 | 62.6041
342 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904010101 | F02-HONNUR | AGRI | DLMS Meter | 1.0164 | 0.91482 | 0 | 1.0164 | 9.9982 | 9.9982
343 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904010102 | F03-BASAVANALLU | AGRI | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
344 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904010103 | F04-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 1.7998 | 1.6557 | 0.095 | 1.7048 | 2.8796 | 9.7083
345 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904020301 | F05-MALLASHETTIHALLI | AGRI | DLMS Meter | 1.3999 | 1.0908 | 0.16616 | 1.2337 | 11.5864 | 11.5864
346 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904020302 | F06-KADAJJI AVG | DOMESTIC | DLMS Meter | 0.4304 | 0.35118 | 0.0304 | 0.4 | 12.204 | 36.6805
347 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904020303 | F07-AVAREGERE | URBAN MIXED LOAD | DLMS Meter | 1.5973 | 1.1008 | 0.3425 | 1.2548 | 12.2679 | 19.1227
348 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904020304 | F08-ANGODU | NJY | DLMS Meter | 1.1274 | 0.84248 | 0.14894 | 0.97846 | 13.8971 | 29.8822
349 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904030501 | F09-BETHUR | AGRI | DLMS Meter | 0.73684 | 0.66347 | 0 | 0.73684 | 9.9575 | 9.9575
350 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904010501 | F10-PUTTUGUNAL | AGRI | DLMS Meter | 0.76786 | 0.53678 | 0.16 | 0.60786 | 11.6941 | 11.6941
351 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904030502 | F11-IGURU | AGRI | DLMS Meter | 1.0108 | 0.69476 | 0.225 | 0.78584 | 11.5896 | 11.5896
352 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904030503 | F12-CHIKKANAHALLI | AGRI | DLMS Meter | 1.4592 | 1.3133 | 0 | 1.4592 | 10 | 10
353 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | AVAREGERE_66 | 1310103904030701 | F13-ANEKONDA | URBAN MIXED LOAD | DLMS Meter | 1.464 | 1.3955 | 0 | 1.464 | 4.6832 | 10.1917
354 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | AVAREGERE_66 | 1310103904030702 | F14-MAHAVEERA | URBAN MIXED LOAD | DLMS Meter | 4.0185 | 2.5193 | 1.2714 | 2.7471 | 8.2921 | 16.3238
355 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | AVAREGERE_66 | 1310103904030703 | F15-RAVI | URBAN MIXED LOAD | DLMS Meter | 2.1952 | 1.9968 | 0.10993 | 2.0853 | 4.2427 | 12.6103
356 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | AVAREGERE_66 | 1310103904030704 | F16-GOSHALE | URBAN MIXED LOAD | DLMS Meter | 0.216 | 0.18685 | 0.014123 | 0.20188 | 7.4445 | 13.5518
357 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904030705 | F17-NJLINGADAHALLI | NJY | DLMS Meter | 0.34206 | 0.000129 | 0.34206 | 0 | 0 | #DIV/0!
358 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904030504 | F18-RAMPURA | NJY | DLMS Meter | 0.43614 | 0.32712 | 0.05674 | 0.3794 | 13.7798 | 42.1306
359 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | AVAREGERE_66 | 1310103904030706 | F19-STP AVARAGERE | INDUSTRIAL | DLMS Meter | 2.9032 | 2.8637 | 0 | 2.9032 | 1.3602 | 2.5287
360 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | AVVERAHALLI_66 | 1210107901010101 | F01-RATHNAM | INDUSTRIAL | DLMS Meter | 2.5122 | 2.5032 | 0 | 2.5122 | 0.35752 | 0.35752
361 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | AVVERAHALLI_66 | 1210107901010102 | F02-KIADB-1SVS CONTROL | INDUSTRIAL | DLMS Meter | 0.8425 | 0.053892 | 0.78805 | 0.05445 | 1.0242 | 1.0242
362 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | AVVERAHALLI_66 | 1210107901010103 | F03-SANGAVI | INDUSTRIAL | DLMS Meter | 1.4509 | 1.1586 | 0.279 | 1.1719 | 1.1371 | 1.5953
363 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | AVVERAHALLI_66 | 1210107901020102 | F08-ASHA | INDUSTRIAL | DLMS Meter | 1.4792 | 0.011189 | 1.4679 | 0.01135 | 1.4163 | 1.4163
364 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | AVVERAHALLI_66 | 1210107901020103 | F09-AVERAHALLI WATER TANK | INDUSTRIAL | DLMS Meter | 0.2063 | 0.13088 | 0.073 | 0.1333 | 1.817 | 7.7664
365 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | AVVERAHALLI_66 | 1210107901020104 | F10-KASSIA | INDUSTRIAL | DLMS Meter | 0.7314 | 0.20435 | 0.523 | 0.2084 | 1.9456 | 14.1854
366 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | AWHO | 1310203907010103 | F01-ARMY | DOMESTIC | DLMS Meter | 0.17724 | 0.16599 | 0.004213 | 0.17303 | 4.0647 | 4.0647
367 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | AWHO | 1310203907010105 | F02-KORALURU | URBAN MIXED LOAD | DLMS Meter | 4.6784 | 3.8532 | 0.22586 | 4.4526 | 13.4617 | 25.0918
368 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | AWHO | 1310203907010104 | F03-ARMY F&G BLOCK | DOMESTIC | DLMS Meter | 0.50192 | 0.43285 | 0.051732 | 0.45019 | 3.8502 | 3.8502
369 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | AWHO | 1310203907010102 | F04-ARMY | DOMESTIC | DLMS Meter | 0.42991 | 0.4202 | 0 | 0.42991 | 2.257 | 3.5186
370 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | AWHO | 1310203907010101 | F05-ARMY | DOMESTIC | DLMS Meter | 0.30729 | 0.29963 | 0 | 0.30729 | 2.4914 | 5.1338
371 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | AWHO | 1310203907010106 | F08-BDA VINDYAGIRI | DOMESTIC | DLMS Meter | 0.4468 | 0.424 | 0.004595 | 0.4422 | 4.1164 | 4.1164
372 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | AWHO | 1310203907010107 | F09-BDA CHANDRAGIRI | DOMESTIC | DLMS Meter | 2.0468 | 1.1491 | 0.8113 | 1.2355 | 6.9904 | 10.5885
373 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | AWHO | 1310203907010108 | F10-ASSETZ MARQ | DOMESTIC | DLMS Meter | 0.37151 | 0.20243 | 0.16136 | 0.21016 | 3.6782 | 3.6782
374 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | AWHO | 1310203907010111 | F13-SEEGEHALLI | URBAN MIXED LOAD | DLMS Meter | 5.2162 | 4.4298 | 0.29929 | 4.9169 | 9.9076 | 13.3098
375 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | AWHO | 1310203907010112 | F15-SUMADHURA INFRACON | DOMESTIC | DLMS Meter | 0.8536 | 0.37098 | 0.46886 | 0.38474 | 3.5751 | 5.402
376 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | B V HALLI_66 | 1220105903010104 | F01-BHOOHALLI | AGRI | DLMS Meter | 0.7736 | 0.70595 | 0 | 0.7736 | 8.7448 | 8.7448
377 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | B V HALLI_66 | 1220105903010102 | F02-SOMEGOWDANADODDI | NJY | DLMS Meter | 0.5494 | 0.35095 | 0.165 | 0.3844 | 8.7015 | 31.3848
378 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | B V HALLI_66 | 1220105903010101 | F03-BYRASHETTIHALLI | AGRI | DLMS Meter | 0.677 | 0.53107 | 0.087 | 0.59 | 9.9888 | 9.9888
379 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | B V HALLI_66 | 1220105903010103 | F04-VITTLENAHALLI | AGRI | DLMS Meter | 0.9204 | 0.82819 | 0 | 0.9204 | 10.018 | 10.018
380 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | B V HALLI_66 | 1220105903010105 | F05-MANGADAHALLI NJY | NJY | DLMS Meter | 0.9052 | 0.37184 | 0.497 | 0.4082 | 8.9068 | 21.2874
381 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | B V HALLI_66 | 1220105903010106 | F06-VIRUPAKSHIPURA | AGRI | DLMS Meter | 1.2326 | 1.1224 | 0 | 1.2326 | 8.942 | 8.942
382 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010101 | F01-ING-VYSYA-BANK | COMMERCIAL | DLMS Meter | 1.5886 | 1.3951 | 0.17176 | 1.4168 | 1.5345 | 1.5345
383 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010102 | F02-MURPHY-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.6994 | 2.3055 | 1.2475 | 2.4519 | 5.9702 | 9.5058
384 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010103 | F03-M.G.ROAD-PUB | URBAN MIXED LOAD | DLMS Meter | 1.5982 | 1.0303 | 0.52946 | 1.0687 | 3.5922 | 22.4692
385 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010104 | F04-UDHANI LAYOUT | DOMESTIC | DLMS Meter | 2.1763 | 2.0467 | 0.011208 | 2.1651 | 5.4693 | 7.7939
386 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010105 | F05-KSRP-RMU | URBAN MIXED LOAD | DLMS Meter | 1.3101 | 1.2583 | 0.002 | 1.3081 | 3.8069 | 5.1064
387 | BMASZ | SOUTH | JAYANAGAR | S2 | B_STATION_66 | 1130201902010106 | F06-FWIPRO-R.M.U. | COMMERCIAL | DLMS Meter | 2.1162 | 1.6563 | 0.39826 | 1.7179 | 3.5903 | 4.4927
388 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010107 | F07-FBARTON-CENTRE-(EGK-RMU) | URBAN MIXED LOAD | DLMS Meter | 1.4274 | 1.3729 | 0 | 1.4274 | 3.8176 | 7.3948
389 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010111 | F08-SAIBABA TEMPLE | URBAN MIXED LOAD | DLMS Meter | 3.569 | 2.115 | 1.2992 | 2.2699 | 6.8251 | 8.9645
390 | BMANZ | EAST | SHIVAJINAGAR | E2 | B_STATION_66 | 1130201902020301 | F09-PLAIN-STREET | COMMERCIAL | DLMS Meter | 1.9029 | 1.8306 | 0 | 1.9029 | 3.7951 | 5.5562
391 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902020302 | F10-MAYO-HALL-RMU | URBAN MIXED LOAD | DLMS Meter | 3.1476 | 2.0403 | 1.0282 | 2.1194 | 3.7294 | 4.4704
392 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902020303 | F11-SHANKAR-NARAYAN | URBAN MIXED LOAD | DLMS Meter | 3.8356 | 3.6906 | 0 | 3.8356 | 3.7797 | 5.6101
393 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010109 | F12-PRIME ROSE ROAD | URBAN MIXED LOAD | DLMS Meter | 2.2632 | 2.1747 | 0 | 2.2632 | 3.9105 | 3.9105
394 | BMANZ | EAST | INDIRA NAGAR | E6 | B_STATION_66 | 1130201902010108 | F13-MOOKAMBIKA TEMPLE | URBAN MIXED LOAD | DLMS Meter | 3.6338 | 3.4449 | 0.006963 | 3.6268 | 5.0167 | 8.7817
395 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010113 | F14-PRESTIGE CONRAD HOTEL | URBAN MIXED LOAD | DLMS Meter | 4.9658 | 4.4318 | 0.26056 | 4.7052 | 5.81 | 7.7122
396 | BMANZ | EAST | SHIVAJINAGAR | E2 | B_STATION_66 | #N/A | F15-KAMARAJA-ROAD | #N/A | DLMS Meter | 2.0172 | 1.9359 | 0 | 2.0172 | 4.0301 | 10.6262
397 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010112 | F16-M.G.ROAD RMU | URBAN MIXED LOAD | DLMS Meter | 1.4324 | 1.0756 | 0.31774 | 1.1146 | 3.498 | 3.5624
398 | BMANZ | EAST | SHIVAJINAGAR | E2 | B_STATION_66 | 1130201902010114 | F17-COOL JOINT | URBAN MIXED LOAD | DLMS Meter | 4.3354 | 3.6778 | 0.50558 | 3.8298 | 3.9693 | 7.7073
399 | BMANZ | EAST | SHIVAJINAGAR | E2 | B_STATION_66 | 1130201902030501 | F18-FOOD-OFFICE | URBAN MIXED LOAD | DLMS Meter | 3.5356 | 3.3374 | 0 | 3.5356 | 5.6053 | 9.7994
400 | BMANZ | EAST | SHIVAJINAGAR | E2 | B_STATION_66 | 1130201902030101 | F19-SAFFINA-PLAZA | COMMERCIAL | DLMS Meter | 1.2393 | 1.1196 | 0.069195 | 1.1701 | 4.3158 | 6.2029
401 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902030504 | F21-PRESTIGE-DYNASITY | URBAN MIXED LOAD | DLMS Meter | 2.1715 | 1.9419 | 0.1445 | 2.027 | 4.1969 | 6.4386
402 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902030505 | F23-OBERAI-RMU | URBAN MIXED LOAD | DLMS Meter | 3.1925 | 2.9562 | 0.11723 | 3.0752 | 3.8698 | 3.9909
403 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902010110 | F24-P.M STREET | URBAN MIXED LOAD | DLMS Meter | 2.9999 | 2.7553 | 0.069071 | 2.9309 | 5.9893 | 11.2336
404 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902040701 | F25-BPL-RMU | URBAN MIXED LOAD | DLMS Meter | 0.92905 | 0.87891 | 0.017267 | 0.91179 | 3.6062 | 6.4283
405 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902040702 | F26-EGK-RMU | URBAN MIXED LOAD | DLMS Meter | 1.0401 | 0.81899 | 0.18918 | 0.8509 | 3.7495 | 3.7495
406 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902040703 | F27-GARUDAMALL | COMMERCIAL | DLMS Meter | 1.8281 | 1.8092 | 0 | 1.8281 | 1.0383 | 1.1054
407 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902040704 | F28-BANGALORE-CENTRAL | COMMERCIAL | DLMS Meter | 2.057 | 1.4022 | 0.60147 | 1.4555 | 3.6613 | 3.6613
408 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902040705 | F29-SHOBHA-PEARL | COMMERCIAL | DLMS Meter | 0.21735 | 0.2148 | 0 | 0.21735 | 1.1728 | 1.1728
409 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902040706 | F30-LIDO | URBAN MIXED LOAD | DLMS Meter | 3.1808 | 1.6914 | 1.4034 | 1.7774 | 4.8353 | 16.7225
410 | BMANZ | EAST | INDIRA NAGAR | E3 | B_STATION_66 | 1130201902040707 | F31-MOTOROLA | URBAN MIXED LOAD | DLMS Meter | 3.5648 | 2.3919 | 1.0687 | 2.4962 | 4.179 | 5.0767
411 | BMANZ | EAST | SHIVAJINAGAR | E2 | B_STATION_66 | 1130201902040708 | F32-TIWARI-FEEDS | COMMERCIAL | DLMS Meter | 2.4827 | 1.6111 | 0.77853 | 1.7042 | 5.4626 | 9.3376
412 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902010101 | F01-RANGAPURA | AGRI | DLMS Meter | 2.5185 | 2.2668 | 0 | 2.5185 | 9.9963 | 9.9963
413 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902010102 | F02-KAVANADALA | AGRI | DLMS Meter | 1.8497 | 1.6643 | 0 | 1.8497 | 10.0221 | 10.0221
414 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902010103 | F03-SIDADARAGALLU | AGRI | DLMS Meter | 1.2056 | 1.0851 | 0 | 1.2056 | 9.9965 | 10.0459
415 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902020301 | F04-DODDERI | AGRI | DLMS Meter | 1.6311 | 1.4603 | 0 | 1.6311 | 10.473 | 10.6442
416 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902020302 | F05-KARPENAHALLY | AGRI | DLMS Meter | 1.3513 | 1.2161 | 0 | 1.3513 | 10.0027 | 10.0027
417 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902020303 | F06-CHANDRAGIRI | AGRI | DLMS Meter | 1.5297 | 1.3766 | 0 | 1.5297 | 10.0061 | 10.5382
418 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902010104 | F07-BADAVANAHALLY | RURAL MIXED LOAD | DLMS Meter | 2.1341 | 0.8856 | 1.16 | 0.97407 | 9.0827 | 13.5883
419 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902010105 | F08-JAVANAIAHNAPALYA | AGRI | DLMS Meter | 1.5124 | 1.3611 | 0 | 1.5124 | 10.0067 | 10.0067
420 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902020304 | F09-BANAGARAHALLY | AGRI | DLMS Meter | 1.2791 | 1.1514 | 0 | 1.2791 | 9.9842 | 10.0577
421 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902010106 | F10-KOONAHALLY--NJY | NJY | DLMS Meter | 0.7078 | 0.40176 | 0.259 | 0.4488 | 10.4809 | 80.5444
422 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902010107 | F11-K.T.HALLY----NJY | NJY | DLMS Meter | 0.83515 | 0.23532 | 0.57615 | 0.259 | 9.1417 | 68.0707
423 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | BADAVANAHALLI_66 | 1320301902010108 | F12-POOJARAHALLY NJY | NJY | DLMS Meter | 1.0106 | 0.72609 | 0.209 | 0.80157 | 9.4168 | 54.3694
424 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | BADDIHALLI_66 | 1320105901010101 | F01-KITHAGANAHALLI | AGRI | DLMS Meter | 0.492 | 0.44272 | 0 | 0.492 | 10.0172 | 10.0172
425 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | BADDIHALLI_66 | 1320105901010102 | F02-PALASANDRA | AGRI | DLMS Meter | 1.0766 | 0.97078 | 0 | 1.0766 | 9.8292 | 10.0517
426 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | BADDIHALLI_66 | 1320105901010103 | F03-SAPTHAGIRI | URBAN MIXED LOAD | DLMS Meter | 3.1168 | 2.5496 | 0.34349 | 2.7733 | 8.0682 | 27.1583
427 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | BADDIHALLI_66 | 1320105901010104 | F04-MARUTHI-NAGARA | URBAN MIXED LOAD | DLMS Meter | 2.5398 | 2.3357 | 0 | 2.5398 | 8.0356 | 21.3922
428 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | BADDIHALLI_66 | 1320105901010105 | F05-NJY-KITTAGANAHALLY | NJY | DLMS Meter | 0.78984 | 0.53428 | 0.20389 | 0.58594 | 8.8169 | 37.4181
429 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | BADDIHALLI_66 | 1320105901010106 | F07-GULARIVE | AGRI | DLMS Meter | 1.1341 | 0.81984 | 0.2254 | 0.90872 | 9.7811 | 9.7811
430 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | BADDIHALLI_66 | 1320105901020301 | F08-BADDIHALLI | URBAN MIXED LOAD | DLMS Meter | 2.4089 | 2.0989 | 0.1154 | 2.2935 | 8.4844 | 31.544
431 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | BADDIHALLI_66 | 1320105901020302 | F09-KESARAMODU-NJY | NJY | DLMS Meter | 2.062 | 1.9504 | 0 | 2.062 | 5.4124 | 17.965
432 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | BADDIHALLI_66 | 1320105901020304 | F11-KALAHALLI | AGRI | DLMS Meter | 0.9794 | 0.78729 | 0.1121 | 0.8673 | 9.2252 | 23.1398
433 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | BADDIHALLI_66 | 1320105901020305 | F12-KESARAMODU | AGRI | DLMS Meter | 1.2578 | 1.0809 | 0.0465 | 1.2113 | 10.772 | 12.9636
434 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | BADDIHALLI_66 | 1320105901010108 | F13-RAGHAVENDRA NAGARA | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
435 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903020301 | F01-MITTEMARI | AGRI | DLMS Meter | 1.3164 | 1.1847 | 0 | 1.3164 | 10.0046 | 10.0046
436 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903020302 | F02-HAMPASANDRA | AGRI | DLMS Meter | 1.3638 | 1.0381 | 0.21 | 1.1538 | 10.0282 | 10.0282
437 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903020303 | F03-PATHAPALYA-OLD | AGRI | DLMS Meter | 0.31245 | 0.28135 | 0 | 0.31245 | 9.9533 | 9.9533
438 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903020304 | F04-ACHEPALLY | AGRI | DLMS Meter | 0.8127 | 0.73118 | 0.000148 | 0.81255 | 10.0138 | 10.0138
439 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010101 | F05-LOCAL | URBAN MIXED LOAD | DLMS Meter | 5.808 | 4.9821 | 0.0009755 | 5.807 | 14.2049 | 14.2049
440 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010102 | F06-GULUR | AGRI | DLMS Meter | 0.855 | 0.76948 | 0 | 0.855 | 10.0022 | 10.0022
441 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010103 | F07-HOSAKOTE | AGRI | DLMS Meter | 1.5792 | 1.4067 | 0.01 | 1.5692 | 10.356 | 10.356
442 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010104 | F08-T.B-CROSS | URBAN MIXED LOAD | DLMS Meter | 2.1282 | 1.7976 | 0.045 | 2.0832 | 13.7106 | 34.7296
443 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010105 | F09-MARGANUKUNTE | AGRI | DLMS Meter | 1.048 | 0.94329 | 0 | 1.048 | 9.9909 | 9.9909
444 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010106 | F11-CHITRAVATHI-DAM | WATER WORKS | DLMS Meter | 0.001652 | 0.001652 | 0 | 0.001652 | 0 | 92.3207
445 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010107 | F12-MALLIGURKI | NJY | DLMS Meter | 1.0876 | 0.95675 | 0 | 1.0876 | 12.0314 | 71.9669
446 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010108 | F13-CHOKKAMPALLI | NJY | DLMS Meter | 0.9283 | 0.78953 | 0.038 | 0.8903 | 11.3185 | 27.3836
447 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010109 | F14-PUTTAPARTHI | NJY | DLMS Meter | 2.0691 | 1.8139 | 0.045 | 2.0241 | 10.3872 | 10.3872
448 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010111 | F15-NALLAPAREDDYPALLI NJY | NJY | DLMS Meter | 1.2727 | 1.0555 | 0.09 | 1.1827 | 10.7551 | 71.5835
449 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010112 | F16-PARAGODU NJY | NJY | DLMS Meter | 0.9919 | 0.88838 | 0.0008055 | 0.99109 | 10.3637 | 37.3452
450 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010113 | F17-MOTAKAPALLI | AGRI | DLMS Meter | 0.8932 | 0.80367 | 0 | 0.8932 | 10.0231 | 10.0231
451 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010114 | F18-NARASAPURA | AGRI | DLMS Meter | 0.9256 | 0.79707 | 0.04 | 0.8856 | 9.9972 | 9.9972
452 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | BAGEPALLI_66 | 1230305903010115 | F19-GADIDHAM | NJY | DLMS Meter | 0.000129 | 0.000129 | 0 | 0.000129 | 0 | 100
453 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | BAGGANADODDI_66 | 1220201906010103 | F02-ADUR | NJY | DLMS Meter | 2.9236 | 0.58352 | 2.2891 | 0.63445 | 8.0275 | 46.5549
454 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | BAGGANADODDI_66 | 1220201906010102 | F03-BAGGANADODDI | NJY | DLMS Meter | 0.291 | 0.21938 | 0.055 | 0.236 | 7.0414 | 68.9909
455 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | BAGGANADODDI_66 | 1220201906010101 | F04-KADUJAKKANA HALLI | AGRI | DLMS Meter | 0.4972 | 0.44806 | 0 | 0.4972 | 9.8837 | 9.8837
456 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902020101 | F02-MOTOROLA | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
457 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902020102 | F03-TEXAS | COMMERCIAL | DLMS Meter | 3.5007 | 3.4628 | 0 | 3.5007 | 1.0828 | 4.0253
458 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902020103 | F04-RETAIL-BLOCK | COMMERCIAL | DLMS Meter | 0.57495 | 0.57232 | 0 | 0.57495 | 0.45808 | 0.45808
459 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902020301 | F05-BAGHMANE-LAKE-VIEW | COMMERCIAL | DLMS Meter | 1.8172 | 1.8088 | 0 | 1.8172 | 0.46442 | 0.46442
460 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902020302 | F06-C-T-S | COMMERCIAL | DLMS Meter | 0.25408 | 0.25335 | 0 | 0.25408 | 0.28686 | 2.1606
461 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902020303 | F07-BAGHMANE-PARIN | COMMERCIAL | DLMS Meter | 5.6064 | 5.587 | 0 | 5.6064 | 0.34435 | 0.34435
462 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902020304 | F08-G-M-PALAYA | URBAN MIXED LOAD | DLMS Meter | 3.5997 | 3.3835 | 0 | 3.5997 | 6.0067 | 8.5415
463 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902020104 | F09-BAGHMANE-LAUREL-BLOCK | COMMERCIAL | DLMS Meter | 3.8451 | 3.8367 | 0 | 3.8451 | 0.21685 | 0.21685
464 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902020105 | F10-MPHASIS-(TRIDIP) | COMMERCIAL | DLMS Meter | 4.4339 | 4.4268 | 0 | 4.4339 | 0.15901 | 0.15901
465 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902010202 | F11-VIGNAN_NAGAR | DOMESTIC | DLMS Meter | 6.4003 | 5.8996 | 0.1214 | 6.2789 | 6.0411 | 8.967
466 | BMANZ | EAST | INDIRA NAGAR | E10 | BAGHMANE_TECHPARK_66 | 1110203902010201 | F12-BHUVANESHWARINAGAR | DOMESTIC | DLMS Meter | 0.57876 | 0.4746 | 0.069302 | 0.50946 | 6.842 | 9.0203
467 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902010203 | F13-AYYAPPA_TEMPLE | DOMESTIC | DLMS Meter | 3.9017 | 3.7435 | 0 | 3.9017 | 4.0545 | 11.6347
468 | BMANZ | EAST | INDIRA NAGAR | E10 | BAGHMANE_TECHPARK_66 | 1110203902020401 | F14-KAGGADASAPURA | URBAN MIXED LOAD | DLMS Meter | 1.5491 | 0.77248 | 0.72267 | 0.8264 | 6.5248 | 8.0551
469 | BMASZ | SOUTH | KORAMANGALA | S17 | BAGHMANE_TECHPARK_66 | 1110203902010402 | F15-KRISHNAPPA_GARDEN | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
470 | BMANZ | EAST | INDIRA NAGAR | E10 | BAGHMANE_TECHPARK_66 | 1110203902010401 | F16-TTK PRESTIGE | URBAN MIXED LOAD | DLMS Meter | 1.0061 | 0.97886 | 0 | 1.0061 | 2.7083 | 2.7083
471 | BMANZ | EAST | INDIRA NAGAR | E10 | BAGHMANE_TECHPARK_66 | 1110203902020402 | F17-KG PURA 2 | URBAN MIXED LOAD | DLMS Meter | 5.3466 | 4.8484 | 0.01165 | 5.335 | 9.1211 | 10.2635
472 | BMANZ | EAST | INDIRA NAGAR | E10 | BAGHMANE_TECHPARK_66 | 1110203902020404 | F19-FQUAY | COMMERCIAL | DLMS Meter | 1.336 | 1.327 | 0 | 1.336 | 0.67179 | 0.86376
473 | BMANZ | EAST | INDIRA NAGAR | E10 | BAGHMANE_TECHPARK_66 | 1110203902020403 | PURVA SEASONS | DOMESTIC | DLMS Meter | 0.43041 | 0.3968 | 0 | 0.43041 | 7.8084 | 7.8084
474 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010101 | F02-W.T.C. | COMMERCIAL | DLMS Meter | 7.412 | 7.2511 | 0 | 7.412 | 2.1706 | 2.1706
475 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010102 | F03-W.T.C. | COMMERCIAL | DLMS Meter | 3.9856 | 3.9004 | 0 | 3.9856 | 2.1365 | 2.1365
476 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010103 | F04-W.T.C. | COMMERCIAL | DLMS Meter | 2.6967 | 2.2036 | 0.44895 | 2.2478 | 1.966 | 1.966
477 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010104 | F05-WTC | COMMERCIAL | DLMS Meter | 4.09 | 4.0649 | 0 | 4.09 | 0.61473 | 0.61473
478 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010105 | F06-F-W.T.C | IDLE | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
479 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010110 | F07-IDLE2 | IDLE | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
480 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010109 | F08-IDLE3 | IDLE | DLMS Meter | 2.3323 | 2.2718 | 0 | 2.3323 | 2.5975 | 2.5975
481 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010108 | F09-IDLE4 | IDLE | DLMS Meter | 3.6179 | 2.1483 | 1.3244 | 2.2935 | 6.3336 | 11.0571
482 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010107 | F10-VIRGO | COMMERCIAL | DLMS Meter | 2.7591 | 2.7267 | 0 | 2.7591 | 1.1729 | 1.1729
483 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010106 | F11-TOTAL MALL | URBAN MIXED LOAD | DLMS Meter | 4.0442 | 3.9683 | 0 | 4.0442 | 1.8774 | 7.3212
484 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901010112 | F12-GARNET | COMMERCIAL | DLMS Meter | 7.2779 | 7.1775 | 0 | 7.2779 | 1.3805 | 1.3805
485 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901020301 | F13-CARINA-EAST | COMMERCIAL | DLMS Meter | 4.3253 | 2.7654 | 1.4142 | 2.9111 | 5.0036 | 5.0036
486 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901020302 | F14-CARINA-WEST | COMMERCIAL | DLMS Meter | 1.5012 | 1.4977 | 0 | 1.5012 | 0.23314 | 0.23314
487 | BMANZ | EAST | WHITEFIELD | E12 | BAGMANEWTP_66 | 1130202901020303 | F15-TAURUS-EAST | COMMERCIAL | DLMS Meter | 1.9298 | 0.9046 | 0.98075 | 0.9491 | 4.6885 | 4.6885
488 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | BAGUR_TMK_66 | 1310204905010101 | F01-HSDROADEXP. | NJY | DLMS Meter | 1.0538 | 0.41762 | 0.58793 | 0.46585 | 10.3533 | 31.8659
489 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | BAGUR_TMK_66 | 1310204905010103 | F02-BAGUR | NJY | DLMS Meter | 0.61098 | 0.43705 | 0.13106 | 0.47992 | 8.9318 | 32.1639
490 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | BAGUR_TMK_66 | 1310204905010102 | F03-ILAPURA | AGRI | DLMS Meter | 0.27134 | 0.24414 | 0 | 0.27134 | 10.0251 | 10.0251
491 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | BAGUR_TMK_66 | 1310204905010104 | F04-HEBBALI | AGRI | DLMS Meter | 1.7155 | 1.544 | 0 | 1.7155 | 9.9984 | 9.9984
492 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | BAGUR_TMK_66 | 1310204905020301 | F05-SANEHALLI | AGRI | DLMS Meter | 0.56659 | 0.51 | 0 | 0.56659 | 9.9873 | 9.9873
493 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | BAGUR_TMK_66 | 1310204905020302 | F06-SRPURA | AGRI | DLMS Meter | 0.79455 | 0.71516 | 0 | 0.79455 | 9.9918 | 9.9918
494 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | BAGUR_TMK_66 | 1310204905020303 | F07-ANIVALA | AGRI | DLMS Meter | 0.87658 | 0.78869 | 0 | 0.87658 | 10.0267 | 10.0267
495 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | BAGUR_TMK_66 | 1310204905020304 | F08-HSDROADRURAL | AGRI | DLMS Meter | 1.4657 | 1.319 | 0 | 1.4657 | 10.01 | 10.01
496 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | BALENAHALLI_66 | 1310402907010101 | F01-KALLAHALLI | NJY | DLMS Meter | 0.74416 | 0.38642 | 0.3041 | 0.44006 | 12.1886 | 32.5404
497 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | BALENAHALLI_66 | 1310402907010102 | F02-KELAGALAHATTI | AGRI | DLMS Meter | 0.9783 | 0.87108 | 0 | 0.9783 | 10.9597 | 10.9597
498 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | BALENAHALLI_66 | 1310402907010104 | F04-HOSAKALLAHALLI | AGRI | DLMS Meter | 0.5422 | 0.48353 | 0 | 0.5422 | 10.8202 | 10.8202
499 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | BALENAHALLI_66 | 1310402907020301 | F05-RATNAGIRI | AGRI | DLMS Meter | 0.77796 | 0.69428 | 0 | 0.77796 | 10.7558 | 12.9658
500 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | BALENAHALLI_66 | 1310402907020302 | F06-RAAMAJOGIHALLY | AGRI | DLMS Meter | 0.73692 | 0.65387 | 0 | 0.73692 | 11.2699 | 11.2987
501 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | BALENAHALLI_66 | 1310402907020303 | F07-KURUDIHALLY | AGRI | DLMS Meter | 0.57116 | 0.51403 | 0 | 0.57116 | 10.0019 | 10.0019
502 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | BALENAHALLI_66 | 1310402907020304 | F08-BAALENAHALLY | AGRI | DLMS Meter | 0.83244 | 0.74903 | 0 | 0.83244 | 10.0197 | 10.0197
503 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | BALENAHALLI_66 | 1310402907020305 | F09-SAPTHAGIRI NJY | NJY | DLMS Meter | 0.49358 | 0.43215 | 0 | 0.49358 | 12.4451 | 45.1411
504 | BMASZ | SOUTH | JAYANAGAR | S15 | BANASHANKARI_66 | 1110105902030501 | F02-BANK-COLONY | URBAN MIXED LOAD | DLMS Meter | 3.7386 | 3.5454 | 0 | 3.7386 | 5.1665 | 6.6386
505 | BMASZ | WEST | RR NAGAR | W1 | BANASHANKARI_66 | 1110105902030502 | F03-GIRINAGAR | URBAN MIXED LOAD | DLMS Meter | 2.1047 | 1.9947 | 0 | 2.1047 | 5.2258 | 15.3158
506 | BMASZ | WEST | RR NAGAR | W8 | BANASHANKARI_66 | 1110105902010102 | F04-VIDYA-PEETHA-CIRCLE | URBAN MIXED LOAD | DLMS Meter | 2.589 | 2.3837 | 0.0201 | 2.5689 | 7.2098 | 17.3729
507 | BMASZ | SOUTH | JAYANAGAR | S15 | BANASHANKARI_66 | 1110105902010103 | F06-BSK 2ND STAGE | URBAN MIXED LOAD | DLMS Meter | 4.1624 | 3.9655 | 0 | 4.1624 | 4.7302 | 11.2704
508 | BMASZ | WEST | RR NAGAR | W1 | BANASHANKARI_66 | 1110105902020401 | F07-HANUMANTHA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 1.963 | 1.7878 | 0.085124 | 1.8779 | 4.7934 | 11.69
509 | BMASZ | WEST | RR NAGAR | W8 | BANASHANKARI_66 | 1110105902020403 | F11-BASAVANAGUDI | URBAN MIXED LOAD | DLMS Meter | 2.246 | 2.0129 | 0.12133 | 2.1246 | 5.26 | 6.9424
510 | BMASZ | SOUTH | JAYANAGAR | S15 | BANASHANKARI_66 | 1110105902020404 | F12-BSK-3RD-STAGE | URBAN MIXED LOAD | DLMS Meter | 3.3253 | 2.8849 | 0.28052 | 3.0448 | 5.2512 | 7.1881
511 | BMASZ | WEST | RR NAGAR | W1 | BANASHANKARI_66 | 1110105902020301 | F13-NAGENDRA-BLOCK | URBAN MIXED LOAD | DLMS Meter | 2.8939 | 2.7196 | 0 | 2.8939 | 6.0226 | 19.182
512 | BMASZ | SOUTH | JAYANAGAR | S15 | BANASHANKARI_66 | 1110105902030602 | F17-KATHRIGUPPE | URBAN MIXED LOAD | DLMS Meter | 3.4083 | 3.1315 | 0.080287 | 3.328 | 5.9045 | 6.5607
513 | BMASZ | SOUTH | JAYANAGAR | S15 | BANASHANKARI_66 | 1110105902010104 | F20-SITA-CIRCLE | URBAN MIXED LOAD | DLMS Meter | 3.5861 | 3.0634 | 0.35736 | 3.2287 | 5.121 | 6.4289
514 | BMASZ | SOUTH | JAYANAGAR | S15 | BANASHANKARI_66 | 1110105902030503 | F22-STERLING-APPARTMENT | URBAN MIXED LOAD | DLMS Meter | 1.2926 | 1.2279 | 0 | 1.2926 | 5.0074 | 6.1935
515 | BMASZ | WEST | RR NAGAR | W8 | BANASHANKARI_66 | 1110105902010106 | F23-HANUMANTHA NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.8512 | 3.5207 | 0.16285 | 3.6883 | 4.5434 | 12.2653
516 | BMASZ | SOUTH | JAYANAGAR | S15 | BANASHANKARI_66 | 1110105902030504 | F24-WATER-TANK | URBAN MIXED LOAD | DLMS Meter | 2.9513 | 2.7785 | 0 | 2.9513 | 5.8525 | 6.4697
517 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | BANASWADI_66 | 1130304901030501 | F00-BILISHIVALE | URBAN MIXED LOAD | DLMS Meter | 4.7794 | 4.076 | 0.26389 | 4.5155 | 9.7335 | 12.8831
518 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901010101 | F01-HORAMAVU | URBAN MIXED LOAD | DLMS Meter | 8.6244 | 7.8706 | 0 | 8.6244 | 8.7404 | 14.9437
519 | BMANZ | EAST | SHIVAJINAGAR | E5 | BANASWADI_66 | 1130304901020301 | F02-LINGARAJ-PURAM | URBAN MIXED LOAD | DLMS Meter | 1.9326 | 1.7552 | 0.071206 | 1.8614 | 5.7022 | 16.0016
520 | BMANZ | EAST | SHIVAJINAGAR | E9 | BANASWADI_66 | 1130304901010102 | F03-HENNUR | URBAN MIXED LOAD | DLMS Meter | 4.6531 | 4.2356 | 0.086803 | 4.5663 | 7.2415 | 11.3111
521 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901030502 | F04-K.CHANSANDRA | URBAN MIXED LOAD | DLMS Meter | 8.3792 | 7.552 | 0.11021 | 8.269 | 8.6704 | 16.0013
522 | BMANZ | EAST | SHIVAJINAGAR | E9 | BANASWADI_66 | 1130304901010103 | F05-CHELIKERE | URBAN MIXED LOAD | DLMS Meter | 2.5646 | 2.3502 | 0 | 2.5646 | 8.3622 | 15.3075
523 | BMANZ | EAST | SHIVAJINAGAR | E5 | BANASWADI_66 | 1130304901020302 | F06-FDJ-HALLI | URBAN MIXED LOAD | DLMS Meter | 1.7109 | 1.6057 | 0 | 1.7109 | 6.1443 | 14.312
524 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901030503 | F07-FSUBBAIHANPALYA. | URBAN MIXED LOAD | DLMS Meter | 4.9073 | 4.5172 | 0 | 4.9073 | 7.9499 | 11.9113
525 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901030504 | F08-H.R.B.R-LAYOUT. | URBAN MIXED LOAD | DLMS Meter | 3.7385 | 3.3417 | 0.086 | 3.6525 | 8.5104 | 9.9177
526 | BMANZ | EAST | SHIVAJINAGAR | E5 | BANASWADI_66 | 1130304901020303 | F09-AFNHB-COLONY | URBAN MIXED LOAD | DLMS Meter | 3.1283 | 2.7805 | 0.18109 | 2.9472 | 5.6581 | 11.5835
527 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901020101 | F10-BALDWIN-SCHOOL | URBAN MIXED LOAD | DLMS Meter | 3.9101 | 3.646 | 0 | 3.9101 | 6.7547 | 12.0295
528 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901010105 | F12-KAMMANAHALLI-MAIN-ROAD | URBAN MIXED LOAD | DLMS Meter | 7.7991 | 6.6222 | 0.5364 | 7.2627 | 8.8183 | 13.8775
529 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901020102 | F13-OMBR-LAY-OUT | URBAN MIXED LOAD | DLMS Meter | 3.653 | 3.2493 | 0.147 | 3.506 | 7.3209 | 12.107
530 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901010106 | F14-BABUSAB-PALYA. | URBAN MIXED LOAD | DLMS Meter | 4.6787 | 4.0869 | 0.185 | 4.4937 | 9.0531 | 20.2604
531 | BMANZ | EAST | SHIVAJINAGAR | E9 | BANASWADI_66 | 1130304901030301 | F15-DODDAGUBBI | URBAN MIXED LOAD | DLMS Meter | 1.9429 | 1.8228 | 0 | 1.9429 | 6.1795 | 16.4445
532 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901020103 | F16-CANOPY-APMT: | URBAN MIXED LOAD | DLMS Meter | 2.7166 | 2.4177 | 0.065 | 2.6516 | 8.8209 | 19.0684
533 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901020105 | F18-PILLAREDDY-NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.4443 | 3.1255 | 0.092 | 3.3523 | 6.7652 | 10.0488
534 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901020106 | F19-DOCTOR'S-LAY-OUT | URBAN MIXED LOAD | DLMS Meter | 3.3553 | 2.9468 | 0.174 | 3.1813 | 7.3713 | 11.5326
535 | BMANZ | EAST | SHIVAJINAGAR | E8 | BANASWADI_66 | 1130304901030505 | F21-BANJAR-LAYLOT | URBAN MIXED LOAD | DLMS Meter | 6.3398 | 5.7716 | 0 | 6.3398 | 8.9626 | 15.1629
536 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905010107 | F01-KODIHALLI | AGRI | DLMS Meter | 0.92522 | 0.83287 | 0 | 0.92522 | 9.9816 | 9.9816
537 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905010101 | F02-DODDAPETE | URBAN MIXED LOAD | DLMS Meter | 1.7104 | 1.5478 | 0.015 | 1.6954 | 8.709 | 10.0968
538 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905010103 | F04-KALKERE | AGRI | DLMS Meter | 0.82926 | 0.66103 | 0.095 | 0.73426 | 9.9739 | 9.9739
539 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905010104 | F05-ERALAGERE | AGRI | DLMS Meter | 0.90304 | 0.81252 | 0 | 0.90304 | 10.0239 | 10.0239
540 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905020301 | F06-SHANTHANAHALLI | AGRI | DLMS Meter | 0.74578 | 0.67112 | 0 | 0.74578 | 10.0109 | 10.0109
541 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905020302 | F07-KOTANAYAKANAHALLI | AGRI | DLMS Meter | 0.48502 | 0.39603 | 0.045 | 0.44002 | 9.997 | 9.997
542 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905020303 | F08-WATERSUPPLY | WATER WORKS | DLMS Meter | 0.8455 | 0.67677 | 0.075 | 0.7705 | 12.1655 | 12.6537
543 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905020304 | F09-RAMENAHALLI NJY | NJY | DLMS Meter | 0.55606 | 0.44763 | 0.034 | 0.52206 | 14.2566 | 36.8575
544 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905020306 | F10 ACHARYA PALYA | NJY | DLMS Meter | 0.29326 | 0.25483 | 0.007 | 0.28626 | 10.9785 | 37.3449
545 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905010105 | F12-BANDIHALLI | INDUSTRIAL | DLMS Meter | 0.57169 | 0.52288 | 0 | 0.57169 | 8.5383 | 8.5383
546 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905010108 | F14-ADHINAYAKANAHALLI | NJY | DLMS Meter | 0.27264 | 0.24199 | 0 | 0.27264 | 11.2422 | 34.5089
547 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903030501 | F01-KADIRENAHALLI | AGRI | DLMS Meter | 1.3017 | 1.1721 | 0 | 1.3017 | 9.9534 | 9.9534
548 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903020301 | F02-SULIKUNTE | AGRI | DLMS Meter | 1.2124 | 1.0916 | 0 | 1.2124 | 9.9657 | 9.9657
549 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903020302 | F03-MAVAHALLI | AGRI | DLMS Meter | 1.3019 | 1.1716 | 0 | 1.3019 | 10.01 | 10.0784
550 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903020303 | F04 AMMARAVATHI | URBAN MIXED LOAD | DLMS Meter | 4.4483 | 2.6823 | 1.58 | 2.8683 | 6.4836 | 21.2901
551 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903010107 | F05-TOWN | URBAN MIXED LOAD | DLMS Meter | 4.1088 | 3.9947 | 0 | 4.1088 | 2.7767 | 22.4696
552 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903010101 | F07-CHALGANAHALLI | AGRI | DLMS Meter | 1.4804 | 1.3322 | 0 | 1.4804 | 10.007 | 10.007
553 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903030502 | F08-HULIBELE | AGRI | DLMS Meter | 1.1708 | 1.0536 | 0 | 1.1708 | 10.0063 | 11.2679
554 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903010102 | F09-KARMANGAL | AGRI | DLMS Meter | 1.2092 | 1.0885 | 0 | 1.2092 | 9.9808 | 9.9808
555 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903030503 | F10-HEREKARAPANAHALLI | AGRI | DLMS Meter | 0.7079 | 0.63717 | 0 | 0.7079 | 9.9912 | 9.9912
556 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903030504 | F11-DASARASHOSAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.5099 | 1.277 | 0.08 | 1.4299 | 10.6901 | 12.4316
557 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903030505 | F12-VATTRAKUNTE | AGRI | DLMS Meter | 1.2791 | 1.151 | 0 | 1.2791 | 10.0192 | 10.0192
558 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903030506 | F13-OMAKARA-KSHETRA | AGRI | DLMS Meter | 1.1261 | 1.0001 | 0 | 1.1261 | 11.1929 | 11.1929
559 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903030507 | F14-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 1.9623 | 1.7824 | 0 | 1.9623 | 9.1673 | 11.7284
560 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903010105 | F15-DESHIHALLI | URBAN MIXED LOAD | DLMS Meter | 1.6104 | 1.5414 | 0 | 1.6104 | 4.2844 | 27.9347
561 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903010106 | F16-KIADB NJY | NJY | DLMS Meter | 1.5666 | 1.4487 | 0 | 1.5666 | 7.5218 | 44.2498
562 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903010104 | F17-GAJAGA NJY | NJY | DLMS Meter | 0.93733 | 0.78036 | 0.09 | 0.84733 | 7.9037 | 64.2418
563 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903020307 | F18-HUNKUNDA NJY | NJY | DLMS Meter | 2.1462 | 1.9574 | 0 | 2.1462 | 8.7967 | 65.8558
564 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903030508 | F19-SIDDANAHALLI NJY | NJY | DLMS Meter | 1.4005 | 1.2831 | 0 | 1.4005 | 8.3796 | 70.3976
565 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903020308 | F20-CHIKKAANKANDAHALLI | NJY | DLMS Meter | 0.455 | 0.41767 | 0 | 0.455 | 8.2037 | 47.2047
566 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903030101 | F21-HUNASANAHALLI NJY | NJY | DLMS Meter | 1.3812 | 1.2779 | 0 | 1.3812 | 7.48 | 48.4427
567 | BRAZ | KOLAR | KGF | BANGARAPETE | BANGARPET_66 | 1230203903020309 | F22-GOLF NJY | NJY | DLMS Meter | 0.81322 | 0.75781 | 0 | 0.81322 | 6.8134 | 18.6171
568 | BMASZ | SOUTH | HSR | S10 | BANNERGHATTAROAD_66 | 1220204901010102 | F02-GOTTIGERE | URBAN MIXED LOAD | DLMS Meter | 2.3712 | 2.2204 | 0.04 | 2.3312 | 4.7521 | 10.3066
569 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | BANNERGHATTAROAD_66 | 1220204901020307 | F03-MANTAPA | RURAL MIXED LOAD | DLMS Meter | 2.8961 | 2.4359 | 0.247 | 2.6491 | 8.0495 | 12.0786
570 | BMASZ | SOUTH | HSR | S10 | BANNERGHATTAROAD_66 | 1220204901020301 | F04-MYLASANDRA | URBAN MIXED LOAD | DLMS Meter | 3.9347 | 3.4629 | 0.31545 | 3.6192 | 4.3196 | 8.5122
571 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | BANNERGHATTAROAD_66 | 1220204901020302 | F06-RAGIHALLI | AGRI | DLMS Meter | 0.39972 | 0.3597 | 0 | 0.39972 | 10.011 | 10.011
572 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | BANNERGHATTAROAD_66 | 1220204901020303 | F08-KASARAGUPPE | NJY | DLMS Meter | 3.19 | 2.5468 | 0.422 | 2.768 | 7.9913 | 18.9518
573 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | BANNERGHATTAROAD_66 | 1220204901010104 | F09-BANNEREGHATTA-NATIONAL-PARK | URBAN MIXED LOAD | DLMS Meter | 1.8926 | 1.6797 | 0.082 | 1.8106 | 7.23 | 27.1258
574 | BMASZ | SOUTH | HSR | S10 | BANNERGHATTAROAD_66 | 1220204901010106 | F10-BASAVANAPURA | URBAN MIXED LOAD | DLMS Meter | 2.6905 | 2.5957 | 0 | 2.6905 | 3.5234 | 15.4552
575 | BMASZ | SOUTH | HSR | S10 | BANNERGHATTAROAD_66 | 1220204901010105 | F11-PURVANKARA | URBAN MIXED LOAD | DLMS Meter | 5.1684 | 4.4093 | 0.004 | 5.1644 | 14.6215 | 25.4284
576 | BMASZ | SOUTH | HSR | S10 | BANNERGHATTAROAD_66 | #N/A | F-12 DLF | #N/A | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
577 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | BANNERGHATTAROAD_66 | 1220204901020305 | F13- BYATARAYANADODDI | AGRI | DLMS Meter | 0.02954 | 0.026578 | 0 | 0.02954 | 10.0271 | 12.0765
578 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | BANNERGHATTAROAD_66 | 1220204901010301 | F14-LAKSHMIPURA | AGRI | DLMS Meter | 0.24156 | 0.21745 | 0 | 0.24156 | 9.9797 | 27.9092
579 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | BANNERGHATTAROAD_66 | 1220204901010108 | F15-SHIVANAHALLY NJY | NJY | DLMS Meter | 2.2406 | 1.7978 | 0.28 | 1.9606 | 8.3037 | 16.3835
580 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | BANUVALLI_66 | 1310301904010101 | F01-BANUVALLI | AGRI | DLMS Meter | 0.9012 | 0.69407 | 0.13 | 0.7712 | 10.0016 | 11.758
581 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | BANUVALLI_66 | 1310301904010102 | F02-SHIVANAHALLI | AGRI | DLMS Meter | 0.4649 | 0.35533 | 0.07 | 0.3949 | 10.0213 | 10.0213
582 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | BANUVALLI_66 | 1310301904010103 | F03-BELLUDI | AGRI | DLMS Meter | 0.548 | 0.4933 | 0 | 0.548 | 9.9812 | 11.4132
583 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | BANUVALLI_66 | 1310301904010104 | F04-SALAGANAHALLI | AGRI | DLMS Meter | 0.8295 | 0.74617 | 0 | 0.8295 | 10.0457 | 10.0457
584 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | BANUVALLI_66 | 1310301904020301 | F05-NJY-ANJANEYA | NJY | DLMS Meter | 1.2274 | 1.0022 | 0.1235 | 1.1039 | 9.2089 | 48.7562
585 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | BANUVALLI_66 | 1310301904020302 | F06-KASHIVISHAWANATHA | NJY | DLMS Meter | 0.7228 | 0.47723 | 0.198 | 0.5248 | 9.0638 | 36.8629
586 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | BANUVALLI_66 | 1310301904020303 | F07-NANDIGAVI-WATER-SUPPLY | WATER WORKS | DLMS Meter | 0.3671 | 0.33657 | 0 | 0.3671 | 8.3175 | 52.3018
587 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | BANUVALLI_66 | 1310301904020304 | F08-GURURENUKA | AGRI | DLMS Meter | 0.9888 | 0.88859 | 0 | 0.9888 | 10.1342 | 10.1342
588 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | BANUVALLI_66 | 1310301904010105 | F09-HOLESIRIGERE | AGRI | DLMS Meter | 0.589 | 0.33655 | 0.215 | 0.374 | 10.0139 | 10.0139
589 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | BANUVALLI_66 | 1310301904020305 | F10-KAMALAPURA | NJY | DLMS Meter | 1.2476 | 1.0758 | 0.074 | 1.1736 | 8.3321 | 47.5621
590 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904010108 | F01-HARALIPURA | NJY | DLMS Meter | 0.5976 | 0.42088 | 0.1295 | 0.4681 | 10.0867 | 58.6214
591 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904010107 | F02-HOSAHALLI | NJY | DLMS Meter | 0.664 | 0.53143 | 0.074 | 0.59 | 9.9264 | 54.6505
592 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904010101 | F03-MARBANAHALLI | AGRI | DLMS Meter | 0.6779 | 0.60984 | 0 | 0.6779 | 10.0394 | 10.0394
593 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904010102 | F04-CHIRADONI | AGRI | DLMS Meter | 0.55912 | 0.5037 | 0 | 0.55912 | 9.912 | 9.912
594 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904010103 | F05-YELLODHALLI AGRI | AGRI | DLMS Meter | 0.7514 | 0.67627 | 0 | 0.7514 | 9.9988 | 9.9988
595 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904010104 | F06-PUNYASTALA | AGRI | DLMS Meter | 0.96194 | 0.86524 | 0 | 0.96194 | 10.0527 | 10.0527
596 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904010105 | F07-SANGAHALLI | NJY | DLMS Meter | 0.86388 | 0.71678 | 0.061 | 0.80288 | 10.7242 | 46.1406
597 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904010106 | F08-BASAVAPATTANA | NJY | DLMS Meter | 1.01 | 0.64152 | 0.291 | 0.71902 | 10.7775 | 27.0376
598 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904020301 | F09-SIDDESHWARANAGAR AGRI | AGRI | DLMS Meter | 0.8068 | 0.726 | 0 | 0.8068 | 10.015 | 10.015
599 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904020302 | F10-NILOGAL AGRI | AGRI | DLMS Meter | 1.0076 | 0.90655 | 0 | 1.0076 | 10.0288 | 10.0288
600 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904020303 | F11-BASAVAPATTANIP | AGRI | DLMS Meter | 0.64094 | 0.5768 | 0 | 0.64094 | 10.0076 | 10.0076
601 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904010109 | F12-KANCHUGARANAHALLI AGRI | AGRI | DLMS Meter | 0.774 | 0.69636 | 0 | 0.774 | 10.0311 | 10.0311
602 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | BASAVAPATNA_66 | 1310107904020306 | F13-DAGINAKATTE NJY | NJY | DLMS Meter | 0.9836 | 0.45808 | 0.468 | 0.5156 | 11.1567 | 39.5625
603 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BEGUR_220 | #N/A | 66KV ITC | #N/A | DLMS Meter | 5.3376 | 5.3376 | 0 | 5.3376 | 0 | 0
604 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BEGUR_220 | #N/A | BIAL-1 | #N/A | DLMS Meter | 19.7856 | 19.7856 | 0 | 19.7856 | 0 | 0
605 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BEGUR_220 | 1210202906010104 | F02-SHETTIGERE | DOMESTIC | DLMS Meter | 1.3311 | 1.0255 | 0.19663 | 1.1345 | 9.6063 | 16.0796
606 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BEGUR_220 | 1210202906010301 | F03-BEGUR | DOMESTIC | DLMS Meter | 2.8797 | 2.4149 | 0.095 | 2.7847 | 13.2794 | 13.2794
607 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BEGUR_220 | 1210202906020101 | F04-MUTHUGADAHALLI | AGRI | DLMS Meter | 0.04446 | 0.040039 | 0 | 0.04446 | 9.9438 | 29.2217
608 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BEGUR_220 | 1210202906010101 | F05-TRUMPET | DOMESTIC | DLMS Meter | 4.1778 | 3.6081 | 0 | 4.1778 | 13.6364 | 15.1422
609 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BEGUR_220 | 1210202906010302 | F07-SEZ | INDUSTRIAL | DLMS Meter | 3.5102 | 2.9771 | 0.1 | 3.4102 | 12.7022 | 12.7022
610 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BEGUR_220 | 1210202906010303 | F08-AEROSPACE | INDUSTRIAL | DLMS Meter | 3.2039 | 3.061 | 0 | 3.2039 | 4.4588 | 4.7698
611 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BEGUR_220 | 1210202906010304 | F09-ITBT | INDUSTRIAL | DLMS Meter | 0.23078 | 0 | 0.23078 | 0 | 0 | #DIV/0!
612 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BEGUR_220 | 1210202906010102 | F10-ITBT | INDUSTRIAL | DLMS Meter | 0.00816 | 0.0080023 | 0 | 0.00816 | 1.9332 | 2.2503
613 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BEGUR_220 | 1210202906010305 | F11-NJY-YARTHIGANAHALLI | NJY | DLMS Meter | 3.1246 | 2.827 | 0 | 3.1246 | 9.5222 | 14.1099
614 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BEGUR_220 | 1210202906060301 | F18-DHAMMANAGI DEVELOPERS | DOMESTIC | DLMS Meter | 0.000736 | 0.000703 | 0 | 0.000736 | 4.4837 | 33.2594
615 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BEGUR_220 | 1210202906060302 | F19-AMIN PROPERTIES | DOMESTIC | DLMS Meter | 3.1033 | 0.7095 | 2.2936 | 0.80972 | 12.3769 | 12.3769
616 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BEGUR_220 | 1210202906060303 | F20-SS DEVELOPERS | DOMESTIC | DLMS Meter | 0.04452 | 0.043477 | 0 | 0.04452 | 2.3428 | 2.3428
617 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELADARA_66 | 1320103904020302 | F02-HOSAHALLI | AGRI | DLMS Meter | 0.86422 | 0.76587 | 0 | 0.86422 | 11.3804 | 11.3804
618 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELADARA_66 | 1320103904010104 | F03-MUDDARAMAYYANAPALYA | AGRI | DLMS Meter | 0.47332 | 0.42579 | 0 | 0.47332 | 10.042 | 10.042
619 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELADARA_66 | 1320103904010101 | F04-AVALIPALYA | AGRI | DLMS Meter | 1.0278 | 0.8875 | 0 | 1.0278 | 13.6485 | 13.6485
620 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELADARA_66 | 1320103904020301 | F05-BELADHARA | NJY | DLMS Meter | 0.52969 | 0.47568 | 0 | 0.52969 | 10.1971 | 35.6547
621 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELADARA_66 | 1320103904020305 | F06-AMALAPURA | NJY | DLMS Meter | 0.91848 | 0.63016 | 0.238 | 0.68048 | 7.3948 | 17.9635
622 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELADARA_66 | 1320103904020303 | F07-JAKKENAHALLI | AGRI | DLMS Meter | 1.1291 | 0.98598 | 0 | 1.1291 | 12.6754 | 12.6754
623 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELADARA_66 | 1320103904020304 | F08-M-GOLLAHALLI | AGRI | DLMS Meter | 0.54686 | 0.31886 | 0.1926 | 0.35426 | 9.9938 | 9.9938
624 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901010101 | F01-BELLAVI | AGRI | DLMS Meter | 0.79014 | 0.71094 | 0 | 0.79014 | 10.0237 | 10.0237
625 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901010102 | F02-DODDERI | AGRI | DLMS Meter | 1.1002 | 0.96047 | 0 | 1.1002 | 12.7031 | 12.7031
626 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901010103 | F03-SINGIPURA | AGRI | DLMS Meter | 0.90084 | 0.79309 | 0 | 0.90084 | 11.9615 | 11.9615
627 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901020301 | F05-BUGUDANAHALLY | NJY | DLMS Meter | 0.6046 | 0.54903 | 0 | 0.6046 | 9.1917 | 29.5834
628 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901020302 | F06-CHANNENAHALLI | AGRI | DLMS Meter | 0.9405 | 0.82259 | 0 | 0.9405 | 12.5372 | 12.5372
629 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901020303 | F07-BANAVARA | AGRI | DLMS Meter | 1.3845 | 1.2262 | 0 | 1.3845 | 11.4361 | 11.4361
630 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901020304 | F08-AGALAGUNTE | AGRI | DLMS Meter | 0.99916 | 0.89476 | 0 | 0.99916 | 10.4487 | 10.4487
631 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901020305 | F09-SUGUNA | INDUSTRIAL | DLMS Meter | 0.87018 | 0.78064 | 0 | 0.87018 | 10.2894 | 15.2601
632 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901020306 | F10-MASHNAPURA-NJY | NJY | DLMS Meter | 0.86156 | 0.76951 | 0 | 0.86156 | 10.6842 | 34.0758
633 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901010104 | F11-WATER-SUPPLY | WATER WORKS | DLMS Meter | 0.47422 | 0.44521 | 0 | 0.47422 | 6.1185 | 6.1185
634 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901010105 | F12-THIMALAPURA | AGRI | DLMS Meter | 0.9684 | 0.87169 | 0 | 0.9684 | 9.9861 | 9.9861
635 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901020307 | F13-DODDA VEERANAHALLI | AGRI | DLMS Meter | 1.0893 | 0.96783 | 0 | 1.0893 | 11.1527 | 11.1527
636 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901020308 | F14-CHIKKA BELLAVI | AGRI | DLMS Meter | 0.7423 | 0.64454 | 0 | 0.7423 | 13.1704 | 13.1704
637 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901010501 | F15-VADAGHATTA | AGRI | DLMS Meter | 1.0906 | 0.95697 | 0 | 1.0906 | 12.2531 | 12.2531
638 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901010502 | F16-BORAGONDANAHALLI | AGRI | DLMS Meter | 1.1514 | 1.0092 | 0 | 1.1514 | 12.3478 | 12.3478
639 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | BELLAVI_66 | 1320103901020309 | F17-MAVINAKUNTE | AGRI | DLMS Meter | 0.88668 | 0.77839 | 0 | 0.88668 | 12.2127 | 12.2127
640 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | BENKIKERE_66 | 1310106903010101 | F01-MADAPURA | AGRI | DLMS Meter | 1.1212 | 1.0057 | 0 | 1.1212 | 10.2948 | 10.2948
641 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | BENKIKERE_66 | 1310106903010102 | F02-HEBBALAGERE | AGRI | DLMS Meter | 2.481 | 1.5185 | 0.79 | 1.691 | 10.1993 | 10.1993
642 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | BENKIKERE_66 | 1310106903010103 | F03-HODIGERE | AGRI | DLMS Meter | 1.4473 | 1.2985 | 0 | 1.4473 | 10.2824 | 10.2824
643 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | BENKIKERE_66 | 1310106903010104 | F04-HONNEBAGI BNK | AGRI | DLMS Meter | 0.79804 | 0.56206 | 0.172 | 0.62604 | 10.2195 | 10.2195
644 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | BENKIKERE_66 | 1310106903020304 | F05-BENKIKERE NJY | NJY | DLMS Meter | 0.39674 | 0.16559 | 0.21 | 0.18674 | 11.3264 | 55.2689
645 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | BENKIKERE_66 | 1310106903020301 | F06-NARASHETTIHALLIIP | AGRI | DLMS Meter | 0.62428 | 0.2748 | 0.3185 | 0.30578 | 10.1305 | 10.1305
646 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | BENKIKERE_66 | 1310106903020302 | F07-BENKIKERE | AGRI | DLMS Meter | 1.1286 | 1.0139 | 0 | 1.1286 | 10.1612 | 10.1612
647 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | BENKIKERE_66 | 1310106903020303 | F08-VADNALBANNIHATTI | AGRI | DLMS Meter | 0.94348 | 0.76097 | 0.096 | 0.84748 | 10.2074 | 10.2074
648 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | BENKIKERE_66 | 1310106903010105 | F09-HEBBALAGERE NJY | NJY | DLMS Meter | 0.8596 | 0.34601 | 0.4745 | 0.3851 | 10.1506 | 40.2365
649 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | BENKIKERE_66 | 1310106903020305 | F10-BENAKANAHALLI | AGRI | DLMS Meter | 0.77878 | 0.41772 | 0.314 | 0.46478 | 10.1263 | 10.1263
650 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906010101 | F01-SASVIHALLI | AGRI | DLMS Meter | 0.75534 | 0.57606 | 0.115 | 0.64034 | 10.0386 | 10.0386
651 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906010102 | F02-NEELAVANJI | AGRI | DLMS Meter | 0.62444 | 0.56189 | 0 | 0.62444 | 10.0165 | 10.0165
652 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906010103 | F03-MUTTIGI | NJY | DLMS Meter | 0.85688 | 0.54879 | 0.2465 | 0.61038 | 10.0897 | 39.057
653 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906010104 | F04-BADA | AGRI | DLMS Meter | 0.62712 | 0.56444 | 0 | 0.62712 | 9.9943 | 9.9943
654 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906010105 | F05-CHIGATERI | AGRI | DLMS Meter | 0.73384 | 0.6603 | 0 | 0.73384 | 10.0217 | 10.0217
655 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906020301 | F06-MATTIHALLI | AGRI | DLMS Meter | 0.77241 | 0.69518 | 0 | 0.77241 | 9.9987 | 9.9987
656 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906010106 | F07-NAGARAKONDA NJY | NJY | DLMS Meter | 0.75004 | 0.47495 | 0.216 | 0.53404 | 11.0647 | 47.6613
657 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906020302 | F08-BENNIHALLI NJY | NJY | DLMS Meter | 0.29812 | 0.19612 | 0.0715 | 0.22662 | 13.4578 | 31.7904
658 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906020303 | F09-HAGARIGUDIHALLI IP | AGRI | DLMS Meter | 0.7356 | 0.66209 | 0 | 0.7356 | 9.9925 | 9.9925
659 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906020304 | F10-GOURIPURA | AGRI | DLMS Meter | 0.50032 | 0.4506 | 0 | 0.50032 | 9.937 | 9.937
660 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | BENNEHALLI_66 | 1310303906020305 | F11-HUNASEHALLI | AGRI | DLMS Meter | 0.67445 | 0.46271 | 0.145 | 0.52945 | 12.6052 | 12.6052
661 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905010101 | F01-CHANGAVARA | AGRI | DLMS Meter | 0.66976 | 0.60261 | 0 | 0.66976 | 10.0261 | 10.0261
662 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905010102 | F02-GC-HALLI | AGRI | DLMS Meter | 0.9412 | 0.84689 | 0 | 0.9412 | 10.0202 | 10.0202
663 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905010103 | F03-HEMDORE | AGRI | DLMS Meter | 0.7034 | 0.60179 | 0.034729 | 0.66867 | 10.0013 | 10.0013
664 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905010104 | F04-MADDAKNAHALLI NJY | NJY | DLMS Meter | 0.61902 | 0.53836 | 0 | 0.61902 | 13.0309 | 48.7627
665 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905010108 | F05-GAJJIGARAHALLI | AGRI | DLMS Meter | 1.1224 | 0.99085 | 0 | 1.1224 | 11.7185 | 11.7185
666 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905010107 | F06-GOWDAGERE | AGRI | DLMS Meter | 1.2114 | 1.0856 | 0 | 1.2114 | 10.3865 | 10.3865
667 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905020301 | F07-YARAVARAHALLI | AGRI | DLMS Meter | 1.1041 | 0.99777 | 0 | 1.1041 | 9.6289 | 9.6289
668 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905020302 | F08-K-RANGANAHALLI | AGRI | DLMS Meter | 1.2201 | 1.0982 | 0 | 1.2201 | 9.9911 | 9.9911
669 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905020303 | F09-BEVINAHALLI | AGRI | DLMS Meter | 0.93516 | 0.8417 | 0 | 0.93516 | 9.9943 | 9.9943
670 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905020304 | F10-HUNASEHALLI NJY | NJY | DLMS Meter | 0.77576 | 0.67914 | 0 | 0.77576 | 12.455 | 61.237
671 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905020305 | F12-HOSUR | AGRI | DLMS Meter | 1.2232 | 1.0899 | 0 | 1.2232 | 10.8953 | 10.8953
672 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | BEVINAHALLI_66 | 1320302905010109 | F13-BETTAPPANAHALLI NJY | NJY | DLMS Meter | 0.6668 | 0.60683 | 0 | 0.6668 | 8.9943 | 69.6894
673 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901010101 | F01-H.MOGENAHALLI | AGRI | DLMS Meter | 0.89966 | 0.80987 | 0 | 0.89966 | 9.9807 | 9.9807
674 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901020301 | F02-HONNAYAKANAHALLI | AGRI | DLMS Meter | 1.3487 | 1.2136 | 0 | 1.3487 | 10.0176 | 10.0176
675 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901010102 | F03-HULUVADI | AGRI | DLMS Meter | 1.3095 | 1.1783 | 0 | 1.3095 | 10.019 | 10.019
676 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901020303 | F05-GOWDAGERE | AGRI | DLMS Meter | 0.84308 | 0.62825 | 0.145 | 0.69808 | 10.0036 | 10.0036
677 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901020304 | F06-BEVOOR | AGRI | DLMS Meter | 0.69356 | 0.62405 | 0 | 0.69356 | 10.0225 | 10.0225
678 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901020305 | F07-KELAGERE | AGRI | DLMS Meter | 0.84008 | 0.75606 | 0 | 0.84008 | 10.0018 | 10.0018
679 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901020306 | F08-MAKALI | AGRI | DLMS Meter | 0.62856 | 0.49358 | 0.08 | 0.54856 | 10.0219 | 10.9879
680 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901010103 | F09-TENKANALLI | NJY | DLMS Meter | 0.26502 | 0.18347 | 0.0643 | 0.20072 | 8.5938 | 38.1202
681 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901020307 | F10-HOSAHALLI | NJY | DLMS Meter | 0.1072 | 0.1072 | 0 | 0.1072 | 0 | 84.1064
682 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901020302 | F11-ARALAPURA-NJY | NJY | DLMS Meter | 0.19893 | 0.16647 | 0.0167 | 0.18223 | 8.6487 | 43.2174
683 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901020309 | F12-KANVA-LIFT | WATER WORKS | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
684 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901020308 | F13-KADAREMANGALA | NJY | DLMS Meter | 0.33766 | 0.22085 | 0.095 | 0.24266 | 8.9878 | 36.4967
685 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901010105 | F14- BYRANAYKANAHALLY NJY | NJY | DLMS Meter | 0.71456 | 0.37071 | 0.307 | 0.40756 | 9.0415 | 18.6004
686 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | BEVOOR_66 | 1220104901010106 | F15-MUNKUNDA | NJY | DLMS Meter | 0.2211 | 0.16484 | 0.04 | 0.1811 | 8.9803 | 40.0404
687 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | BGKERE_66 | 1310403904010101 | F01-GOWRASAMUDRA | AGRI | DLMS Meter | 0.77294 | 0.68091 | 0 | 0.77294 | 11.9061 | 11.9061
688 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | BGKERE_66 | 1310403904010102 | F02-BGKERE | AGRI | DLMS Meter | 1.3326 | 1.1992 | 0 | 1.3326 | 10.0068 | 10.0068
689 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | BGKERE_66 | 1310403904010103 | F03-ABBENAHALLI | AGRI | DLMS Meter | 1.0389 | 0.93506 | 0 | 1.0389 | 9.9973 | 9.9973
690 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | BGKERE_66 | 1310403904010104 | F04-SURAMMANAHALLI | AGRI | DLMS Meter | 1.2296 | 1.1063 | 0 | 1.2296 | 10.031 | 10.031
691 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | BGKERE_66 | 1310403904010105 | F05-NJY-MUSTELLAGUMMI | NJY | DLMS Meter | 0.68522 | 0.5949 | 0 | 0.68522 | 13.1809 | 72.8287
692 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | BGKERE_66 | 1310403904010106 | F07-KONDALAHALLY | NJY | DLMS Meter | 1.4486 | 0.80788 | 0.50756 | 0.94101 | 14.1477 | 43.132
693 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | BGKERE_66 | 1310403904020301 | F10-MOGHALAHALLY NJY | NJY | DLMS Meter | 0.9253 | 0.43025 | 0.42734 | 0.49796 | 13.5962 | 47.0312
694 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901010101 | F01-KALLUPALYA | AGRI | DLMS Meter | 0.54032 | 0.48373 | 0 | 0.54032 | 10.4742 | 10.9532
695 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901010102 | F02-TERADAKUPPE | AGRI | DLMS Meter | 1.0214 | 0.91902 | 0 | 1.0214 | 10.0202 | 10.0202
696 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901010103 | F03-GANGAMMANAGUDDE | AGRI | DLMS Meter | 1.0241 | 0.92159 | 0 | 1.0241 | 10.008 | 10.008
697 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901010104 | F04-KAMANAHALLI | AGRI | DLMS Meter | 0.96184 | 0.86549 | 0 | 0.96184 | 10.0177 | 10.0177
698 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901010105 | F05-BANNIMARADAKATTE -NJY | NJY | DLMS Meter | 0.63404 | 0.28079 | 0.321 | 0.31304 | 10.3013 | 44.5176
699 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901010106 | F06-BHAKTHRAHALLI-NJY | NJY | DLMS Meter | 0.9178 | 0.8176 | 0 | 0.9178 | 10.9177 | 58.6986
700 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901020302 | F07-GIDADAPALYA | AGRI | DLMS Meter | 1.0201 | 0.73786 | 0.2 | 0.8201 | 10.0282 | 10.0282
701 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901010108 | F08-CHIKKAMALAVADI | AGRI | DLMS Meter | 0.84902 | 0.58398 | 0.2 | 0.64902 | 10.0214 | 10.0214
702 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901010301 | F09-KODIHALLI PALYA | AGRI | DLMS Meter | 0.867 | 0.77947 | 0 | 0.867 | 10.0955 | 10.0955
703 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901020301 | F10-VANIGERE IP | AGRI | DLMS Meter | 0.77806 | 0.70002 | 0 | 0.77806 | 10.0297 | 10.0297
704 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | BHAKTHARAHALLI_66 | 1320110901010107 | F11-NJY BAGENAHALLI | NJY | DLMS Meter | 0.6592 | 0.58084 | 0 | 0.6592 | 11.8872 | 60.1255
705 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910010101 | F01-KUBARAHALLY | AGRI | DLMS Meter | 1.0081 | 0.89798 | 0 | 1.0081 | 10.9221 | 10.9221
706 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910010301 | F02-LAKKIHALLI | AGRI | DLMS Meter | 1.9288 | 1.7186 | 0 | 1.9288 | 10.8985 | 10.8985
707 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910010102 | F03-NJYMARIKANUVE | NJY | DLMS Meter | 0.42874 | 0.39652 | 0 | 0.42874 | 7.5149 | 40.4648
708 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910010103 | F04-V.V.PURA | AGRI | DLMS Meter | 1.0832 | 0.967 | 0 | 1.0832 | 10.7245 | 10.7245
709 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910020301 | F05-A.V.KOTTEGE | AGRI | DLMS Meter | 0.91272 | 0.82018 | 0 | 0.91272 | 10.1387 | 10.1387
710 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910020302 | F06-GOGUDDU | AGRI | DLMS Meter | 1.1374 | 0.96908 | 0.050125 | 1.0873 | 10.8724 | 10.8724
711 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910020303 | F07-BHOOTHAYANAHATTI | AGRI | DLMS Meter | 1.5725 | 1.3955 | 0 | 1.5725 | 11.2558 | 11.2558
712 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910020304 | F08-NJYBHARAMAGIRI | NJY | DLMS Meter | 0.61838 | 0.56208 | 0 | 0.61838 | 9.1043 | 59.4605
713 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910010104 | F09- VVS WATER SUPPLY | WATER WORKS | DLMS Meter | 0.64636 | 0.6438 | 0 | 0.64636 | 0.39606 | 86.8269
714 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910010106 | F10-AIMANGALA WATER SUPPLY | WATER WORKS | DLMS Meter | 0.068 | 0.06756 | 0 | 0.068 | 0.64706 | 96.4855
715 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | BHARAMAGIRI_66 | 1310401910010105 | F11-KUNIKERE KAVALU | AGRI | DLMS Meter | 1.1551 | 1.0301 | 0 | 1.1551 | 10.8211 | 10.8211
716 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904020101 | F01-HEGGERE | AGRI | DLMS Meter | 0.7997 | 0.70372 | 0 | 0.7997 | 12.0015 | 12.0015
717 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904010105 | F02-YEMMEHATTI | AGRI | DLMS Meter | 0.98314 | 0.86913 | 0 | 0.98314 | 11.5967 | 11.5967
718 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904010101 | F03-NALLIKATTE | AGRI | DLMS Meter | 0.59775 | 0.53802 | 0 | 0.59775 | 9.9917 | 9.9917
719 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904010102 | F04-KOLAHAL NJY | NJY | DLMS Meter | 0.62972 | 0.29882 | 0.28395 | 0.34577 | 13.5791 | 27.657
720 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904020301 | F05-HEGDEHAL | AGRI | DLMS Meter | 0.56871 | 0.51175 | 0 | 0.56871 | 10.0151 | 10.0151
721 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904020302 | F06-VIJAPUR | AGRI | DLMS Meter | 1.0289 | 0.93035 | 0 | 1.0289 | 9.578 | 9.578
722 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904020303 | F07-SHIVANAKERE | AGRI | DLMS Meter | 1.2036 | 1.0829 | 0 | 1.2036 | 10.031 | 10.031
723 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904020304 | F08-NANDIHALLI | AGRI | DLMS Meter | 1.2497 | 1.1246 | 0 | 1.2497 | 10.0111 | 10.0111
724 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904010103 | F09-BHADURGATTA | AGRI | DLMS Meter | 0.95276 | 0.75039 | 0.11869 | 0.83407 | 10.0325 | 10.4866
725 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904010104 | F10-ADAVIGOLLARAHALLI NJY | NJY | DLMS Meter | 1.9602 | 0.35706 | 1.5475 | 0.4127 | 13.4825 | 31.6013
726 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904010106 | F11-BHARAMASAGARA | DOMESTIC | DLMS Meter | 0.88168 | 0.79893 | 0 | 0.88168 | 9.3855 | 19.945
727 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904020306 | F12-PAMERAHALLI | AGRI | DLMS Meter | 0.57 | 0.50362 | 0 | 0.57 | 11.6451 | 11.6451
728 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904010107 | F13-KOGUNDE NJY | NJY | DLMS Meter | 0.71168 | 0.33401 | 0.32762 | 0.38406 | 13.0317 | 42.8062
729 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904020305 | F14-SKM INDUSTRIAL FEEDER | INDUSTRIAL | DLMS Meter | 1.1528 | 1.1289 | 0 | 1.1528 | 2.0761 | 2.4104
730 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904020307 | F15-KODIHALLI | AGRI | DLMS Meter | 0.9226 | 0.65893 | 0.18269 | 0.73991 | 10.9443 | 10.9443
731 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | BHARAMASAGARA_66 | 1310202904020102 | F16-HARALAKATTE | AGRI | DLMS Meter | 0.093176 | 0.08174 | 0 | 0.093176 | 12.2735 | 12.2735
732 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010101 | F02-ITTAMADU | AGRI | DLMS Meter | 0.55332 | 0.22741 | 0.308 | 0.24532 | 7.2994 | 7.2994
733 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010102 | F03-BYRAMANGALA | AGRI | DLMS Meter | 1.0506 | 0.95313 | 0 | 1.0506 | 9.2762 | 9.4724
734 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010103 | F04-HOSUR | AGRI | DLMS Meter | 0.26451 | 0.24379 | 0 | 0.26451 | 7.8318 | 7.8318
735 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010104 | F05-BANANDUR | URBAN MIXED LOAD | DLMS Meter | 1.2398 | 1.1432 | 0 | 1.2398 | 7.7876 | 15.2118
736 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901020301 | F06-BIDADI-URBAN | URBAN MIXED LOAD | DLMS Meter | 3.1532 | 2.8955 | 0 | 3.1532 | 8.1738 | 26.3001
737 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901020302 | F07-KIADB-1 | INDUSTRIAL | DLMS Meter | 4.2141 | 4.3291 | 0 | 4.2141 | -2.7281 | -2.6783
738 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901020303 | F08-COCA-COLA-GREEN | INDUSTRIAL | DLMS Meter | 3.9681 | 4.0409 | 0 | 3.9681 | -1.8341 | -1.7998
739 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901020304 | F09-KIADB-3 | URBAN MIXED LOAD | DLMS Meter | 2.4274 | 1.1544 | 1.1629 | 1.2645 | 8.7102 | 8.7102
740 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901020305 | F10-SHANUMANGALA | AGRI | DLMS Meter | 0.98874 | 0.91029 | 0 | 0.98874 | 7.9341 | 7.9341
741 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901020306 | F11-TOYOTA-TECHNO-PARK | INDUSTRIAL | DLMS Meter | 4.4293 | 4.5393 | 0 | 4.4293 | -2.4828 | -2.4828
742 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901020307 | F12-EAGLETON-GOLF-RESORT | URBAN MIXED LOAD | DLMS Meter | 5.5709 | 5.1163 | 0 | 5.5709 | 8.1601 | 8.4698
743 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901020308 | F13-TKAP | INDUSTRIAL | DLMS Meter | 3.817 | 3.9449 | 0 | 3.817 | -3.3525 | -3.3525
744 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010105 | F14-INGERSOLLRAND | INDUSTRIAL | DLMS Meter | 0.05526 | 0.05539 | 0 | 0.05526 | -0.23525 | -0.23525
745 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010106 | F15-MITSHUBUSHI | INDUSTRIAL | DLMS Meter | 0.8463 | 0.11655 | 0.73116 | 0.11514 | -1.2246 | -1.2246
746 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010107 | F16-KIADB-2 | INDUSTRIAL | DLMS Meter | 5.5613 | 5.4546 | 0 | 5.5613 | 1.9174 | 2.2074
747 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010108 | F17-MTPL | INDUSTRIAL | DLMS Meter | 3.6942 | 3.6932 | 0 | 3.6942 | 0.02504 | 0.02504
748 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010109 | F18-PGCIL | INDUSTRIAL | DLMS Meter | 0.235 | 0.21321 | 0 | 0.235 | 9.2728 | 9.2728
749 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010201 | F19-NXTEGEN | INDUSTRIAL | DLMS Meter | 1.1516 | 1.1603 | 0 | 1.1516 | -0.75897 | -0.58576
750 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010202 | F20-THOREDODDI | AGRI | DLMS Meter | 1.2924 | 0.33379 | 0.9298 | 0.36258 | 7.9411 | 7.9411
751 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010203 | F21-MEDANAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.3251 | 1.2409 | 0 | 1.3251 | 6.3502 | 13.282
752 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010204 | F22-KIADB-4 | INDUSTRIAL | DLMS Meter | 11.4795 | 7.8228 | 3.6942 | 7.7854 | -0.48154 | 5.6925
753 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010205 | F23-NJY ITTAMADU | NJY | DLMS Meter | 0.59072 | 0.33438 | 0.2261 | 0.36462 | 8.2943 | 23.2384
754 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901030401 | F24-OXYGEN PLANT | INDUSTRIAL | DLMS Meter | 3.0676 | 2.7566 | 0.255 | 2.8126 | 1.9907 | 1.9907
755 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901020401 | F25-BHARATHIYAM | INDUSTRIAL | DLMS Meter | 1.4125 | 1.3863 | 0 | 1.4125 | 1.8535 | 1.8572
756 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901020402 | F26-KODIYALA NJY | NJY | DLMS Meter | 3.3 | 0.57397 | 2.6672 | 0.63281 | 9.2978 | 39.154
757 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010206 | F27-CHOWKAHALLI NJY | NJY | DLMS Meter | 1.1234 | 0.71023 | 0.3395 | 0.7839 | 9.3972 | 44.5481
758 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010111 | F29-LUMAX | INDUSTRIAL | DLMS Meter | 2.4948 | 2.507 | 0 | 2.4948 | -0.48902 | -0.48902
759 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901010112 | F30-HIGH TEMP | INDUSTRIAL | DLMS Meter | 0.3646 | 0.33789 | 0.028495 | 0.3361 | -0.53125 | -0.53125
760 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | BIDADI_220 | 1220101901030402 | F31-TOYOTETSU | INDUSTRIAL | DLMS Meter | 0.1247 | 0.1254 | 0 | 0.1247 | -0.56135 | -0.56135
761 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904010101 | F01-GUDADHALLY-NJY | NJY | DLMS Meter | 0.4837 | 0.44256 | 0 | 0.4837 | 8.5053 | 52.8059
762 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904010102 | F02-KAGGERE | AGRI | DLMS Meter | 0.92036 | 0.80771 | 0 | 0.92036 | 12.2403 | 12.2403
763 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904010103 | F03-BIDARE | AGRI | DLMS Meter | 1.1201 | 0.96033 | 0 | 1.1201 | 14.2638 | 14.2638
764 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904010104 | F04-RANGANATHA-PURA | AGRI | DLMS Meter | 1.0974 | 0.84213 | 0.14687 | 0.95051 | 11.402 | 11.402
765 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904010105 | F05-GOWRIPURA | AGRI | DLMS Meter | 0.83698 | 0.63857 | 0.12856 | 0.70842 | 9.8596 | 9.8596
766 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904010106 | F06-JAINIGARALLY | AGRI | DLMS Meter | 1.5905 | 0.92691 | 0.51978 | 1.0708 | 13.4343 | 13.4343
767 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904020301 | F07-MS PALYA | AGRI | DLMS Meter | 0.9104 | 0.35236 | 0.50224 | 0.40816 | 13.6699 | 14.4057
768 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904020302 | F08-KASHIMATA | AGRI | DLMS Meter | 0.8546 | 0.61355 | 0.15852 | 0.69608 | 11.8563 | 11.8563
769 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904020303 | F09-MUNIYAPPANA PALYA | AGRI | DLMS Meter | 0.902 | 0.48028 | 0.34653 | 0.55547 | 13.5367 | 13.5367
770 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904020304 | F10-BAJJANAKATTE | AGRI | DLMS Meter | 0.5864 | 0.25758 | 0.30024 | 0.28616 | 9.9875 | 9.9875
771 | CTAZ | TUMKUR | TUMKUR | GUBBI | BIDARE_110 | 1320106904020305 | F12-MANNAMA TEMPLE | AGRI | DLMS Meter | 1.1042 | 0.77027 | 0.2299 | 0.8743 | 11.8986 | 11.8986
772 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BIDARKERE_66 | 1310105905010101 | F01-BASTIHALLI | AGRI | DLMS Meter | 0.58673 | 0.52826 | 0 | 0.58673 | 9.9648 | 9.9648
773 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BIDARKERE_66 | 1310105905010102 | F02-YALAGODU NJY | NJY | DLMS Meter | 0.32774 | 0.17291 | 0.12901 | 0.19872 | 12.9898 | 24.0938
774 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BIDARKERE_66 | 1310105905010103 | F03-HOSAHATTI | AGRI | DLMS Meter | 0.71908 | 0.18705 | 0.51103 | 0.20805 | 10.0919 | 10.0919
775 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BIDARKERE_66 | 1310105905010104 | F04-NALLIKATTE | AGRI | DLMS Meter | 1.6626 | 1.4967 | 0 | 1.6626 | 9.9758 | 9.9758
776 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BIDARKERE_66 | 1310105905010105 | F05-ESAMUDRA NJY | NJY | DLMS Meter | 1.035 | 0.45245 | 0.51198 | 0.52302 | 13.4937 | 32.285
777 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BIDARKERE_66 | 1310105905020301 | F06-NIBHAGURU | AGRI | DLMS Meter | 0.4433 | 0.40111 | 0 | 0.4433 | 9.5179 | 9.5179
778 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BIDARKERE_66 | 1310105905020303 | F07-BIDARAKERE | AGRI | DLMS Meter | 0.31801 | 0.28623 | 0 | 0.31801 | 9.9928 | 9.9928
779 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BIDARKERE_66 | 1310105905020304 | F08-KATTIGEHALLY | NJY | DLMS Meter | 0.36464 | 0.24667 | 0.08531 | 0.27933 | 11.6908 | 46.7643
780 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BIDARKERE_66 | 1310105905020302 | F09 DIBADHAHATTI | AGRI | DLMS Meter | 0.3094 | 0.2784 | 0 | 0.3094 | 10.0207 | 10.0207
781 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | BIEC_66 | 1210104906010102 | F02-BIEC | INDUSTRIAL | DLMS Meter | 0.4404 | 0.44566 | 0 | 0.4404 | -1.1944 | -1.1944
782 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | BIEC_66 | 1210104906010103 | F03-MADANAYAKANAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.4822 | 2.1875 | 0.05 | 2.4322 | 10.0597 | 21.7982
783 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | BIEC_66 | 1210104906010104 | F04-T.G.HALLI | URBAN MIXED LOAD | DLMS Meter | 2.3244 | 1.5904 | 0.55 | 1.7744 | 10.3688 | 15.1455
784 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | BIEC_66 | 1210104906010105 | F05-ANCHEPALYA | URBAN MIXED LOAD | DLMS Meter | 1.2288 | 0.82903 | 0.308 | 0.9208 | 9.9668 | 17.9673
785 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | BIEC_66 | 1210104906010106 | F06-BUDDHAJYOTHI LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.5802 | 1.2698 | 1.2064 | 1.3738 | 7.5708 | 8.26
786 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | BIEC_66 | 1210104906010107 | F07-SIDDANAHOSAHALLI | URBAN MIXED LOAD | DLMS Meter | 0.314 | 0.29119 | 0 | 0.314 | 7.2637 | 14.9045
787 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | BIEC_66 | 1210104906010110 | F08-TCI | URBAN MIXED LOAD | DLMS Meter | 3.7268 | 2.4503 | 1.095 | 2.6318 | 6.8969 | 14.9103
788 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | BIEC_66 | 1210104906010108 | F09-GANGONDANAHALLI | URBAN MIXED LOAD | DLMS Meter | 4.3178 | 2.9417 | 1.12 | 3.1978 | 8.009 | 18.2109
789 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | BIEC_66 | 1210104906010109 | F10-MADAVARA | URBAN MIXED LOAD | DLMS Meter | 0.754 | 0.69675 | 0 | 0.754 | 7.5932 | 18.3382
790 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | BIEC_66 | 1210104906010111 | F11-PRESTIGE_JINDAL_CITY | DOMESTIC | DLMS Meter | 0.5894 | 0.58256 | 0 | 0.5894 | 1.1606 | 2.1893
791 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | BIJJAHALLY MUSS | 1220302904010201 | F01-BIJJAHALLY NJY | NJY | DLMS Meter | 0.29748 | 0.23798 | 0.03608 | 0.2614 | 8.9587 | 42.4064
792 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | BIJJAHALLY MUSS | 1220302904010202 | F02-BOMMASANDRA IP | AGRI | DLMS Meter | 0.95714 | 0.86128 | 0 | 0.95714 | 10.0152 | 10.0152
793 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | BIJJAHALLY MUSS | 1220302904010203 | F03-GULAGANAHALLY IP | AGRI | DLMS Meter | 0.18658 | 0.16781 | 0 | 0.18658 | 10.059 | 10.059
794 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | BIJJAHALLY MUSS | 1220302904010204 | F04-KADUSHIVANAHALLY | AGRI | DLMS Meter | 0.53364 | 0.48032 | 0 | 0.53364 | 9.9921 | 9.9921
795 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BILICHODU_66 | 1310105906010204 | F01-GUTTIDURGA(HALAVADANDI) | AGRI | DLMS Meter | 1.0359 | 0.93217 | 0 | 1.0359 | 10.0176 | 10.0176
796 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BILICHODU_66 | 1310105906010201 | F02-HALEKALLU | AGRI | DLMS Meter | 1.1625 | 1.0134 | 0 | 1.1625 | 12.8229 | 12.8229
797 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BILICHODU_66 | 1310105906010202 | F03-CHADARAGOLLA | NJY | DLMS Meter | 0.75572 | 0.48271 | 0.20413 | 0.55159 | 12.4876 | 52.7244
798 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BILICHODU_66 | 1310105906010203 | F04-THUPPADAHALLI | AGRI | DLMS Meter | 0.6473 | 0.56685 | 0 | 0.6473 | 12.4285 | 12.4285
799 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BILICHODU_66 | 1310105906020203 | F05-CHIKKA ARAKERE | AGRI | DLMS Meter | 1.1345 | 0.99025 | 0 | 1.1345 | 12.7129 | 12.7129
800 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BILICHODU_66 | 1310105906020204 | F06-KURUDI | AGRI | DLMS Meter | 1.1213 | 0.52505 | 0.51999 | 0.60129 | 12.6787 | 12.6787
801 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BILICHODU_66 | 1310105906020201 | F07-MUGGIDARAGIHALLI | AGRI | DLMS Meter | 0.9708 | 0.85199 | 0 | 0.9708 | 12.2388 | 12.2388
802 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | BILICHODU_66 | 1310105906020202 | F08-BILICHODU | NJY | DLMS Meter | 0.62128 | 0.40957 | 0.1583 | 0.46298 | 11.5366 | 38.7159
803 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901010101 | F02-SUBBAYYA-CIRCLE | URBAN MIXED LOAD | DLMS Meter | 3.4963 | 3.1804 | 0.18263 | 3.3137 | 4.022 | 5.5265
804 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901010102 | F03-WIPRO-RMU | URBAN MIXED LOAD | DLMS Meter | 1.975 | 1.1916 | 0.72666 | 1.2483 | 4.5486 | 5.5907
805 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901010103 | F04-BMTC-COMPOUND | URBAN MIXED LOAD | DLMS Meter | 1.6431 | 1.3169 | 0.27599 | 1.3671 | 3.6711 | 6.4785
806 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901010104 | F05-PRINTING-PRESS | URBAN MIXED LOAD | DLMS Meter | 4.1041 | 3.9252 | 0 | 4.1041 | 4.3593 | 7.0508
807 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901010105 | F06-WILSON-GARDEN | URBAN MIXED LOAD | DLMS Meter | 2.7438 | 2.4457 | 0.18601 | 2.5578 | 4.3856 | 6.3631
808 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901020301 | F07-F-HUL-KUL-RMU | URBAN MIXED LOAD | DLMS Meter | 2.4226 | 2.064 | 0.2624 | 2.1602 | 4.4542 | 10.1887
809 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901020302 | F08-K.H.-ROAD | URBAN MIXED LOAD | DLMS Meter | 1.9349 | 1.084 | 0.80813 | 1.1268 | 3.7944 | 5.8717
810 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901020303 | F09-CORPORATION-HOSPITAL | URBAN MIXED LOAD | DLMS Meter | 1.876 | 1.79 | 0 | 1.876 | 4.5872 | 7.8787
811 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901020304 | F10-PURE-PHARMA | URBAN MIXED LOAD | DLMS Meter | 2.709 | 0.98102 | 1.6823 | 1.0267 | 4.4479 | 6.5417
812 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901020305 | F11-SHANTHI-ROAD | URBAN MIXED LOAD | DLMS Meter | 2.4447 | 2.3381 | 0 | 2.4447 | 4.3587 | 6.5579
813 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901020306 | F12-MOIN-VILLA-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.099 | 1.975 | 1.0351 | 2.0638 | 4.3043 | 5.3037
814 | BMANZ | EAST | INDIRA NAGAR | E3 | BMTC_66 | 1110102901020307 | F14-ITC-HOTEL | URBAN MIXED LOAD | DLMS Meter | 3.5232 | 1.2934 | 2.1841 | 1.3392 | 3.4144 | 7.9178
815 | BMANZ | EAST | INDIRA NAGAR | E3 | BMTC_66 | 1110102901010106 | F15-UBCITY | COMMERCIAL | DLMS Meter | 3.3107 | 2.89 | 0.38567 | 2.925 | 1.1963 | 1.1963
816 | BMASZ | SOUTH | JAYANAGAR | S2 | BMTC_66 | 1110102901020309 | F16-BMTC | URBAN MIXED LOAD | DLMS Meter | 0.94496 | 0.79441 | 0.12045 | 0.82451 | 3.6501 | 10.4528
817 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010110 | F01-RESAL-CHEMICALS | INDUSTRIAL | DLMS Meter | 2.6902 | 2.4728 | 0.13 | 2.5602 | 3.4137 | 3.4302
818 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010102 | F02-VINAYAKANAGARA | URBAN MIXED LOAD | DLMS Meter | 1.43 | 1.3129 | 0 | 1.43 | 8.1881 | 10.8433
819 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010103 | F03-ORLICON | INDUSTRIAL | DLMS Meter | 6.8926 | 6.7784 | 0 | 6.8926 | 1.6563 | 1.6563
820 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010104 | F04-KSSIDC-ND-STAGE | INDUSTRIAL | DLMS Meter | 2.993 | 2.9357 | 0 | 2.993 | 1.9141 | 3.6476
821 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010106 | F06-APOTEX | INDUSTRIAL | DLMS Meter | 5.6236 | 5.6541 | 0 | 5.6236 | -0.54218 | -0.53861
822 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010107 | F07-MAINE MATERIALS ROAD | INDUSTRIAL | DLMS Meter | 3.8613 | 3.7854 | 0 | 3.8613 | 1.9659 | 1.9659
823 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010101 | F08-BBS-ALLOYS | INDUSTRIAL | DLMS Meter | 5.782 | 5.6355 | 0 | 5.782 | 2.5333 | 2.5333
824 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904020303 | F09-TEGUTECH | INDUSTRIAL | DLMS Meter | 2.6456 | 2.6075 | 0 | 2.6456 | 1.4417 | 1.9244
825 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904020302 | F10-RASHI-GRANITES | INDUSTRIAL | DLMS Meter | 6.3052 | 5.9563 | 0 | 6.3052 | 5.5342 | 5.5342
826 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904020301 | F11-BILLFORGE | INDUSTRIAL | DLMS Meter | 3.6416 | 3.3046 | 0.29 | 3.3516 | 1.4014 | 1.4014
827 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010302 | F12-EFBE PRECISION | INDUSTRIAL | DLMS Meter | 2.5732 | 2.5161 | 0 | 2.5732 | 2.2189 | 3.1934
828 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010304 | F13-MESHA ENGINEERING | INDUSTRIAL | DLMS Meter | 5.023 | 4.584 | 0.34 | 4.683 | 2.1132 | 3.5175
829 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010305 | F14-ARIHANT METALS | INDUSTRIAL | DLMS Meter | 3.3508 | 3.2757 | 0 | 3.3508 | 2.2403 | 2.2403
830 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010108 | F15-GEAROCK | INDUSTRIAL | DLMS Meter | 6.6594 | 6.5864 | 0 | 6.6594 | 1.0962 | 1.0962
831 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010112 | F16-G.M.INFINITY | DOMESTIC | DLMS Meter | 0.7396 | 0.44077 | 0.273 | 0.4666 | 5.5364 | 5.5835
832 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904010109 | F17-MICROLABS | INDUSTRIAL | DLMS Meter | 4.354 | 4.384 | 0 | 4.354 | -0.68902 | -0.68902
833 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | BOMMASANDRA INDL 4TH PHASE_66 | 1220203904020304 | F18-STELIS BIOPHARMA | INDUSTRIAL | DLMS Meter | 1.217 | 1.2176 | 0 | 1.217 | -0.052588 | -0.052588
834 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BOMMEPALLI_ CROSS_66 | 1230402905010101 | F01-KADADANAMARI | NJY | DLMS Meter | 0.2262 | 0.19447 | 0 | 0.2262 | 14.0285 | 64.5881
835 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BOMMEPALLI_ CROSS_66 | 1230402905010102 | F02-BILLANDLAHALLI | AGRI | DLMS Meter | 0.3928 | 0.35348 | 0 | 0.3928 | 10.0107 | 10.0107
836 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BOMMEPALLI_ CROSS_66 | 1230402905010107 | F03-ANKALAMADAGU | AGRI | DLMS Meter | 0.5162 | 0.46437 | 0 | 0.5162 | 10.0415 | 10.0415
837 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BOMMEPALLI_ CROSS_66 | 1230402905010103 | F04-SOMAKALAHALLI | AGRI | DLMS Meter | 0.918 | 0.82623 | 0 | 0.918 | 9.9971 | 9.9971
838 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BOMMEPALLI_ CROSS_66 | 1230402905010104 | F05-KONAKUNTLU | NJY | DLMS Meter | 0.3986 | 0.34437 | 0 | 0.3986 | 13.6056 | 60.2579
839 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BOMMEPALLI_ CROSS_66 | 1230402905010106 | F06-KONAPURA | AGRI | DLMS Meter | 0.3858 | 0.34725 | 0 | 0.3858 | 9.9917 | 9.9917
840 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BOMMEPALLI_ CROSS_66 | 1230402905010105 | F07-CHEEMALAGUTTA | AGRI | DLMS Meter | 0.3664 | 0.32977 | 0 | 0.3664 | 9.9981 | 9.9981
841 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BOODIGERE_66 | 1210202905010105 | F01-MARENAHALLI | DOMESTIC | DLMS Meter | 2.9782 | 2.7137 | 0 | 2.9782 | 8.8808 | 22.415
842 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BOODIGERE_66 | 1210202905010101 | F02-M-HOSAHALLI | DOMESTIC | DLMS Meter | 0.5301 | 0.36422 | 0.12 | 0.4101 | 11.1871 | 19.469
843 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BOODIGERE_66 | 1210202905010102 | F03-NALLUR | AGRI | DLMS Meter | 1.1618 | 1.0082 | 0 | 1.1618 | 13.221 | 13.221
844 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BOODIGERE_66 | 1210202905010103 | F04-KAGGALAHALLI | AGRI | DLMS Meter | 0.99696 | 0.87951 | 0 | 0.99696 | 11.7806 | 15.083
845 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BOODIGERE_66 | 1210202905020301 | F05-MANCHAPPANAHALLI | DOMESTIC | DLMS Meter | 2.7871 | 1.6969 | 0.83115 | 1.956 | 13.2459 | 13.2459
846 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BOODIGERE_66 | 1210202905020302 | F06-BUDIGERE-IP | AGRI | DLMS Meter | 0.63224 | 0.57239 | 0 | 0.63224 | 9.4671 | 9.4914
847 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BOODIGERE_66 | 1210202905020303 | F07-BUDIGERE | NJY | DLMS Meter | 1.9798 | 1.6286 | 0.2084 | 1.7714 | 8.059 | 37.1011
848 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BOODIGERE_66 | 1210202905020304 | F08-GANGAWARA | AGRI | DLMS Meter | 1.2135 | 1.1099 | 0 | 1.2135 | 8.5375 | 10.7759
849 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BOODIGERE_66 | 1210202905020305 | F09-BETTAKOTE | NJY | DLMS Meter | 1.9154 | 1.7727 | 0 | 1.9154 | 7.4538 | 43.4818
850 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BOODIGERE_66 | 1210202905010104 | F10-SOMATHANAHALLI | NJY | DLMS Meter | 2.8294 | 2.5652 | 0 | 2.8294 | 9.3386 | 59.7245
851 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BOODIGERE_66 | 1210202905020306 | F11-HARDWARE-PARK | INDUSTRIAL | DLMS Meter | 3.24 | 2.5037 | 0.51523 | 2.7248 | 8.1114 | 12.0151
852 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BOODIGERE_66 | 1210202905020307 | F12-HARDWARE-PARK | INDUSTRIAL | DLMS Meter | 3.7497 | 3.6271 | 0 | 3.7497 | 3.2682 | 3.2682
853 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | BOODIGERE_66 | 1210202905020308 | F13-HARDWARE-PARK | INDUSTRIAL | DLMS Meter | 0.8252 | 0.41595 | 0.385 | 0.4402 | 5.51 | 5.51
854 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BOODIGERE_66 | 1210202905020309 | F14-AEROSPACE-PACKAGE | INDUSTRIAL | DLMS Meter | 2.7245 | 1.6241 | 0.95031 | 1.7742 | 8.4606 | 8.504
855 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901010101 | F01-DODDASEEBI | AGRI | DLMS Meter | 1.481 | 1.0665 | 0.25525 | 1.2258 | 12.9957 | 12.9957
856 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901010102 | F02-HUNJINAL | AGRI | DLMS Meter | 1.0152 | 0.89296 | 0 | 1.0152 | 12.0389 | 12.0389
857 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901010103 | F03-YALDABAGI | AGRI | DLMS Meter | 1.0314 | 0.90925 | 0 | 1.0314 | 11.8398 | 11.8398
858 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901010104 | F04-KAGENINGANAHALLI | AGRI | DLMS Meter | 1.015 | 0.90966 | 0 | 1.015 | 10.3815 | 10.3815
859 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901020301 | F05-HALDODDERI | AGRI | DLMS Meter | 0.78293 | 0.6815 | 0 | 0.78293 | 12.9553 | 13.2036
860 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901020302 | F06-BRAHMASANDRA | AGRI | DLMS Meter | 1.0282 | 0.91369 | 0 | 1.0282 | 11.1392 | 11.1392
861 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901020303 | F07-AMALAGONDI | AGRI | DLMS Meter | 1.1218 | 0.97563 | 0 | 1.1218 | 13.0284 | 13.0284
862 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901020304 | F08-G C PALYA | AGRI | DLMS Meter | 0.97485 | 0.85432 | 0 | 0.97485 | 12.3637 | 12.3637
863 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901010105 | F09-KALLASHETTIHALLI | NJY | DLMS Meter | 1.0656 | 0.9247 | 0 | 1.0656 | 13.2238 | 53.1282
864 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901020305 | F10-THALAGUNDA | NJY | DLMS Meter | 0.68057 | 0.6016 | 0 | 0.68057 | 11.6035 | 50.8168
865 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901010107 | F11-HETTAPPANAHATTI | AGRI | DLMS Meter | 0.958 | 0.83742 | 0 | 0.958 | 12.5865 | 13.8992
866 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901010108 | F12-DASARAHALLI | AGRI | DLMS Meter | 0.9534 | 0.83649 | 0 | 0.9534 | 12.2627 | 12.3062
867 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901020306 | F13-TARUR | AGRI | DLMS Meter | 0.73629 | 0.64799 | 0 | 0.73629 | 11.9915 | 11.9915
868 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BRAHMASANDRA_66 | 1320303901020307 | F14-VADDANAHALLI | AGRI | DLMS Meter | 0.73197 | 0.66343 | 0 | 0.73197 | 9.3644 | 9.3644
869 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BRIGADE ORCHARDS_66/11 | 1210202908010102 | F01-SIGNATURECLUB | COMMERCIAL | DLMS Meter | 0.25847 | 0.2577 | 0 | 0.25847 | 0.29791 | 0.29791
870 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BRIGADE ORCHARDS_66/11 | 1210202908010101 | F02-ASPEN | DOMESTIC | DLMS Meter | 0.4809 | 0.27624 | 0.17444 | 0.30646 | 9.8626 | 10.909
871 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BRIGADE ORCHARDS_66/11 | 1210202908010103 | F04-PARKSIDE | DOMESTIC | DLMS Meter | 0.0426 | 0.016744 | 0.0242 | 0.0184 | 9 | #DIV/0!
872 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BRIGADE ORCHARDS_66/11 | 1210202908020101 | F08-ARCADE | DOMESTIC | DLMS Meter | 0.097223 | 0.091935 | 0 | 0.097223 | 5.439 | 5.439
873 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | BRIGADE ORCHARDS_66/11 | 1210202908020102 | F11-DEODAR | DOMESTIC | DLMS Meter | 0.2604 | 0.20751 | 0.023268 | 0.23713 | 12.493 | 12.493
874 | BMASZ | WEST | KENGERI | K3 | BRIGADE_MEADOWS_66 | 1140302902010101 | F01-A BLOCK | DOMESTIC | DLMS Meter | 0.27343 | 0.26189 | 0 | 0.27343 | 4.2206 | 4.2206
875 | BMASZ | WEST | KENGERI | K3 | BRIGADE_MEADOWS_66 | 1140302902010103 | F03-B2 BLOCK | DOMESTIC | DLMS Meter | 0.3027 | 0.29278 | 0 | 0.3027 | 3.2776 | 3.2776
876 | BMASZ | WEST | KENGERI | K3 | BRIGADE_MEADOWS_66 | 1140302902010104 | F04-WISTERIA | DOMESTIC | DLMS Meter | 0.21625 | 0.20584 | 0 | 0.21625 | 4.8144 | 7.418
877 | BMASZ | WEST | KENGERI | K3 | BRIGADE_MEADOWS_66 | 1140302902010105 | F05-SRI RAVISHANKAR ASHRAMA | DOMESTIC | DLMS Meter | 4.5777 | 4.2063 | 0 | 4.5777 | 8.1137 | 14.9569
878 | BMASZ | WEST | KENGERI | K3 | BRIGADE_MEADOWS_66 | 1140302902020101 | F07-AGARA | DOMESTIC | DLMS Meter | 3.2419 | 2.4256 | 0.62799 | 2.6139 | 7.202 | 15.1948
879 | BMASZ | WEST | KENGERI | K3 | BRIGADE_MEADOWS_66 | 1140302902020102 | F08-UDIPALYA | DOMESTIC | DLMS Meter | 1.6821 | 1.5274 | 0 | 1.6821 | 9.1977 | 9.92
880 | BMASZ | WEST | KENGERI | K3 | BRIGADE_MEADOWS_66 | 1140302902020103 | F09-AYURVEDA HOSPITAL | DOMESTIC | DLMS Meter | 1.4162 | 1.3113 | 0 | 1.4162 | 7.4086 | 9.4602
881 | BMASZ | WEST | KENGERI | K3 | BRIGADE_MEADOWS_66 | 1140302902020104 | F10-ARCADE | DOMESTIC | DLMS Meter | 0.34727 | 0.33698 | 0 | 0.34727 | 2.9648 | 2.9648
882 | BMASZ | WEST | KENGERI | K3 | BRIGADE_MEADOWS_66 | 1140302902020105 | F11-C BLOCK | DOMESTIC | DLMS Meter | 0.70263 | 0.65585 | 0 | 0.70263 | 6.658 | 8.0295
883 | BMASZ | WEST | KENGERI | K3 | BRIGADE_MEADOWS_66 | 1140302902020106 | F12 SJS | INDUSTRIAL | DLMS Meter | 1.6258 | 1.5771 | 0 | 1.6258 | 2.997 | 3.6246
884 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901010304 | F01-CLUB-HOUSE | COMMERCIAL | DLMS Meter | 0.10437 | 0.10477 | 0 | 0.10437 | -0.38437 | -0.38437
885 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901020105 | F02-F-WTC | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
886 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901010305 | F03-PHOENIX & PEGUSUS | DOMESTIC | DLMS Meter | 1.7057 | 1.6329 | 0 | 1.7057 | 4.2671 | 8.9538
887 | BMANZ | NORTH | MALLESHWARA | C2 | BRIGADEGTW_66 | 1120201901010303 | F04-GEMINI-&-LEO | DOMESTIC | DLMS Meter | 3.5598 | 3.3094 | 0.18 | 3.3798 | 2.0837 | 7.6493
888 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901010302 | F05-VEGA-ANDROMEDA-LYNX | DOMESTIC | DLMS Meter | 0.24497 | 0.22249 | 0 | 0.24497 | 9.1743 | 11.7935
889 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901010101 | F06-ORION-MALL | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
890 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901010306 | F07-SHERTON-HOTEL | COMMERCIAL | DLMS Meter | 2.8244 | 2.8207 | 0 | 2.8244 | 0.13123 | 0.13123
891 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901020104 | F09-WTC CHANGR-OVER | COMMERCIAL | DLMS Meter | 1.7459 | 1.7619 | 0 | 1.7459 | -0.916 | -0.916
892 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901020102 | F10-HERCULAS-DOLARIS CYGRUS | DOMESTIC | DLMS Meter | 0.40167 | 0.36979 | 0 | 0.40167 | 7.9349 | 7.9349
893 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901010301 | F11-SIRIUS-CORONA | DOMESTIC | DLMS Meter | 0.4676 | 0.41883 | 0 | 0.4676 | 10.4294 | 10.4612
894 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901020101 | F12GEMINI & LEO CHANGE-OVER | DOMESTIC | DLMS Meter | 0.11323 | 0.10683 | 0 | 0.11323 | 5.6526 | 9.7104
895 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901010307 | F13-ORION-MALL CHANGE OVER | COMMERCIAL | DLMS Meter | 4.4415 | 4.4532 | 0 | 4.4415 | -0.26376 | -0.26376
896 | BMANZ | NORTH | MALLESHWARA | C1 | BRIGADEGTW_66 | 1120201901020103 | F14-MULTI-LEVEL-CAR-PARKING | COMMERCIAL | DLMS Meter | 1.3439 | 1.3579 | 0 | 1.3439 | -1.0374 | -1.0374
897 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902010102 | F01-BRGABC | DOMESTIC | DLMS Meter | 1.5548 | 1.4991 | 0 | 1.5548 | 3.5784 | 3.5784
898 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020101 | F02-TR.-YARD--DEF-BLOCK | DOMESTIC | DLMS Meter | 0.6012 | 0.57802 | 0 | 0.6012 | 3.8558 | 7.1019
899 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020102 | F03-TR.-YARD-GHI-BLOCK. | DOMESTIC | DLMS Meter | 0.43474 | 0.28133 | 0.14034 | 0.2944 | 4.4373 | 7.941
900 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020103 | F04-SIPANI-FIBER | INDUSTRIAL | DLMS Meter | 3.8142 | 3.7001 | 0 | 3.8142 | 2.9917 | 7.3825
901 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020104 | F05-TR.-YARD-SUMMIT. | DOMESTIC | DLMS Meter | 1.384 | 1.337 | 0 | 1.384 | 3.3972 | 12.6055
902 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020105 | F06-F--TR.YARD-SUMMIT. | DOMESTIC | DLMS Meter | 0.66393 | 0.66 | 0 | 0.66393 | 0.59195 | 3.6575
903 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020301 | F07-F--TR.-YARD-ABC-BLOCK. | DOMESTIC | DLMS Meter | 0.44717 | 0.42967 | 0 | 0.44717 | 3.9143 | 7.231
904 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020302 | F08-DODDANEKUNDI-INDUSTRIAL-AREA | URBAN MIXED LOAD | DLMS Meter | 5.1072 | 4.1021 | 0.7586 | 4.3486 | 5.6683 | 5.6683
905 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020303 | F09-TR.-YARD-GHI-BLOCK. | DOMESTIC | DLMS Meter | 0.090796 | 0.087078 | 0 | 0.090796 | 4.0951 | 9.6034
906 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020304 | F11-TR.YARD-SHOPPING-COMPLEX. | DOMESTIC | DLMS Meter | 2.2431 | 1.6798 | 0.45852 | 1.7846 | 5.8715 | 19.0731
907 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020305 | F12-TR.YARD-SUMMIT.-/-GRAPHITE-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.3068 | 3.2039 | 0 | 3.3068 | 3.1099 | 4.3095
908 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020106 | F13-PHEONIX-MALL | COMMERCIAL | DLMS Meter | 5.0275 | 4.9492 | 0 | 5.0275 | 1.5573 | 1.5573
909 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020306 | F14-BESCOM-OFFICE | COMMERCIAL | DLMS Meter | 3.2063 | 2.6615 | 0.34262 | 2.8637 | 7.0596 | 17.5202
910 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902010108 | F15-VR-MALL | COMMERCIAL | DLMS Meter | 1.8518 | 1.6802 | 0.09177 | 1.76 | 4.5332 | 4.5332
911 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902010201 | F16-NETAPP-INDIA-PVT-LTD | COMMERCIAL | DLMS Meter | 4.7663 | 4.6236 | 0 | 4.7663 | 2.9943 | 2.9943
912 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902010202 | F17-DURGA PETALS | URBAN MIXED LOAD | DLMS Meter | 3.0732 | 2.7865 | 0.13234 | 2.9409 | 5.2512 | 9.3811
913 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902010203 | F18-KUSUMALLOYS | COMMERCIAL | DLMS Meter | 2.2444 | 2.0422 | 0.15215 | 2.0923 | 2.3953 | 9.155
914 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902020201 | F19-UNITED OXYGEN | DOMESTIC | DLMS Meter | 0.39015 | 0.378 | 0 | 0.39015 | 3.1122 | 4.5852
915 | BMANZ | EAST | WHITEFIELD | E12 | BRIGADEMP_66 | 1130202902010204 | F20-KYOTO | COMMERCIAL | DLMS Meter | 3.1599 | 2.2528 | 0.9 | 2.2599 | 0.31201 | 0.31201
916 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902010108 | F01-PEENYA I/A 3RD STAGE | INDUSTRIAL | DLMS Meter | 4.9611 | 3.2599 | 1.6252 | 3.3359 | 2.2808 | 4.0683
917 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902010101 | F02-RD-STG.PIA | INDUSTRIAL | DLMS Meter | 4.6869 | 4.2317 | 0.36014 | 4.3267 | 2.1959 | 4.6635
918 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902020301 | F04-PENNYA-GYMKHANNA | URBAN MIXED LOAD | DLMS Meter | 2.9169 | 2.6175 | 0.27109 | 2.6458 | 1.0718 | 9.0459
919 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902030501 | F07-FGKW-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.5157 | 4.1491 | 0.18 | 4.3357 | 4.3037 | 5.19
920 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902030502 | F08-REMIDEX | INDUSTRIAL | DLMS Meter | 2.5967 | 2.4924 | 0 | 2.5967 | 4.0176 | 9.3109
921 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902030503 | F09-SLV-INDL.-EST. | URBAN MIXED LOAD | DLMS Meter | 4.5199 | 4.3531 | 0 | 4.5199 | 3.6898 | 11.6292
922 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902030504 | F10-IBH-PRAKASHANA | INDUSTRIAL | DLMS Meter | 2.6666 | 2.4212 | 0.19501 | 2.4716 | 2.0411 | 5.1462
923 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902030505 | F11-BAJAJ-PACKAGE | INDUSTRIAL | DLMS Meter | 3.5588 | 3.4195 | 0 | 3.5588 | 3.9143 | 3.9143
924 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902020308 | F13-KHDC | INDUSTRIAL | DLMS Meter | 3.1918 | 3.0495 | 0 | 3.1918 | 4.4577 | 9.6412
925 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902020302 | F14-ND-STG.PEENYA | INDUSTRIAL | DLMS Meter | 2.0878 | 1.6589 | 0.355 | 1.7328 | 4.264 | 9.7604
926 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902020303 | F15-SHIVAPURA | INDUSTRIAL | DLMS Meter | 2.505 | 2.4722 | 0 | 2.505 | 1.3078 | 3.8135
927 | BMANZ | NORTH | PEENYA | N5 | BRINDAVANA_66 | 1120101902020101 | F16-NTTF,-RAJARAM | URBAN MIXED LOAD | DLMS Meter | 3.9825 | 3.3747 | 0.445 | 3.5375 | 4.6011 | 6.6558
928 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902020304 | F17-R.G.NAGAR | INDUSTRIAL | DLMS Meter | 4.7001 | 4.6026 | 0.015018 | 4.6851 | 1.7615 | 6.4908
929 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902020305 | F18-BATA | INDUSTRIAL | DLMS Meter | 4.5367 | 4.3219 | 0.12314 | 4.4136 | 2.077 | 9.9477
930 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902020306 | F19-KIADB-I | URBAN MIXED LOAD | DLMS Meter | 0.43038 | 0.41238 | 0.002216 | 0.42817 | 3.6863 | 5.5647
931 | BMANZ | NORTH | PEENYA | N5 | BRINDAVANA_66 | 1120101902020309 | F20-ICT-WISTRON | INDUSTRIAL | DLMS Meter | 2.0783 | 1.9835 | 0.04 | 2.0383 | 2.6904 | 5.6649
932 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902010105 | F21-SYNTHETIC-PACKERS | INDUSTRIAL | DLMS Meter | 1.3638 | 1.3623 | 0 | 1.3638 | 0.10951 | 0.10951
933 | BMANZ | NORTH | PEENYA | N4 | BRINDAVANA_66 | 1120101902020307 | F22-REXAM | INDUSTRIAL | DLMS Meter | 3.3995 | 3.2092 | 0.2055 | 3.194 | -0.478 | -0.478
934 | BMASZ | SOUTH | HSR | S8 | BTMIVPHASE_66 | 1110302901020101 | F01-CAUVERY-NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.0494 | 2.7947 | 0 | 3.0494 | 8.3539 | 8.3539
935 | BMASZ | SOUTH | HSR | S19 | BTMIVPHASE_66 | 1110302901020102 | F02-HULIMAVU | URBAN MIXED LOAD | DLMS Meter | 2.9348 | 2.7897 | 0 | 2.9348 | 4.943 | 4.943
936 | BMASZ | SOUTH | HSR | S19 | BTMIVPHASE_66 | 1110302901020103 | F03-AKSHAYA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.7644 | 2.2271 | 0.34221 | 2.4222 | 8.0568 | 9.1893
937 | BMASZ | SOUTH | HSR | S8 | BTMIVPHASE_66 | 1110302901020104 | F04-HONGASANDRA | URBAN MIXED LOAD | DLMS Meter | 4.0774 | 3.7542 | 0 | 4.0774 | 7.9261 | 11.1305
938 | BMASZ | SOUTH | HSR | S19 | BTMIVPHASE_66 | 1110302901010102 | F05-B T S LAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.8436 | 1.7154 | 0.04 | 1.8036 | 4.8941 | 6.0894
939 | BMASZ | SOUTH | HSR | S8 | BTMIVPHASE_66 | 1110302901020301 | F06-VIRATNAGARA | URBAN MIXED LOAD | DLMS Meter | 3.6117 | 3.3192 | 0 | 3.6117 | 8.0999 | 10.1208
940 | BMASZ | SOUTH | HSR | S8 | BTMIVPHASE_66 | 1110302901020105 | F07-KALENA-AGRAHARA | URBAN MIXED LOAD | DLMS Meter | 5.7884 | 5.2844 | 0.1155 | 5.6729 | 6.8481 | 8.9176
941 | BMASZ | SOUTH | HSR | S19 | BTMIVPHASE_66 | 1110302901020302 | F08-ARAKERE | URBAN MIXED LOAD | DLMS Meter | 5.7618 | 4.8613 | 0.59 | 5.1718 | 6.0042 | 6.0042
942 | BMASZ | SOUTH | HSR | S10 | BTMIVPHASE_66 | 1110302901020303 | F09-NYANAPPANAHALLI | URBAN MIXED LOAD | DLMS Meter | 4.8896 | 4.4389 | 0.29081 | 4.5988 | 3.4766 | 10.21
943 | BMASZ | SOUTH | HSR | S19 | BTMIVPHASE_66 | 1110302901020304 | F10-SATHYA-SAI-BDA | URBAN MIXED LOAD | DLMS Meter | 4.3102 | 4.146 | 0 | 4.3102 | 3.8107 | 9.4035
944 | BMASZ | SOUTH | HSR | S19 | BTMIVPHASE_66 | 1110302901020305 | F11-KODI-CHIKKANAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.6297 | 1.586 | 0 | 1.6297 | 2.6789 | 5.2844
945 | BMASZ | SOUTH | HSR | S19 | BTMIVPHASE_66 | 1110302901020306 | F12-VIJAYA-BANK-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.4149 | 2.1935 | 0.02 | 2.3949 | 8.4089 | 10.9914
946 | BMASZ | SOUTH | JAYANAGAR | S14 | BTMIVPHASE_66 | 1110302901020308 | F15-VEGACITY | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
947 | BRAZ | KOLAR | KGF | BANGARAPETE | BUDIKOTE_66 | 1230203902010101 | F02-GODAGU-MANDE | AGRI | DLMS Meter | 1.8739 | 1.6866 | 0 | 1.8739 | 9.9983 | 9.9983
948 | BRAZ | KOLAR | KGF | BANGARAPETE | BUDIKOTE_66 | 1230203902020301 | F04-BUDIKOTE NJY | NJY | DLMS Meter | 0.82244 | 0.75135 | 0 | 0.82244 | 8.6432 | 74.0741
949 | BRAZ | KOLAR | KGF | BANGARAPETE | BUDIKOTE_66 | 1230203902020302 | F05-MARKANDAIAH-DAM | AGRI | DLMS Meter | 1.1639 | 1.0369 | 0 | 1.1639 | 10.9103 | 10.9103
950 | BRAZ | KOLAR | KGF | BANGARAPETE | BUDIKOTE_66 | 1230203902010102 | F06-PACHARALAHALLI | AGRI | DLMS Meter | 1.271 | 1.1441 | 0 | 1.271 | 9.9822 | 9.9822
951 | BRAZ | KOLAR | KGF | BANGARAPETE | BUDIKOTE_66 | 1230203902020303 | F07-ALAMBADI | AGRI | DLMS Meter | 1.1922 | 1.0728 | 0 | 1.1922 | 10.0156 | 17.7688
952 | BRAZ | KOLAR | KGF | BANGARAPETE | BUDIKOTE_66 | 1230203902020101 | F08-RAMASANDRA | AGRI | DLMS Meter | 1.343 | 1.2086 | 0 | 1.343 | 10.0076 | 10.0076
953 | BRAZ | KOLAR | KGF | BANGARAPETE | BUDIKOTE_66 | 1230203902010106 | F09-UKKUNDA GADI NJY | NJY | DLMS Meter | 1.2648 | 1.1579 | 0 | 1.2648 | 8.4527 | 74.7244
954 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902010101 | F01-BUKKAPATNA | AGRI | DLMS Meter | 0.95534 | 0.86205 | 0 | 0.95534 | 9.7652 | 9.7652
955 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902010102 | F02-HUNASEKATTE | AGRI | DLMS Meter | 2.0145 | 1.7537 | 0 | 2.0145 | 12.9458 | 12.9458
956 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902010103 | F03-RAMLINGAPURA | AGRI | DLMS Meter | 0.69976 | 0.62968 | 0 | 0.69976 | 10.0147 | 10.243
957 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902010104 | F04-PURA | AGRI | DLMS Meter | 1.6958 | 1.5264 | 0 | 1.6958 | 9.9919 | 9.9919
958 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902020301 | F05-BELLARA | AGRI | DLMS Meter | 1.1305 | 1.0173 | 0 | 1.1305 | 10.0119 | 10.0119
959 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902020302 | F06-RANGANATHAPURA | AGRI | DLMS Meter | 1.4495 | 1.2784 | 0 | 1.4495 | 11.8038 | 11.8038
960 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902020303 | F07-HUILDORE | AGRI | DLMS Meter | 0.97482 | 0.87725 | 0 | 0.97482 | 10.0091 | 10.0091
961 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902020304 | F08-SAKSHIHALLI | AGRI | DLMS Meter | 1.2416 | 1.1072 | 0 | 1.2416 | 10.8284 | 10.8284
962 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902010107 | F09-MANNAMMA TEMPLE NJY | NJY | DLMS Meter | 0.59552 | 0.5367 | 0 | 0.59552 | 9.8778 | 63.9859
963 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902010105 | F10-MARUTHI NJY | NJY | DLMS Meter | 0.95409 | 0.43831 | 0.46019 | 0.4939 | 11.2557 | 38.7642
964 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902020306 | F11-KURUBARAHALLI NJY | NJY | DLMS Meter | 0.26049 | 0.22971 | 0 | 0.26049 | 11.8178 | 18.1498
965 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902020305 | F12-SHAGADADU | NJY | DLMS Meter | 0.53401 | 0.37623 | 0.10467 | 0.42934 | 12.3705 | 53.9314
966 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902010106 | F13-MURUDESHWARA CERAMIC FACTORY | INDUSTRIAL | DLMS Meter | 2.224 | 2.1131 | 0.09525 | 2.1287 | 0.73331 | 0.73331
967 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902010108 | F15-JANAKAL | AGRI | DLMS Meter | 1.3068 | 1.1727 | 0 | 1.3068 | 10.2594 | 10.2594
968 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | BUKKAPATNA_66 | 1320303902010109 | F16-KILARADAHALLI | AGRI | DLMS Meter | 1.078 | 0.97571 | 0 | 1.078 | 9.4892 | 9.4892
969 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BURUDUGUNTE_66 | 1230402906010102 | F01-JANGALHALLI | AGRI | DLMS Meter | 0.3604 | 0.32441 | 0 | 0.3604 | 9.9858 | 9.9858
970 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BURUDUGUNTE_66 | 1230402906010101 | F02-AMITTAHALLI | AGRI | DLMS Meter | 0.8696 | 0.78234 | 0 | 0.8696 | 10.0342 | 10.0342
971 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BURUDUGUNTE_66 | 1230402906010103 | F03-RANGENHALLI | NJY | DLMS Meter | 0.066577 | 0.057921 | 0 | 0.066577 | 13.0015 | 78.1296
972 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BURUDUGUNTE_66 | 1230402906010104 | F04-APPSANHALLI | AGRI | DLMS Meter | 0.2764 | 0.24873 | 0 | 0.2764 | 10.0109 | 10.0109
973 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BURUDUGUNTE_66 | 1230402906010105 | F05-CHIKKAKURBARHALLI | AGRI | DLMS Meter | 0.3434 | 0.30894 | 0 | 0.3434 | 10.0364 | 10.0364
974 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | BURUDUGUNTE_66 | 1230402906010106 | F06-B.ANAPALLI | NJY | DLMS Meter | 0.32 | 0.27739 | 0 | 0.32 | 13.3147 | 68.7133
975 | BMASZ | WEST | RAJAJINAGAR | N8 | BYADRAHALLI_66 | 1140303901010101 | F01-FSUNKADAKATTE | INDUSTRIAL | DLMS Meter | 3.102 | 2.9385 | 0 | 3.102 | 5.27 | 11.2486
976 | BMASZ | WEST | KENGERI | K2 | BYADRAHALLI_66 | 1140303901010102 | F02-UAPAKER | DOMESTIC | DLMS Meter | 4.5789 | 4.2022 | 0.15793 | 4.421 | 4.9487 | 15.9645
977 | BMASZ | WEST | KENGERI | K2 | BYADRAHALLI_66 | 1140303901010103 | F03-UALLALA | URBAN MIXED LOAD | DLMS Meter | 3.7587 | 3.4659 | 0 | 3.7587 | 7.7891 | 19.1907
978 | BMASZ | WEST | KENGERI | K2 | BYADRAHALLI_66 | 1140303901010104 | F04-D-GROUP-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.3331 | 4.0703 | 0.027799 | 4.3053 | 5.4593 | 15.1667
979 | BMASZ | WEST | KENGERI | K2 | BYADRAHALLI_66 | 1140303901010105 | F05-THUNGANAGARA | URBAN MIXED LOAD | DLMS Meter | 5.5347 | 4.6009 | 0.675 | 4.8597 | 5.3246 | 8.0008
980 | BMASZ | WEST | KENGERI | K2 | BYADRAHALLI_66 | 1140303901020301 | F06-FBALAJILAYOUT | DOMESTIC | DLMS Meter | 3.3446 | 2.5083 | 0.71838 | 2.6262 | 4.4882 | 14.8047
981 | BMASZ | WEST | RAJAJINAGAR | N6 | BYADRAHALLI_66 | 1140303901020302 | F07-F-BWSSB | HOSPITAL | DLMS Meter | 2.134 | 1.9964 | 0.11069 | 2.0233 | 1.3324 | 1.3324
982 | BMASZ | WEST | RAJAJINAGAR | N8 | BYADRAHALLI_66 | 1140303901020101 | F08-FANNAPORNESHWARINAGAR | URBAN MIXED LOAD | DLMS Meter | 4.2321 | 3.3118 | 0.71631 | 3.5158 | 5.8022 | 9.9634
983 | BMASZ | WEST | KENGERI | K2 | BYADRAHALLI_66 | 1140303901010106 | F12-VIDYAMANANAGARA | URBAN MIXED LOAD | DLMS Meter | 4.4664 | 2.7347 | 1.5529 | 2.9134 | 6.1348 | 14.201
984 | BMASZ | WEST | KENGERI | K2 | BYADRAHALLI_66 | 1140303901020306 | F14-PROVIDENT TREE | DOMESTIC | DLMS Meter | 1.3025 | 0.27346 | 1.0101 | 0.29239 | 6.4737 | 26.0988
985 | BRAZ | KOLAR | KGF | MULABAGILU | BYRKUR_66 | 1230202903010101 | F01-HONNIKERE | AGRI | DLMS Meter | 1.179 | 1.0613 | 0 | 1.179 | 9.984 | 9.984
986 | BRAZ | KOLAR | KGF | MULABAGILU | BYRKUR_66 | 1230202903010102 | F02-NAGANAHALLI | AGRI | DLMS Meter | 1.0081 | 0.90736 | 0 | 1.0081 | 9.9943 | 9.9943
987 | BRAZ | KOLAR | KGF | MULABAGILU | BYRKUR_66 | 1230202903010103 | F03-PUNYAHALLI | AGRI | DLMS Meter | 0.95562 | 0.86013 | 0 | 0.95562 | 9.9923 | 9.9923
988 | BRAZ | KOLAR | KGF | MULABAGILU | BYRKUR_66 | 1230202903010104 | F04-RAJENDRAHALLI-NJY | NJY | DLMS Meter | 2.0471 | 1.8496 | 0 | 2.0471 | 9.6493 | 71.3432
989 | BRAZ | KOLAR | KGF | MULABAGILU | BYRKUR_66 | 1230202903020301 | F05-BYRKUR | AGRI | DLMS Meter | 0.9999 | 0.89994 | 0 | 0.9999 | 9.997 | 9.997
990 | BRAZ | KOLAR | KGF | MULABAGILU | BYRKUR_66 | 1230202903020302 | F06-KOTHUR | AGRI | DLMS Meter | 1.1142 | 1.0027 | 0 | 1.1142 | 10.0068 | 10.0068
991 | BRAZ | KOLAR | KGF | MULABAGILU | BYRKUR_66 | 1230202903020303 | F08-MUSTOOR | AGRI | DLMS Meter | 1.1645 | 0.81031 | 0.264 | 0.90052 | 10.0179 | 10.0179
992 | BRAZ | KOLAR | KGF | MULABAGILU | BYRKUR_66 | 1230202903020304 | F09-PETHANDLAHALLI NJY | NJY | DLMS Meter | 1.5919 | 1.4381 | 0 | 1.5919 | 9.6581 | 71.4515
993 | BRAZ | KOLAR | KGF | MULABAGILU | BYRKUR_66 | 1230202903010106 | F10-KAGGALANATHA | AGRI | DLMS Meter | 0.3062 | 0.27555 | 0 | 0.3062 | 10.0095 | 10.0095
994 | BMANZ | EAST | SHIVAJINAGAR | E2 | C_STATION_66 | 1130302901010102 | F02-GANESH-RMU | URBAN MIXED LOAD | DLMS Meter | 1.3891 | 0.81318 | 0.53655 | 0.85256 | 4.6198 | 7.542
995 | BMANZ | EAST | SHIVAJINAGAR | E1 | C_STATION_66 | 1130302901010104 | F04-JAYAMAHAL | URBAN MIXED LOAD | DLMS Meter | 2.9678 | 2.6632 | 0 | 2.9678 | 10.264 | 16.7812
996 | BMANZ | EAST | SHIVAJINAGAR | E2 | C_STATION_66 | 1130302901010105 | F05-MK-STREET | URBAN MIXED LOAD | DLMS Meter | 3.8309 | 3.4159 | 0.24974 | 3.5811 | 4.6142 | 9.6301
997 | BMANZ | EAST | SHIVAJINAGAR | E2 | C_STATION_66 | 1130302901020301 | F06-F-CUNNINGHAM-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.9477 | 3.3589 | 0.337 | 3.6107 | 6.9718 | 8.5414
998 | BMANZ | EAST | SHIVAJINAGAR | E1 | C_STATION_66 | 1130302901020302 | F07-F-KEMPROAD | URBAN MIXED LOAD | DLMS Meter | 3.6724 | 3.2555 | 0.15 | 3.5224 | 7.5762 | 10.9486
999 | BMANZ | EAST | SHIVAJINAGAR | E1 | C_STATION_66 | 1130302901020303 | F08-BENSON-TOWN | URBAN MIXED LOAD | DLMS Meter | 2.1381 | 1.0855 | 0.94578 | 1.1923 | 8.9555 | 12.4697
1000 | BMANZ | EAST | SHIVAJINAGAR | E1 | C_STATION_66 | 1130302901020304 | F09-SPENCER-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.0118 | 2.3445 | 0.41988 | 2.5919 | 9.5435 | 11.9626
1001 | BMANZ | EAST | SHIVAJINAGAR | E2 | C_STATION_66 | 1130302901020101 | F10-SULTANJIGUNTA-ROAD | URBAN MIXED LOAD | DLMS Meter | 4.0775 | 3.6116 | 0.24701 | 3.8305 | 5.714 | 8.783
1002 | BMANZ | EAST | INDIRA NAGAR | E3 | C_STATION_66 | 1130302901020401 | F11-RMZ-MILLENIA | COMMERCIAL | DLMS Meter | 2.7301 | 2.6224 | 0 | 2.7301 | 3.9428 | 22.6941
1003 | BMANZ | EAST | SHIVAJINAGAR | E2 | C_STATION_66 | 1130302901020402 | F12-BOWRING-HOSPITAL-&-STNAUX | HOSPITAL | DLMS Meter | 0.70272 | 0.69612 | 0 | 0.70272 | 0.9402 | 0.9402
1004 | BMANZ | EAST | VIDHANASOUDHA | W4 | C_STATION_66 | 1130302901020403 | F13-VASANTHNAGAR | COMMERCIAL | DLMS Meter | 4.4326 | 4.2301 | 0.00928 | 4.4234 | 4.3693 | 6.6319
1005 | BMANZ | EAST | SHIVAJINAGAR | E2 | C_STATION_66 | 1130302901020404 | F14-CHIKKA-BAZAAR | URBAN MIXED LOAD | DLMS Meter | 3.1268 | 1.8642 | 1.1634 | 1.9634 | 5.0556 | 8.3921
1006 | BMANZ | EAST | SHIVAJINAGAR | E2 | C_STATION_66 | 1130302901010106 | F16-THIMMAIAH-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.2601 | 2.3382 | 0.75791 | 2.5022 | 6.5564 | 6.7376
1007 | BMANZ | EAST | SHIVAJINAGAR | E2 | C_STATION_66 | 1130302901010107 | F17-TASKER-TOWN | URBAN MIXED LOAD | DLMS Meter | 2.2406 | 2.1028 | 0 | 2.2406 | 6.1508 | 7.6482
1008 | BMANZ | EAST | SHIVAJINAGAR | E2 | C_STATION_66 | 1130302901020405 | F19-HAINS-ROAD | DOMESTIC | DLMS Meter | 3.6052 | 3.1089 | 0.36251 | 3.2427 | 4.1263 | 7.2876
1009 | BMANZ | EAST | VIDHANASOUDHA | W4 | C_STATION_66 | 1130302901010203 | F20-EXPRESS VIDHANASOUDHA | GOVERNMENT OFFICES | DLMS Meter | 0.099967 | 0.095279 | 0 | 0.099967 | 4.6891 | 4.6991
1010 | BMANZ | NORTH | HEBBAL | C5 | C_STATION_66 | 1130302901020406 | F23-MUNESHWARA NAGARA | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1011 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903010101 | F01-MUDDENAHALLY | AGRI | DLMS Meter | 1.929 | 1.7359 | 0 | 1.929 | 10.0082 | 10.0082
1012 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903010102 | F02-H.S-GARDEN | AGRI | DLMS Meter | 1.3794 | 1.2416 | 0 | 1.3794 | 9.996 | 9.996
1013 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903010103 | F03-KONDENAHALLY | AGRI | DLMS Meter | 1.9859 | 1.7873 | 0 | 1.9859 | 10.0038 | 10.0038
1014 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903020301 | F04-D.HOSUR | AGRI | DLMS Meter | 2.4307 | 2.2532 | 0 | 2.4307 | 7.3032 | 7.3032
1015 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903020302 | F05-NANDI-HILLS | RURAL MIXED LOAD | DLMS Meter | 1.5758 | 1.2303 | 0.22 | 1.3558 | 9.251 | 23.0489
1016 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903020303 | F06-JAKKALAMADAGU | WATER WORKS | DLMS Meter | 1.2234 | 0.34106 | 0.84 | 0.38343 | 11.0496 | 95.7692
1017 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903020304 | F07-INDUSTRIAL-AREA | INDUSTRIAL | DLMS Meter | 2.5206 | 2.4073 | 0 | 2.5206 | 4.4947 | 8.9307
1018 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903020305 | F08-LOCAL | URBAN MIXED LOAD | DLMS Meter | 2.037 | 1.8794 | 0 | 2.037 | 7.7362 | 29.3447
1019 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903030501 | F09-SRIRAMPURA | AGRI | DLMS Meter | 1.2169 | 1.0698 | 0 | 1.2169 | 12.0896 | 12.0896
1020 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903030502 | F10-KUPPAHALLY | AGRI | DLMS Meter | 1.5301 | 1.3771 | 0 | 1.5301 | 10.0011 | 10.0011
1021 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903010105 | F11-KELAGINA TOTA | URBAN MIXED LOAD | DLMS Meter | 1.6987 | 1.5475 | 0 | 1.6987 | 8.9 | 41.8528
1022 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903030503 | F12-CHADALAPURA | AGRI | DLMS Meter | 1.6469 | 1.4824 | 0 | 1.6469 | 9.9856 | 9.9856
1023 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903030504 | F13-SJCIT | RURAL MIXED LOAD | DLMS Meter | 2.4673 | 1.4075 | 1.03 | 1.4373 | 2.0774 | 10.5771
1024 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903010104 | F14-MYLAPPANAHALLI | AGRI | DLMS Meter | 1.1916 | 1.0725 | 0 | 1.1916 | 9.9968 | 9.9968
1025 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903030505 | F15-CHELUMENAHALLI-NJY | NJY | DLMS Meter | 1.4172 | 0.80094 | 0.535 | 0.88222 | 9.2136 | 46.7797
1026 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903030506 | F16-KANGANAHALLI-NJY | NJY | DLMS Meter | 2.8747 | 2.5173 | 0.01 | 2.8647 | 12.124 | 15.5425
1027 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903020307 | F17-KUDUVATHI | AGRI | DLMS Meter | 1.4254 | 1.2829 | 0 | 1.4254 | 10.0001 | 10.0001
1028 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903030509 | F18- DODDAMARALI NJY | NJY | DLMS Meter | 1.1063 | 0.60346 | 0.44 | 0.6663 | 9.4313 | 37.1074
1029 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903030508 | F19-SWAN SILK NJY | NJY | DLMS Meter | 0.6946 | 0.62256 | 0.01 | 0.6846 | 9.062 | 45.9354
1030 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903030510 | F20-AJJAWARA | AGRI | DLMS Meter | 1.3122 | 1.1654 | 0 | 1.3122 | 11.191 | 11.191
1031 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_IA_66 | 1230301903030511 | F21-MEGA DAIRY | INDUSTRIAL | DLMS Meter | 1.127 | 1.125 | 0 | 1.127 | 0.17547 | 0.51151
1032 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902020301 | F02-APMC-YARD | URBAN MIXED LOAD | DLMS Meter | 2.8768 | 2.5769 | 0 | 2.8768 | 10.4254 | 25.7734
1033 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902020302 | F03-PERESANDRA | AGRI | DLMS Meter | 1.3212 | 1.189 | 0 | 1.3212 | 10.0064 | 10.0064
1034 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902020303 | F04-MANCHENAHALLY | AGRI | DLMS Meter | 1.4644 | 1.3181 | 0 | 1.4644 | 9.9872 | 9.9872
1035 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902010101 | F05-MACHANBELE | AGRI | DLMS Meter | 1.9746 | 1.7772 | 0 | 1.9746 | 9.9946 | 9.9946
1036 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902010102 | F06-SIDLAGHATTA | AGRI | DLMS Meter | 1.8762 | 1.6886 | 0 | 1.8762 | 9.9983 | 9.9983
1037 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902010103 | F07-LOCAL | URBAN MIXED LOAD | DLMS Meter | 4.3944 | 3.8778 | 0.03 | 4.3644 | 11.1488 | 27.3898
1038 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902010104 | F08-PARASADINNE-NJY | NJY | DLMS Meter | 2.6267 | 1.711 | 0.7331 | 1.8937 | 9.6453 | 26.9244
1039 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902010105 | F09-DIBBUR | AGRI | DLMS Meter | 0.9944 | 0.89526 | 0 | 0.9944 | 9.9702 | 9.9702
1040 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902020304 | F10-HOSAHUDYA | AGRI | DLMS Meter | 1.4448 | 1.3003 | 0 | 1.4448 | 10.0038 | 10.0038
1041 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902020305 | F11-LINGASHETTYPURA-NJY | NJY | DLMS Meter | 1.6014 | 1.0817 | 0.415 | 1.1864 | 8.8218 | 40.4905
1042 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902020306 | F12-BB-ROAD | URBAN MIXED LOAD | DLMS Meter | 1.438 | 1.2101 | 0.1 | 1.338 | 9.5595 | 25.157
1043 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902020308 | F13-JNS | AGRI | DLMS Meter | 1.0682 | 0.96146 | 0 | 1.0682 | 9.9924 | 9.9924
1044 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902010106 | F14-RANGASTHALA | NJY | DLMS Meter | 0.47 | 0.42113 | 0 | 0.47 | 10.3981 | 45.451
1045 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902020309 | F15-KANDAVARA PUMP HOUSE | WATER WORKS | DLMS Meter | 1.0891 | 1.0905 | 0 | 1.0891 | -0.12855 | -0.12855
1046 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | CBPURA_U_66 | 1230301902020310 | F16-NANJAPURA | AGRI | DLMS Meter | 0.8246 | 0.65174 | 0.1 | 0.7246 | 10.0547 | 19.1151
1047 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906010103 | F01-EMBASSY | COMMERCIAL | DLMS Meter | 3.6256 | 3.5955 | 0.02 | 3.6056 | 0.28042 | 0.28042
1048 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906010104 | F02-CESSNA ROAD | COMMERCIAL | DLMS Meter | 1.3418 | 1.1916 | 0.085 | 1.2568 | 5.1856 | 7.7963
1049 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906010105 | F03-KAVERAPPA LAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.0484 | 3.8076 | 0.03 | 4.0184 | 5.2459 | 14.1913
1050 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906010106 | F04-CISCO B8B | COMMERCIAL | DLMS Meter | 4.4211 | 4.2287 | 0.199 | 4.2221 | -0.15533 | -0.15533
1051 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906010101 | F05-CISCO-B | COMMERCIAL | DLMS Meter | 8.8057 | 8.786 | 0 | 8.8057 | 0.22341 | 0.22341
1052 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906010301 | F06-F-CISCO-BB | COMMERCIAL | DLMS Meter | 0.58362 | 0 | 0.58362 | 0 | 0 | #DIV/0!
1053 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906010302 | F07-F--CISCO-BB | COMMERCIAL | DLMS Meter | 7.9141 | 7.9604 | 0 | 7.9141 | -0.58555 | -0.58555
1054 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906010303 | F08-CISCO-B | COMMERCIAL | DLMS Meter | 8.305 | 8.3528 | 0 | 8.305 | -0.57472 | -0.57472
1055 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906020303 | F09-CISCO B8A | COMMERCIAL | DLMS Meter | 3.1892 | 2.4668 | 0.715 | 2.4742 | 0.30223 | 0.30223
1056 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906020304 | F11-PARDHANI | URBAN MIXED LOAD | DLMS Meter | 2.5415 | 2.4177 | 0 | 2.5415 | 4.8722 | 9.2804
1057 | BMASZ | SOUTH | KORAMANGALA | S7 | CESSNA_66 | 1110203906020305 | F12-BOGANAHALLI | DOMESTIC | DLMS Meter | 2.1626 | 1.9362 | 0.087 | 2.0756 | 6.7161 | 14.3168
1058 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904010101 | F01-RASCHERUVU | AGRI | DLMS Meter | 1.2257 | 1.1032 | 0 | 1.2257 | 9.9954 | 9.9954
1059 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904010102 | F02-VANDAMAN-DAM | WATER WORKS | DLMS Meter | 0.00238 | 0.00215 | 6e-05 | 0.00232 | 7.3276 | 95.8557
1060 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904010103 | F03-UGRANAMPALLI | NJY | DLMS Meter | 1.0357 | 0.84941 | 0.055 | 0.98066 | 13.3842 | 76.1985
1061 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904010104 | F04-CHAKAVELU | AGRI | DLMS Meter | 1.2237 | 1.1012 | 0 | 1.2237 | 10.0109 | 10.0109
1062 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904010107 | F05-MANJUNATHAPURA | NJY | DLMS Meter | 0.47885 | 0.37014 | 0.06 | 0.41885 | 11.6304 | 73.068
1063 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904010105 | F06-MIDDILLU | AGRI | DLMS Meter | 1.0314 | 0.9146 | 0.015 | 1.0164 | 10.019 | 10.019
1064 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904020301 | F07-SHIVAPURA | NJY | DLMS Meter | 0.64597 | 0.53375 | 0.03994 | 0.60603 | 11.9272 | 69.2036
1065 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904010108 | F08-KOTHAPALLI | AGRI | DLMS Meter | 1.082 | 0.91091 | 0.07 | 1.012 | 9.9891 | 9.9891
1066 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904020302 | F09-VENKATESHAPALLI | NJY | DLMS Meter | 0.67797 | 0.608 | 0 | 0.67797 | 10.3207 | 83.2827
1067 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904020303 | F10-PULAGAL | AGRI | DLMS Meter | 0.55744 | 0.50177 | 0 | 0.55744 | 9.9867 | 9.9867
1068 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHAKAVELU_66 | 1230305904020304 | F11-RAMANPADI | AGRI | DLMS Meter | 1.0816 | 0.97355 | 0 | 1.0816 | 9.9935 | 9.9935
1069 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906020302 | F03-DUGGAVARA | AGRI | DLMS Meter | 1.1242 | 1.0097 | 0 | 1.1242 | 10.1823 | 10.1823
1070 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906020303 | F04-REDDIHALLY | AGRI | DLMS Meter | 1.0289 | 0.92564 | 0 | 1.0289 | 10.0359 | 10.7186
1071 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906020304 | F05-SIDDAPURA | AGRI | DLMS Meter | 1.0994 | 0.98589 | 0 | 1.0994 | 10.3233 | 11.2156
1072 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906020305 | F06-NANNIVALA | AGRI | DLMS Meter | 1.3441 | 1.2096 | 0 | 1.3441 | 10.0112 | 10.1563
1073 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906010103 | F09-GANDHINAGARA | URBAN MIXED LOAD | DLMS Meter | 1.249 | 1.1482 | 0 | 1.249 | 8.0729 | 16.0868
1074 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | #N/A | F10-AUXILARY+TOWNWATERSUPPLY(NEW) | #N/A | DLMS Meter | 0.0062 | 0.005525 | 0 | 0.0062 | 10.8871 | 10.8871
1075 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906020102 | F11-VEERADIMMANAHALLY NJY | NJY | DLMS Meter | 0.63142 | 0.55878 | 0 | 0.63142 | 11.5047 | 42.2167
1076 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906010106 | F12-WATER SUPPLY (KUW) | WATER WORKS | DLMS Meter | 0.35358 | 0.23133 | 0.093 | 0.26058 | 11.225 | 59.101
1077 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906020307 | F13-KHB-1 | URBAN MIXED LOAD | DLMS Meter | 0 | 0.000339 | 0 | 0 | 0 | #DIV/0!
1078 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906020308 | F14-KHB-2 | URBAN MIXED LOAD | DLMS Meter | 0 | 3.3e-05 | 0 | 0 | 0 | #DIV/0!
1079 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010101 | F01-MARSOOR | URBAN MIXED LOAD | DLMS Meter | 1.3404 | 1.2714 | 0 | 1.3404 | 5.1511 | 5.1511
1080 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010105 | F03-HEELALIGE NJY | NJY | DLMS Meter | 2.4855 | 1.8271 | 0.481 | 2.0045 | 8.85 | 8.85
1081 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010102 | F04-MUTHANALLUR | AGRI | DLMS Meter | 0.32996 | 0.29707 | 0 | 0.32996 | 9.9671 | 11.1513
1082 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010103 | F05-NERALURU NJY | NJY | DLMS Meter | 3.2604 | 2.5192 | 0.5095 | 2.7509 | 8.4226 | 13.075
1083 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010104 | F06-NIRANTHARA-JYOTHI | NJY | DLMS Meter | 1.6437 | 1.2203 | 0.32 | 1.3237 | 7.8085 | 7.8085
1084 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010301 | F07-ATTIBELE | URBAN MIXED LOAD | DLMS Meter | 1.6616 | 0.036638 | 1.6221 | 0.0395 | 7.2453 | 30.14
1085 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010302 | F08-KEERTI-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.1564 | 2.9321 | 0 | 3.1564 | 7.1073 | 7.1639
1086 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010303 | F09-HENNAGARA | URBAN MIXED LOAD | DLMS Meter | 1.9404 | 1.6053 | 0.185 | 1.7554 | 8.5487 | 17.7003
1087 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010304 | F10-CHANDAPURA | URBAN MIXED LOAD | DLMS Meter | 2.3216 | 2.1215 | 0.055 | 2.2666 | 6.4007 | 10.6767
1088 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010305 | F11-VAKIL-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.2736 | 1.6086 | 0.51 | 1.7636 | 8.7877 | 14.5463
1089 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902020301 | F12-BOMMASANDRA-INDL-AREA | URBAN MIXED LOAD | DLMS Meter | 2.8148 | 2.0744 | 0.5877 | 2.2271 | 6.8545 | 6.8545
1090 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902020302 | F13-SPARSH-HOSPITAL-ROAD | URBAN MIXED LOAD | DLMS Meter | 4.2656 | 3.8046 | 0.209 | 4.0566 | 6.2131 | 6.2131
1091 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902010109 | F15-THIRUMAGONDANAHALLI | AGRI | DLMS Meter | 0.0854 | 0.075863 | 0.0012 | 0.0842 | 9.9014 | 9.9014
1092 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902020308 | F16-ANDHAPURA AGRI | AGRI | DLMS Meter | 0.5584 | 0.041643 | 0.5124 | 0.046 | 9.4717 | 9.4717
1093 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | CHANDAPURA_66 | 1220203902020309 | F17-HALE CHANDAPURA | AGRI | DLMS Meter | 0.000849 | 0.000749 | 0 | 0.000849 | 11.7786 | 11.7786
1094 | BMASZ | WEST | RAJAJINAGAR | N2 | CHANDRA LAYOUT_66 | 1140102901020201 | F01-SUBBANNA-GARDEN | URBAN MIXED LOAD | DLMS Meter | 3.4089 | 2.762 | 0.41694 | 2.992 | 7.6861 | 11.9136
1095 | BMASZ | WEST | RAJAJINAGAR | N2 | CHANDRA LAYOUT_66 | 1140102901020101 | F04-BTS-DEPO | URBAN MIXED LOAD | DLMS Meter | 1.6141 | 1.5114 | 0 | 1.6141 | 6.3567 | 6.5412
1096 | BMASZ | WEST | RAJAJINAGAR | N2 | CHANDRA LAYOUT_66 | 1140102901020301 | F05-ATTIGUPPE | URBAN MIXED LOAD | DLMS Meter | 1.5258 | 1.3841 | 0.020156 | 1.5057 | 8.0716 | 9.4159
1097 | BMASZ | WEST | RAJAJINAGAR | N8 | CHANDRA LAYOUT_66 | 1140102901020303 | F07-FNAGARBHAVI | URBAN MIXED LOAD | DLMS Meter | 5.3673 | 3.1575 | 1.9947 | 3.3726 | 6.3777 | 18.7361
1098 | BMASZ | WEST | RAJAJINAGAR | N2 | CHANDRA LAYOUT_66 | 1140102901020102 | F08-CHANDRA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.8116 | 4.0924 | 0.41498 | 4.3966 | 6.9196 | 10.3429
1099 | BMASZ | WEST | RAJAJINAGAR | N8 | CHANDRA LAYOUT_66 | 1140102901010102 | F09-FMALLATHAHALLY | URBAN MIXED LOAD | DLMS Meter | 4.6322 | 3.8133 | 0.59268 | 4.0396 | 5.6003 | 12.7042
1100 | BMASZ | WEST | RR NAGAR | W6 | CHANDRA LAYOUT_66 | 1140102901020305 | F13-BASE | GOVERNMENT OFFICES | DLMS Meter | 2.7446 | 0.10378 | 2.6339 | 0.11069 | 6.2428 | 6.2428
1101 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | CHANDRAPPA_CIRCLE_66 | 1210105903010102 | F02-CHIKKANAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.7515 | 1.646 | 0 | 1.7515 | 6.0264 | 21.7459
1102 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | CHANDRAPPA_CIRCLE_66 | 1210105903010101 | F03 - LAKKAIANAPALYA | URBAN MIXED LOAD | DLMS Meter | 1.9557 | 1.8557 | 0 | 1.9557 | 5.1152 | 16.9087
1103 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | CHANDRAPPA_CIRCLE_66 | 1210105903010104 | F04-DODDERI | URBAN MIXED LOAD | DLMS Meter | 1.4952 | 1.4181 | 0 | 1.4952 | 5.1549 | 26.1577
1104 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | CHANDRAPPA_CIRCLE_66 | 1210105903010103 | F05-HULUVENAHALLI STONE CRUSHER | INDUSTRIAL | DLMS Meter | 3.9195 | 2.601 | 1.205 | 2.7145 | 4.1837 | 4.1837
1105 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | CHANDRAPPA_CIRCLE_66 | 1210105903020301 | F06- C K THANDYA | INDUSTRIAL | DLMS Meter | 4.1346 | 3.7843 | 0 | 4.1346 | 8.4733 | 10.3239
1106 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | CHANDRAPPA_CIRCLE_66 | 1210105903020302 | F07-LAKSHMIPURA STONE CRUSHER | INDUSTRIAL | DLMS Meter | 1.1588 | 1.1338 | 0 | 1.1588 | 2.1567 | 2.1567
1107 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | CHANDRAPPA_CIRCLE_66 | 1210105903020303 | F08-KURUBARAPALYA CRUSHER | INDUSTRIAL | DLMS Meter | 3.3278 | 3.0993 | 0 | 3.3278 | 6.865 | 8.7782
1108 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | CHANDRAPPA_CIRCLE_66 | 1210105903020304 | F09-GOLLAHALLI STONE CRUSHER | INDUSTRIAL | DLMS Meter | 3.5501 | 3.3397 | 0 | 3.5501 | 5.9277 | 8.5682
1109 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHANGAVARA_66 | 1320302906010101 | F01-KUDUREKUNTE | AGRI | DLMS Meter | 0.7114 | 0.52166 | 0.11273 | 0.59867 | 12.8643 | 12.8643
1110 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHANGAVARA_66 | 1320302906010102 | F02-LAKKAVVANAHALLI | AGRI | DLMS Meter | 1.0126 | 0.74352 | 0.16013 | 0.85247 | 12.7809 | 12.7809
1111 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHANGAVARA_66 | 1320302906010103 | F03-SHASAMARU | AGRI | DLMS Meter | 0.6514 | 0.53042 | 0.041319 | 0.61008 | 13.0578 | 13.0578
1112 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHANGAVARA_66 | 1320302906010104 | F04-M.K.PALYA | AGRI | DLMS Meter | 0.7044 | 0.45027 | 0.18799 | 0.51641 | 12.8073 | 12.8073
1113 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901020301 | F01-NARASHETTYHALLI | AGRI | DLMS Meter | 1.075 | 0.96775 | 0 | 1.075 | 9.975 | 9.975
1114 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901020302 | F02-HARONALLY | AGRI | DLMS Meter | 2.912 | 2.5647 | 0.058 | 2.854 | 10.1378 | 10.1378
1115 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901020303 | F03-HONNEBAGINJY | NJY | DLMS Meter | 1.9852 | 0.80731 | 1.08 | 0.90525 | 10.8188 | 44.1368
1116 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901020304 | F04-HONNEBAGI | AGRI | DLMS Meter | 1.5545 | 1.3575 | 0.045 | 1.5095 | 10.0746 | 10.0746
1117 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901010102 | F05-MUDIGERE | AGRI | DLMS Meter | 0.48214 | 0.43298 | 0 | 0.48214 | 10.197 | 10.197
1118 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901020101 | F06-CHANNAGIRI | DOMESTIC | DLMS Meter | 3.4478 | 2.2142 | 1.035 | 2.4128 | 8.2311 | 15.0576
1119 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901020102 | F07-MAVINAHOLE | AGRI | DLMS Meter | 1.7116 | 1.5354 | 0 | 1.7116 | 10.2911 | 10.2911
1120 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901020103 | F08-AKKLIKATTE | AGRI | DLMS Meter | 2.3052 | 1.1027 | 1.079 | 1.2262 | 10.0717 | 10.0717
1121 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901010501 | F09-AGARABANNIHATTINJY | NJY | DLMS Meter | 0.40148 | 0.3602 | 0 | 0.40148 | 10.2822 | 27.4953
1122 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901010502 | F10-BILLAHALLI | AGRI | DLMS Meter | 1.875 | 1.6501 | 0.037 | 1.838 | 10.2233 | 10.2233
1123 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901010503 | F11-AGARABANNIHATTIIP | AGRI | DLMS Meter | 1.4755 | 1.3241 | 0 | 1.4755 | 10.2567 | 10.2567
1124 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901010504 | F12-GARAGA | AGRI | DLMS Meter | 2.154 | 1.7607 | 0.192 | 1.962 | 10.2587 | 10.2587
1125 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901020104 | F14-AJJIHALLI | AGRI | DLMS Meter | 1.6647 | 1.3317 | 0.182 | 1.4827 | 10.1833 | 10.1833
1126 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901020105 | F15-AJJIHALLINJY | NJY | DLMS Meter | 0.64014 | 0.45067 | 0.144 | 0.49614 | 9.1642 | 32.9128
1127 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901020106 | F16-CHIKKULEGERE | AGRI | DLMS Meter | 0.83134 | 0.74844 | 0 | 0.83134 | 9.9714 | 9.9714
1128 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901010103 | F17-HARONAHALLI NJY | NJY | DLMS Meter | 0.16832 | 0.15221 | 0 | 0.16832 | 9.5722 | 43.7471
1129 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | CHANNAGIRI_66 | 1310106901010104 | F18-GARAGA NJY | NJY | DLMS Meter | 1.2383 | 0.23875 | 0.972 | 0.2663 | 10.3453 | 35.3374
1130 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904010101 | F01-DASHWARA | AGRI | DLMS Meter | 0.10716 | 0.096423 | 0 | 0.10716 | 10.0196 | 10.0196
1131 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904010102 | F02-BRAMANIPURA | AGRI | DLMS Meter | 1.0818 | 0.97364 | 0 | 1.0818 | 9.9945 | 9.9945
1132 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904010103 | F03-B-V-HALLI | AGRI | DLMS Meter | 1.033 | 0.92939 | 0 | 1.033 | 10.0304 | 10.0304
1133 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904010104 | F04-VIRUPSANDRA | AGRI | DLMS Meter | 0.6524 | 0.24043 | 0.385 | 0.2674 | 10.0864 | 10.0864
1134 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904010105 | F05-MUDUGERE | AGRI | DLMS Meter | 1.3201 | 1.1249 | 0.07 | 1.2501 | 10.0138 | 10.0138
1135 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904010106 | F06-WATER-SUPPLY | WATER WORKS | DLMS Meter | 0.53716 | 0.54731 | 0 | 0.53716 | -1.8905 | 13.3971
1136 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020302 | F07-S-S-MILL | URBAN MIXED LOAD | DLMS Meter | 3.7276 | 3.5013 | 0 | 3.7276 | 6.0715 | 16.1179
1137 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020303 | F08-HONGANOOR | AGRI | DLMS Meter | 1.2368 | 1.1131 | 0 | 1.2368 | 10.004 | 11.0383
1138 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020304 | F09-SANKALAGERE | AGRI | DLMS Meter | 1.1904 | 0.97325 | 0.11 | 1.0804 | 9.9179 | 9.9179
1139 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020305 | F10-ABBUR | AGRI | DLMS Meter | 1.3835 | 1.245 | 0 | 1.3835 | 10.0097 | 10.0097
1140 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020306 | F11-CPT | URBAN MIXED LOAD | DLMS Meter | 2.9895 | 2.7401 | 0.05255 | 2.937 | 6.7048 | 13.3485
1141 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020307 | F12-THITTAMARANAHALLI | AGRI | DLMS Meter | 0.5553 | 0.49914 | 0 | 0.5553 | 10.1133 | 10.1133
1142 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020308 | F13-KUDLUR | AGRI | DLMS Meter | 1.5815 | 1.4238 | 0 | 1.5815 | 9.9705 | 9.9705
1143 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020313 | F15-YELEKERE | DOMESTIC | DLMS Meter | 2.5791 | 2.4124 | 0 | 2.5791 | 6.4612 | 16.6091
1144 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020309 | F16-CHAKKERE-NJY | NJY | DLMS Meter | 0.8429 | 0.67984 | 0.095 | 0.7479 | 9.1 | 29.8819
1145 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020310 | F17-THAGACHGERE-NJY | NJY | DLMS Meter | 0.4627 | 0.38074 | 0.044 | 0.4187 | 9.0653 | 25.5179
1146 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020311 | F18-GOVINDAHALLI NJY | NJY | DLMS Meter | 2.0065 | 1.6413 | 0.2019 | 1.8046 | 9.0494 | 22.6418
1147 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904020301 | F20-DEVARAHOSAHALLI-NJY | NJY | DLMS Meter | 0.3502 | 0.19437 | 0.1367 | 0.2135 | 8.9601 | 15.9872
1148 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904010108 | F21-HODAKE HOSAHALLY | NJY | DLMS Meter | 0.88943 | 0.63268 | 0.195 | 0.69443 | 8.8915 | 32.0009
1149 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | CHANNAPATNA_66 | 1220104904010109 | F22-MAHADESHWARA NAGARA | URBAN MIXED LOAD | DLMS Meter | 2.9354 | 2.7643 | 0 | 2.9354 | 5.8295 | 17.3914
1150 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | CHANNARAYAPATNA _66 | 1210202907020102 | F02-POLANAHALLI | AGRI | DLMS Meter | 0.2067 | 0.18598 | 0 | 0.2067 | 10.0223 | 10.0223
1151 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | CHANNARAYAPATNA _66 | 1210202907020101 | F04-NAGANAYAKANAHALLI | AGRI | DLMS Meter | 0.945 | 0.85017 | 0 | 0.945 | 10.0351 | 10.2468
1152 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | CHANNARAYAPATNA _66 | 1210202907010101 | F06-CHANNARAYAPATNA | DOMESTIC | DLMS Meter | 1.1065 | 1.0151 | 0 | 1.1065 | 8.2641 | 40.2489
1153 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | CHANNARAYAPATNA _66 | 1210202907010102 | F07-IBASAPURA | DOMESTIC | DLMS Meter | 0.92869 | 0.83693 | 0.041242 | 0.88745 | 5.6927 | 47.2699
1154 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | CHANNARAYAPATNA _66 | 1210202907010103 | F08-GOPASANDRA | AGRI | DLMS Meter | 1.4626 | 1.2519 | 0.052371 | 1.4102 | 11.2291 | 35.7904
1155 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHATRA_66 | 1220301903010201 | F01-THUNGANI | AGRI | DLMS Meter | 0.8552 | 0.76965 | 0 | 0.8552 | 10.0041 | 10.0041
1156 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHATRA_66 | 1220301903010202 | F02-P RAMPURA | AGRI | DLMS Meter | 0.934 | 0.83059 | 0.011 | 0.923 | 10.0115 | 10.0115
1157 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHATRA_66 | 1220301903010203 | F03-KALLAHALLI INDUSTRIAL(I) | RURAL MIXED LOAD | DLMS Meter | 1.8536 | 1.3854 | 0.3726 | 1.481 | 6.4522 | 13.4429
1158 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHATRA_66 | 1220301903010205 | F05-AGRAHARA | NJY | DLMS Meter | 0.82 | 0.49515 | 0.281 | 0.539 | 8.1348 | 38.5132
1159 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHATRA_66 | 1220301903020201 | F06-VARAGERAHALLI | AGRI | DLMS Meter | 0.7284 | 0.35687 | 0.3319 | 0.3965 | 9.9947 | 9.9947
1160 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHATRA_66 | 1220301903020202 | F07-BUDIGUPPE | AGRI | DLMS Meter | 1.1053 | 0.99487 | 0 | 1.1053 | 9.9905 | 9.9905
1161 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHATRA_66 | 1220301903020203 | F08-PADUVANAGERE | AGRI | DLMS Meter | 0.9102 | 0.69757 | 0.135 | 0.7752 | 10.0146 | 10.0146
1162 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | CHAWANAKUPPE_66 | 1320109901010101 | F01-NILASANDRA | AGRI | DLMS Meter | 0.64338 | 0.57884 | 0 | 0.64338 | 10.0316 | 10.0316
1163 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | CHAWANAKUPPE_66 | 1320109901010102 | F02-CHOWDANAKUPPE | AGRI | DLMS Meter | 0.6 | 0.54011 | 0 | 0.6 | 9.981 | 9.981
1164 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | CHAWANAKUPPE_66 | 1320109901010103 | F03-TAVARAKERE | AGRI | DLMS Meter | 0.48746 | 0.43881 | 0 | 0.48746 | 9.9795 | 9.9795
1165 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | CHAWANAKUPPE_66 | 1320109901010104 | F04-HANGARAHALLI | AGRI | DLMS Meter | 0.70102 | 0.63067 | 0 | 0.70102 | 10.0357 | 10.0357
1166 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | CHAWANAKUPPE_66 | 1320109901010105 | F05-CHOWDANAKUPPE-NJY | IDLE | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1167 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | CHAWANAKUPPE_66 | 1320109901010106 | F06- T BOMMANAHALLI | AGRI | DLMS Meter | 0.51344 | 0.46209 | 0 | 0.51344 | 10.0018 | 10.0018
1168 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | CHAWANAKUPPE_66 | 1320109901020301 | F07-CHIKKONAHALLI NJY | NJY | DLMS Meter | 0.9751 | 0.89183 | 0 | 0.9751 | 8.5395 | 49.1948
1169 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | CHEEMANGALA_66 | 1230404904010101 | F01-H-CROSS | NJY | DLMS Meter | 2.2182 | 1.9434 | 0 | 2.2182 | 12.3853 | 53.6135
1170 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | CHEEMANGALA_66 | 1230404904020101 | F02-ATTIGANAHALLI | AGRI | DLMS Meter | 1.543 | 1.3887 | 0 | 1.543 | 10.0035 | 10.0035
1171 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | CHEEMANGALA_66 | 1230404904010102 | F03-BASAVAPATNA | AGRI | DLMS Meter | 0.82328 | 0.74072 | 0 | 0.82328 | 10.0283 | 10.0283
1172 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | CHEEMANGALA_66 | 1230404904020301 | F04-NJY-CHIKKADASARAHALLI | NJY | DLMS Meter | 1.1692 | 1.0321 | 0 | 1.1692 | 11.7309 | 65.5336
1173 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | CHEEMANGALA_66 | 1230404904010103 | F05-KANNAMANGALA | AGRI | DLMS Meter | 1.2444 | 1.12 | 0 | 1.2444 | 9.9951 | 9.9951
1174 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | CHEEMANGALA_66 | 1230404904020302 | F06-CHIKKADASARAHALLI | AGRI | DLMS Meter | 1.2672 | 1.1407 | 0 | 1.2672 | 9.9852 | 9.9852
1175 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | CHEEMANGALA_66 | 1230404904020303 | F07-CHEEMANGALA | AGRI | DLMS Meter | 1.1727 | 1.0553 | 0 | 1.1727 | 10.0079 | 10.7094
1176 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | CHEEMANGALA_66 | 1230404904020304 | F09-HT MIRACLE | INDUSTRIAL | DLMS Meter | 0.009633 | 0.00981 | 0 | 0.009633 | -1.8374 | -1.8374
1177 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | CHEEMANGALA_66 | 1230404904020305 | F10-NJY CHINTHADAPI | NJY | DLMS Meter | 0.34596 | 0.3032 | 0 | 0.34596 | 12.3599 | 69.337
1178 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | CHEEMANGALA_66 | 1230404904020306 | F11-KALANAYAKANAHALLI | AGRI | DLMS Meter | 0.93503 | 0.839 | 0.0025 | 0.93254 | 10.0304 | 10.0304
1179 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHELUR_66 | 1230305901010101 | F01-CHELUR | NJY | DLMS Meter | 1.252 | 1.0713 | 0.022 | 1.23 | 12.9023 | 59.2526
1180 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHELUR_66 | 1230305901010102 | F02-CHELUR-EXPRESS | AGRI | DLMS Meter | 1.221 | 1.0989 | 0 | 1.221 | 9.9971 | 9.9971
1181 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHELUR_66 | 1230305901010104 | F03-VENKATAPURA | AGRI | DLMS Meter | 0.65446 | 0.58905 | 0 | 0.65446 | 9.995 | 9.995
1182 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | CHELUR_66 | 1230305901010103 | F04-NALLAGUTLAPALLI | AGRI | DLMS Meter | 1.1166 | 1.005 | 0 | 1.1166 | 9.9934 | 9.9934
1183 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902020101 | F01-THALEKOPPA | AGRI | DLMS Meter | 2.6258 | 2.2616 | 0 | 2.6258 | 13.8687 | 13.8687
1184 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902010101 | F02-THONASANAHALLY | AGRI | DLMS Meter | 2.0269 | 1.7657 | 0.003652 | 2.0232 | 12.7265 | 12.7265
1185 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902010102 | F03-YENNEKATTE | AGRI | DLMS Meter | 0.5953 | 0.53569 | 0 | 0.5953 | 10.0133 | 10.0133
1186 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902010103 | F04-NANDIHALLY | AGRI | DLMS Meter | 1.3555 | 0.76038 | 0.49954 | 0.85592 | 11.1625 | 11.1625
1187 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902010104 | F05-CHELUR TOWN | URBAN MIXED LOAD | DLMS Meter | 0.52922 | 0.47323 | 0 | 0.52922 | 10.5805 | 19.6985
1188 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902010105 | F06-JAALGUNI | AGRI | DLMS Meter | 1.09 | 0.98104 | 0 | 1.09 | 9.9978 | 9.9978
1189 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902020102 | F07-IRAKASANDRA | AGRI | DLMS Meter | 1.6804 | 1.5122 | 0 | 1.6804 | 10.0083 | 10.0083
1190 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902020303 | F08-NIMBEKATTE | AGRI | DLMS Meter | 1.9176 | 1.1389 | 0.61987 | 1.2977 | 12.2393 | 12.2393
1191 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902020301 | F09-MADENAHALLY | AGRI | DLMS Meter | 3.0727 | 2.6419 | 0 | 3.0727 | 14.0214 | 14.0214
1192 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902020302 | F10-IDAKANAHALLI | AGRI | DLMS Meter | 1.0347 | 0.93135 | 0 | 1.0347 | 9.9902 | 9.9902
1193 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902020103 | F11 C-HARIVESANDRA | AGRI | DLMS Meter | 1.8127 | 1.5573 | 0 | 1.8127 | 14.0852 | 14.0852
1194 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902020304 | F12-WATER-SUPPLY | WATER WORKS | DLMS Meter | 0.11532 | 0.10415 | 0 | 0.11532 | 9.6896 | 9.6896
1195 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902020104 | F13-NALLUR-NJY | NJY | DLMS Meter | 0.61819 | 0.56185 | 0 | 0.61819 | 9.1137 | 58.8597
1196 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902020305 | F14-KODIYALA-NJY | NJY | DLMS Meter | 0.22548 | 0.20488 | 0 | 0.22548 | 9.137 | 60.7792
1197 | CTAZ | TUMKUR | TUMKUR | GUBBI | CHELURU_66 | 1320106902020307 | F15-SATHENAHALLY-NJY | NJY | DLMS Meter | 0.3227 | 0.29005 | 0 | 0.3227 | 10.1165 | 64.6398
1198 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | CHIKKA_GANGANVADI_66 | 1220103902010101 | F01-TALAVADI | AGRI | DLMS Meter | 0.44066 | 0.39639 | 0 | 0.44066 | 10.0467 | 10.0467
1199 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | CHIKKA_GANGANVADI_66 | 1220103902010105 | F02-DODDAGANGAWADI NJY | NJY | DLMS Meter | 0.20965 | 0.15577 | 0.0376 | 0.17205 | 9.4641 | 47.5073
1200 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | CHIKKA_GANGANVADI_66 | 1220103902010102 | F03-VIRUPASANDRA | AGRI | DLMS Meter | 0.86834 | 0.72745 | 0.06 | 0.80834 | 10.0067 | 10.0067
1201 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | CHIKKA_GANGANVADI_66 | 1220103902010103 | F04-B.S.DODDI | AGRI | DLMS Meter | 0.28415 | 0.23395 | 0.024 | 0.26015 | 10.07 | 10.07
1202 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | CHIKKA_GANGANVADI_66 | 1220103902010104 | F05-AKKUR NJY | NJY | DLMS Meter | 0.221 | 0.15758 | 0.0475 | 0.1735 | 9.1775 | 41.7155
1203 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904010101 | F01-CB-GERE | AGRI | DLMS Meter | 0.74048 | 0.66638 | 0 | 0.74048 | 10.0068 | 10.0068
1204 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904010102 | F02-HULIKUNTE | AGRI | DLMS Meter | 0.87312 | 0.72743 | 0.034855 | 0.83827 | 13.2218 | 13.2218
1205 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904010103 | F03-KOTTI | AGRI | DLMS Meter | 1.4291 | 1.1961 | 0.056311 | 1.3728 | 12.8724 | 12.8724
1206 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904010104 | F04-KAAREHALLI | AGRI | DLMS Meter | 0.8839 | 0.79526 | 0 | 0.8839 | 10.0283 | 10.0283
1207 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904020101 | F05-V.B.HALLI | AGRI | DLMS Meter | 0.9513 | 0.85607 | 0 | 0.9513 | 10.0108 | 10.0108
1208 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904020102 | F06-DEVAGIRI NJY | NJY | DLMS Meter | 0.27904 | 0.25301 | 0 | 0.27904 | 9.3295 | 79.6182
1209 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904020103 | F07-BARAGUR | AGRI | DLMS Meter | 0.8624 | 0.77604 | 0 | 0.8624 | 10.0145 | 10.0145
1210 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904020301 | F08-AGRAHARA | AGRI | DLMS Meter | 1.0385 | 0.93454 | 0 | 1.0385 | 10.0102 | 10.0102
1211 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904020302 | F09-K.R.HALLI | AGRI | DLMS Meter | 1.026 | 0.92312 | 0 | 1.026 | 10.0292 | 10.0292
1212 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904010105 | F10-LAKKANAHALLI NJY | NJY | DLMS Meter | 0.69032 | 0.6188 | 0 | 0.69032 | 10.3598 | 68.125
1213 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904010106 | F11-GANDIHALLI NJY | NJY | DLMS Meter | 0.31757 | 0.28843 | 0 | 0.31757 | 9.1753 | 75.9986
1214 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904010107 | F12-DWARANAKUNTE NJY | NJY | DLMS Meter | 0.6332 | 0.5661 | 0 | 0.6332 | 10.5978 | 64.3494
1215 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904010108 | F13-HAROGERE NJY | NJY | DLMS Meter | 0.5746 | 0.5156 | 0 | 0.5746 | 10.2677 | 58.829
1216 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904010109 | F15-NARAGONDANAHALLI(NJY) | NJY | DLMS Meter | 0.175 | 0.15906 | 0 | 0.175 | 9.1063 | 67.0273
1217 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | CHIKKABANAGERE_66 | 1320302904010110 | F16-BEERANAHALLI | AGRI | DLMS Meter | 0.6224 | 0.56006 | 0 | 0.6224 | 10.0156 | 10.0156
1218 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905010106 | F01-CHIKKANAKATTE | AGRI | DLMS Meter | 0.8342 | 0.59235 | 0.16 | 0.6742 | 12.1408 | 12.1408
1219 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905010101 | F02-HIREKANDAVADI | AGRI | DLMS Meter | 2.3262 | 2.0412 | 0 | 2.3262 | 12.252 | 12.252
1220 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905010102 | F03-GUNJIGANUR | AGRI | DLMS Meter | 1.2511 | 1.1221 | 0 | 1.2511 | 10.3109 | 10.3109
1221 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905010103 | F04-BDURGA | AGRI | DLMS Meter | 0.55896 | 0.50321 | 0 | 0.55896 | 9.9735 | 9.9735
1222 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905020301 | F05-KADUR | AGRI | DLMS Meter | 0.97 | 0.87301 | 0 | 0.97 | 9.9991 | 9.9991
1223 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905020302 | F06-KOTEHAL | AGRI | DLMS Meter | 1.0867 | 0.9443 | 0 | 1.0867 | 13.1048 | 13.1048
1224 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905020303 | F07-CHIKANDVADI | AGRI | DLMS Meter | 2.3095 | 2.0173 | 0 | 2.3095 | 12.6533 | 12.6533
1225 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905020304 | F08-CHIKJAJUR | DOMESTIC | DLMS Meter | 0.75898 | 0.64072 | 0.028 | 0.73098 | 12.3478 | 28.2104
1226 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905010104 | F09-ILTERHOUSE | WATER WORKS | DLMS Meter | 2.0317 | 0.40478 | 1.5742 | 0.45749 | 11.5231 | 42.7059
1227 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905020305 | F10-HIREEMMIGANUR NJY | NJY | DLMS Meter | 0.95564 | 0.43561 | 0.46557 | 0.49007 | 11.1131 | 63.0608
1228 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905020101 | F11-ARASANAGATTA | NJY | DLMS Meter | 0.46032 | 0.25802 | 0.17285 | 0.28747 | 10.2465 | 45.5808
1229 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHIKKAJAJUR_66 | 1310203905020306 | F12-KAVALAHATTI | AGRI | DLMS Meter | 0.5274 | 0.45237 | 0 | 0.5274 | 14.2273 | 14.2273
1230 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010101 | F02-CN-HALLI | URBAN MIXED LOAD | DLMS Meter | 1.9479 | 1.6709 | 0 | 1.9479 | 14.2219 | 14.2219
1231 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010102 | F03-TALUK-OFFICE | URBAN MIXED LOAD | DLMS Meter | 0.72014 | 0.62213 | 0 | 0.72014 | 13.6094 | 13.6989
1232 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010103 | F04-BAVANAHALLI | AGRI | DLMS Meter | 1.3694 | 1.233 | 0 | 1.3694 | 9.9636 | 9.9636
1233 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010104 | F05-SOMANAHALLI | AGRI | DLMS Meter | 1.4302 | 1.2405 | 0 | 1.4302 | 13.2637 | 13.2637
1234 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010105 | F06-JC-PURA | AGRI | DLMS Meter | 0.66332 | 0.59716 | 0 | 0.66332 | 9.9733 | 9.9733
1235 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901020301 | F07-NADUVANAHALLI | AGRI | DLMS Meter | 1.4606 | 1.2952 | 0 | 1.4606 | 11.3262 | 11.3262
1236 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901020302 | F08-MARASANDRA | AGRI | DLMS Meter | 1.0499 | 0.94488 | 0 | 1.0499 | 9.9997 | 9.9997
1237 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901020303 | F09-PAPANAKONA | AGRI | DLMS Meter | 0.82908 | 0.74607 | 0 | 0.82908 | 10.0122 | 10.0122
1238 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010106 | F10-SALAKATTE | AGRI | DLMS Meter | 0.86974 | 0.78287 | 0 | 0.86974 | 9.9879 | 9.9879
1239 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010107 | F11-MUDDENAHALLI-NJY | NJY | DLMS Meter | 0.63322 | 0.57841 | 0 | 0.63322 | 8.6563 | 46.0909
1240 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010108 | F12-GODEKERE-NJY | NJY | DLMS Meter | 0.63725 | 0.54798 | 0 | 0.63725 | 14.0093 | 59.8721
1241 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010109 | F13-HONNEBAGI-NJY | NJY | DLMS Meter | 0.17929 | 0.16358 | 0 | 0.17929 | 8.7607 | 43.6219
1242 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901020304 | F14-SONDENAHALLI | AGRI | DLMS Meter | 0.6976 | 0.62776 | 0 | 0.6976 | 10.0115 | 12.8168
1243 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901020305 | F15-RAYAPPANA PALLYA | AGRI | DLMS Meter | 0.83582 | 0.73448 | 0 | 0.83582 | 12.1243 | 12.1243
1244 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010111 | F16-DABBEGATTA | AGRI | DLMS Meter | 0.7906 | 0.71129 | 0 | 0.7906 | 10.032 | 10.032
1245 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010112 | F17-DURGADAKERE | AGRI | DLMS Meter | 0.9294 | 0.82908 | 0 | 0.9294 | 10.7937 | 10.7937
1246 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010113 | F18-HOSPITAL | HOSPITAL | DLMS Meter | 0.02356 | 0.02355 | 0 | 0.02356 | 0.042445 | 98.311
1247 | CTAZ | TUMKUR | TIPTUR | CN HALLY | CHIKKANAYAKANAHALLI_110 | 1320203901010501 | F19- BYALADAKERE | AGRI | DLMS Meter | 0.8468 | 0.76322 | 0 | 0.8468 | 9.8703 | 9.8703
1248 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903010106 | F01-KALSATKUNTE | AGRI | DLMS Meter | 0.81164 | 0.7102 | 0 | 0.81164 | 12.498 | 12.498
1249 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903010101 | F02-KUCHANGI | AGRI | DLMS Meter | 0.93338 | 0.75589 | 0.0667 | 0.86668 | 12.7831 | 12.7831
1250 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903010102 | F03-CT-KERE | AGRI | DLMS Meter | 0.89666 | 0.77737 | 0 | 0.89666 | 13.3037 | 14.7065
1251 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903010103 | F04-BOMMANHALLI | AGRI | DLMS Meter | 0.62252 | 0.56029 | 0 | 0.62252 | 9.9969 | 9.9969
1252 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903020301 | F05-KONTHIHALLI | AGRI | DLMS Meter | 1.0617 | 0.93257 | 0 | 1.0617 | 12.1661 | 12.1661
1253 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903010105 | F06 DEVELAPURA | AGRI | DLMS Meter | 0.81752 | 0.73569 | 0 | 0.81752 | 10.0091 | 10.0091
1254 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903020302 | F07-KARIKERE | AGRI | DLMS Meter | 0.89366 | 0.79587 | 0 | 0.89366 | 10.943 | 10.943
1255 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903010107 | F08-HIRETHOTLUKERE | AGRI | DLMS Meter | 1.0206 | 0.89501 | 0 | 1.0206 | 12.306 | 12.306
1256 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903010104 | F09- RG HALLI | NJY | DLMS Meter | 0.61008 | 0.50413 | 0.061016 | 0.54906 | 8.1846 | 42.746
1257 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903020303 | F10-HEREGUNDAGAL-NJY | NJY | DLMS Meter | 0.30327 | 0.27774 | 0 | 0.30327 | 8.4193 | 20.3843
1258 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903020305 | F12-MAVUKERE | NJY | DLMS Meter | 0.3355 | 0.30483 | 0 | 0.3355 | 9.1419 | 10.1312
1259 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | CHIKKATOTLUKERE_66 | 1320103903020306 | F13-LOTUS FARMS | INDUSTRIAL | DLMS Meter | 0.60786 | 0.56808 | 0.021 | 0.58686 | 3.2001 | 3.2001
1260 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHIKKENAHALLI_66 | 1220301902020301 | F01-UDARAHALLI | AGRI | DLMS Meter | 1.1346 | 1.0213 | 0 | 1.1346 | 9.9929 | 9.9929
1261 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHIKKENAHALLI_66 | 1220301902020302 | F02-MATHIKUNTTE | AGRI | DLMS Meter | 1.2561 | 1.1035 | 0.03 | 1.2261 | 10.0002 | 10.0002
1262 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHIKKENAHALLI_66 | 1220301902010108 | F04-KOTTAGALLU | AGRI | DLMS Meter | 1.4403 | 1.2961 | 0 | 1.4403 | 10.0137 | 10.0137
1263 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHIKKENAHALLI_66 | 1220301902010102 | F05-HULIKERE | AGRI | DLMS Meter | 0.84904 | 0.76393 | 0 | 0.84904 | 10.0239 | 10.0239
1264 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHIKKENAHALLI_66 | 1220301902010112 | F06-VEERABHADRA NJY | NJY | DLMS Meter | 1.0506 | 0.72359 | 0.2542 | 0.7964 | 9.1423 | 46.8288
1265 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHIKKENAHALLI_66 | 1220301902010106 | F07-MARUTHI NJY | NJY | DLMS Meter | 0.161 | 0.1388 | 0 | 0.161 | 13.7871 | 42.7575
1266 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHIKKENAHALLI_66 | 1220301902010103 | F08-SRS-BETTA | AGRI | DLMS Meter | 0.94462 | 0.85008 | 0 | 0.94462 | 10.0084 | 10.0084
1267 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHIKKENAHALLI_66 | 1220301902010104 | F09-KOTAHALI | AGRI | DLMS Meter | 0.9702 | 0.58195 | 0.3236 | 0.6466 | 9.9991 | 9.9991
1268 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHIKKENAHALLI_66 | 1220301902010101 | F10-ANAJAWADI | NJY | DLMS Meter | 0.98102 | 0.17698 | 0.79006 | 0.19096 | 7.3208 | 59.8681
1269 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | CHIKKENAHALLI_66 | 1220301902010113 | F11-BASAVESHWARA NJY | NJY | DLMS Meter | 0.5907 | 0.40675 | 0.154 | 0.4367 | 6.8578 | 53.4133
1270 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | CHILLUR_66 | 1310302901010101 | F01-CHILUR | AGRI | DLMS Meter | 1.543 | 1.3821 | 0 | 1.543 | 10.4236 | 10.4236
1271 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | CHILLUR_66 | 1310302901010102 | F02-MALALI | NJY | DLMS Meter | 0.76044 | 0.62732 | 0.04033 | 0.72011 | 12.8854 | 31.7278
1272 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | CHILLUR_66 | 1310302901010103 | F03-TGOPAGONDANAHALLI | AGRI | DLMS Meter | 1.2695 | 1.1451 | 0 | 1.2695 | 9.7943 | 9.7943
1273 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | CHILLUR_66 | 1310302901010104 | F04-KURUVA NJY | NJY | DLMS Meter | 0.83352 | 0.47458 | 0.28831 | 0.54521 | 12.9546 | 32.8944
1274 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | CHILLUR_66 | 1310302901020301 | F05-GADEKATTE | AGRI | DLMS Meter | 1.7275 | 1.482 | 0 | 1.7275 | 14.2105 | 14.2105
1275 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | CHILLUR_66 | 1310302901020302 | F06-GOVINAKOVI | AGRI | DLMS Meter | 0.93559 | 0.84201 | 0 | 0.93559 | 10.0019 | 10.0019
1276 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | CHILLUR_66 | 1310302901020303 | F07-CHI.KADADAKATTE | AGRI | DLMS Meter | 1.0416 | 0.92928 | 0 | 1.0416 | 10.7838 | 10.7838
1277 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | CHILLUR_66 | 1310302901020304 | F08-MARIGONDANAHALLI | AGRI | DLMS Meter | 2.0067 | 1.7456 | 0 | 2.0067 | 13.0123 | 13.0123
1278 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | CHILLUR_66 | 1310302901020305 | F09-KENGATTE | AGRI | DLMS Meter | 0.9626 | 0.84483 | 0 | 0.9626 | 12.2347 | 12.2347
1279 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010101 | F01-BURAMAKALAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.4055 | 1.2397 | 0 | 1.4055 | 11.7931 | 57.1952
1280 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010102 | F02-GOPALAPURA | AGRI | DLMS Meter | 1.9269 | 1.7342 | 0 | 1.9269 | 10.001 | 10.001
1281 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901020301 | F03-SEEKAL | AGRI | DLMS Meter | 1.2268 | 1.1042 | 0 | 1.2268 | 9.9903 | 9.9903
1282 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901020302 | F04-KAIWARA | AGRI | DLMS Meter | 1.814 | 1.6328 | 0 | 1.814 | 9.9891 | 9.9891
1283 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010103 | F05-MURUGAMALLA | AGRI | DLMS Meter | 0.84856 | 0.76367 | 0 | 0.84856 | 10.0046 | 10.0046
1284 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010104 | F06-L-D-KOTE | AGRI | DLMS Meter | 1.0019 | 0.90165 | 0 | 1.0019 | 10.0101 | 10.0101
1285 | BRAZ | KOLAR | Chinthamani | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010105 | F07-LOCAL | URBAN MIXED LOAD | DLMS Meter | 4.4266 | 3.8391 | 0.085 | 4.3416 | 11.5741 | 23.524
1286 | BRAZ | KOLAR | Chinthamani | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901020303 | F08-LOCAL 1 | URBAN MIXED LOAD | DLMS Meter | 3.5815 | 3.0789 | 0 | 3.5815 | 14.0344 | 23.1449
1287 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901020304 | F09-NANDIGANAHALLI | AGRI | DLMS Meter | 1.191 | 1.0719 | 0 | 1.191 | 9.9992 | 9.9992
1288 | BRAZ | KOLAR | Chinthamani | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010109 | F10-PRABHAKAR LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.8621 | 2.5962 | 0 | 2.8621 | 9.2924 | 19.9269
1289 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901020305 | F11-LOCAL 3 | URBAN MIXED LOAD | DLMS Meter | 3.2056 | 1.4902 | 1.52 | 1.6856 | 11.5929 | 11.5929
1290 | BRAZ | KOLAR | Chinthamani | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010107 | F13-SAPTHAGIRI | URBAN MIXED LOAD | DLMS Meter | 1.9023 | 1.7393 | 0 | 1.9023 | 8.5645 | 23.2472
1291 | BRAZ | KOLAR | Chinthamani | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010108 | F14-DAIRY+ARCHIDPLY | INDUSTRIAL | DLMS Meter | 0.80001 | 0.66305 | 0.11181 | 0.6882 | 3.6543 | 4.7449
1292 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010110 | F16-SERICO | GOVERNMENT OFFICES | DLMS Meter | 0.72146 | 0.1215 | 0.58656 | 0.1349 | 9.9326 | 14.9917
1293 | BRAZ | KOLAR | Chinthamani | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901020308 | F17-RAMAMANDIRA | URBAN MIXED LOAD | DLMS Meter | 0.8708 | 0.74966 | 0 | 0.8708 | 13.9116 | 24.2368
1294 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010112 | F18-KURUTAHALLI-NJY | NJY | DLMS Meter | 0.843 | 0.74645 | 0 | 0.843 | 11.4527 | 74.7653
1295 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903020301 | F01-COPPERMINES | NJY | DLMS Meter | 1.0695 | 0.92938 | 0.056523 | 1.013 | 8.2528 | 19.6697
1296 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903020302 | F02-KYADIGERE | AGRI | DLMS Meter | 0.47172 | 0.36454 | 0.059 | 0.41272 | 11.673 | 11.673
1297 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903020303 | F03-J.N.KOTE | AGRI | DLMS Meter | 0.46552 | 0.40895 | 0.011 | 0.45452 | 10.0266 | 10.0266
1298 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903020304 | F04-KASAVARATTI | AGRI | DLMS Meter | 0.46684 | 0.41926 | 0 | 0.46684 | 10.1915 | 10.1915
1299 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903010101 | F07-PALLAVAGERE | AGRI | DLMS Meter | 0.52128 | 0.46712 | 0 | 0.52128 | 10.3894 | 10.3894
1300 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903010102 | F08-INDUSTRIAL AREA | URBAN MIXED LOAD | DLMS Meter | 1.1505 | 1.0726 | 0 | 1.1505 | 6.7713 | 24.1386
1301 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903010103 | F09-KOTE | URBAN MIXED LOAD | DLMS Meter | 2.6135 | 2.4181 | 0 | 2.6135 | 7.4756 | 25.6874
1302 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903010104 | F10-ZILLA PANCHAYAT | URBAN MIXED LOAD | DLMS Meter | 2.2616 | 2.0852 | 0 | 2.2616 | 7.8003 | 33.3094
1303 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903010108 | F11-SAJJANAKERE | AGRI | DLMS Meter | 1.2417 | 1.1232 | 0 | 1.2417 | 9.5471 | 22.9558
1304 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903010109 | F12-DANDINAKURUBARAHATTI | AGRI | DLMS Meter | 0.98334 | 0.89434 | 0 | 0.98334 | 9.0509 | 23.4661
1305 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_220 | 1310201903010107 | F13-KENNEDALU | AGRI | DLMS Meter | 1.9378 | 1.7464 | 0 | 1.9378 | 9.8776 | 19.4699
1306 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010101 | F01-NAGARA | URBAN MIXED LOAD | DLMS Meter | 1.3699 | 1.2537 | 0 | 1.3699 | 8.4794 | 24.6589
1307 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010102 | F02-KELAGOTE | URBAN MIXED LOAD | DLMS Meter | 0.75554 | 0.68816 | 0 | 0.75554 | 8.918 | 20.3329
1308 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010103 | F03-BANKCLNY | DOMESTIC | DLMS Meter | 2.1909 | 1.9393 | 0.05 | 2.1409 | 9.4168 | 12.4315
1309 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010104 | F04-GONUR | AGRI | DLMS Meter | 1.066 | 0.95905 | 0 | 1.066 | 10.0343 | 10.0343
1310 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901020301 | F06-GRHALLI | AGRI | DLMS Meter | 1.0567 | 0.91371 | 0 | 1.0567 | 13.5337 | 13.5337
1311 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901020302 | F08-VIDYANAGAR | DOMESTIC | DLMS Meter | 2.6559 | 2.2702 | 0.19655 | 2.4594 | 7.6914 | 15.6834
1312 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901020303 | F09-SEEBARA | AGRI | DLMS Meter | 0.86233 | 0.76867 | 0 | 0.86233 | 10.8623 | 10.8623
1313 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901020304 | F11-CGHALLI | AGRI | DLMS Meter | 0.96934 | 0.87197 | 0 | 0.96934 | 10.0446 | 10.0446
1314 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010501 | F12- JCR | DOMESTIC | DLMS Meter | 1.3162 | 1.2139 | 0 | 1.3162 | 7.7687 | 10.9187
1315 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010503 | F14-PKHALLI | NJY | DLMS Meter | 1.6109 | 1.4357 | 0.065 | 1.5459 | 7.1247 | 11.0192
1316 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010504 | F15-MILLAREA | URBAN MIXED LOAD | DLMS Meter | 3.0844 | 2.9393 | 0 | 3.0844 | 4.7052 | 25.0572
1317 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010108 | F17-KWSSB | WATER WORKS | DLMS Meter | 0.0804 | 0.07526 | 0 | 0.0804 | 6.393 | 38.2912
1318 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010109 | F18-UNIVERSITY | NJY | DLMS Meter | 2.1932 | 2.0245 | 0 | 2.1932 | 7.6927 | 10.7369
1319 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHITRAHALLI_66 | 1310203906010101 | F01-ECHAGHATTA | AGRI | DLMS Meter | 0.8431 | 0.73417 | 0 | 0.8431 | 12.9197 | 12.9197
1320 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHITRAHALLI_66 | 1310203906010102 | F02-T NULENUR | AGRI | DLMS Meter | 0.8208 | 0.70942 | 0 | 0.8208 | 13.5691 | 13.5691
1321 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHITRAHALLI_66 | 1310203906010103 | F03-BG HALLI | AGRI | DLMS Meter | 1.627 | 1.4316 | 0 | 1.627 | 12.0133 | 12.0133
1322 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHITRAHALLI_66 | 1310203906010304 | F04-CHITRAHALLI | AGRI | DLMS Meter | 1.3094 | 1.1439 | 0 | 1.3094 | 12.6412 | 12.6412
1323 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHITRAHALLI_66 | 1310203906020301 | F05-HULIKERE NJY | NJY | DLMS Meter | 1.2873 | 0.3211 | 0.92312 | 0.36419 | 11.8316 | 40.6985
1324 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHITRAHALLI_66 | 1310203906020302 | F06-T-EMMIGANURU NJY | NJY | DLMS Meter | 0.9715 | 0.42087 | 0.49097 | 0.48053 | 12.4154 | 46.465
1325 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHITRAHALLI_66 | 1310203906020303 | F07-MADDERU | AGRI | DLMS Meter | 1.5066 | 1.3563 | 0 | 1.5066 | 9.9748 | 9.9748
1326 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHITRAHALLI_66 | 1310203906020304 | F08-SHIVAGANGA | AGRI | DLMS Meter | 0.80472 | 0.70768 | 0 | 0.80472 | 12.0587 | 12.0587
1327 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | CHITRAHALLI_66 | 1310203906010105 | F09-AMRUTHAPURA NJY | NJY | DLMS Meter | 0.88262 | 0.41785 | 0.40678 | 0.47584 | 12.1882 | 25.6106
1328 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | CHOKKASANDRA_HUSKUR_66 | 1220205901010102 | F02-BASAVESHWARA TEMPLE | URBAN MIXED LOAD | DLMS Meter | 1.3313 | 1.2104 | 0.0102 | 1.3211 | 8.3809 | 15.9624
1329 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | CHOKKASANDRA_HUSKUR_66 | 1220205901010103 | F03-NARAYANAGATA CIRCLE | URBAN MIXED LOAD | DLMS Meter | 2.1131 | 1.89 | 0.0534 | 2.0597 | 8.239 | 18.8872
1330 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | CHOKKASANDRA_HUSKUR_66 | 1220205901010104 | F04-CHOKKASANDRA | URBAN MIXED LOAD | DLMS Meter | 1.5026 | 1.226 | 0.157 | 1.3456 | 8.8891 | 24.8885
1331 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | CHOKKASANDRA_HUSKUR_66 | 1220205901010101 | F06-AVALAHALLY | URBAN MIXED LOAD | DLMS Meter | 0.1765 | 0.16289 | 0 | 0.1765 | 7.7088 | 9.3511
1332 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | CHOKKASANDRA_HUSKUR_66 | 1220205901020101 | F07-GOPSANDRA | URBAN MIXED LOAD | DLMS Meter | 1.0376 | 0.68349 | 0.3048 | 0.7328 | 6.7285 | 22.6786
1333 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | CHOKKASANDRA_HUSKUR_66 | 1220205901020102 | F08-MADURAMMA TEMPLE | URBAN MIXED LOAD | DLMS Meter | 1.8494 | 1.7096 | 0 | 1.8494 | 7.5574 | 31.0868
1334 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | CHOKKASANDRA_HUSKUR_66 | 1220205901020103 | F09-GATAHALLY | URBAN MIXED LOAD | DLMS Meter | 2.4678 | 1.7483 | 0.5791 | 1.8887 | 7.4316 | 11.7516
1335 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903010101 | F01-BACHAREDDYHALLI | AGRI | DLMS Meter | 0.81258 | 0.61428 | 0.13 | 0.68258 | 10.0066 | 10.0066
1336 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903010104 | F02-CHINCHANAHALLI | AGRI | DLMS Meter | 0.97968 | 0.8816 | 0 | 0.97968 | 10.0111 | 10.0111
1337 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903010103 | F03-D.PALYA | AGRI | DLMS Meter | 0.71711 | 0.64542 | 0 | 0.71711 | 9.9972 | 9.9972
1338 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903010102 | F04-LAKKASANDRA | AGRI | DLMS Meter | 0.60126 | 0.54115 | 0 | 0.60126 | 9.997 | 9.997
1339 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903020301 | F05-BYCHAPURA NJY | NJY | DLMS Meter | 1.5909 | 1.3402 | 0.084074 | 1.5068 | 11.0546 | 63.7432
1340 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903020302 | F06-GANGASANDRA | NJY | DLMS Meter | 0.91816 | 0.81751 | 0 | 0.91816 | 10.9626 | 57.3238
1341 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903020303 | F07-HUDUGURU | AGRI | DLMS Meter | 0.98674 | 0.88791 | 0 | 0.98674 | 10.0161 | 10.0161
1342 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903020304 | F08-KADBURU | AGRI | DLMS Meter | 2.0894 | 1.8802 | 0 | 2.0894 | 10.0139 | 10.0139
1343 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903020305 | F09-NAMAGONDLU | AGRI | DLMS Meter | 0.9981 | 0.83502 | 0.07 | 0.9281 | 10.0294 | 10.0294
1344 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903010105 | F10-VENKATAPURA | AGRI | DLMS Meter | 0.71062 | 0.63939 | 0 | 0.71062 | 10.0232 | 10.0232
1345 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | D_PALYA_66 | 1230304903010106 | F11-BALAREDDYHALLI NJY | NJY | DLMS Meter | 0.783 | 0.66797 | 0.033682 | 0.74932 | 10.8567 | 56.1893
1346 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010101 | F02-DEVARAHOSAHALLI-AGRI | AGRI | DLMS Meter | 1.4691 | 1.0009 | 0.325 | 1.1441 | 12.5181 | 12.5181
1347 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010102 | F03-DABBESPET-RURAL-AGRI | AGRI | DLMS Meter | 0.78528 | 0.70681 | 0 | 0.78528 | 9.9921 | 10.3506
1348 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010103 | F04-KAIDB | URBAN MIXED LOAD | DLMS Meter | 2.865 | 2.7001 | 0.055 | 2.81 | 3.9095 | 22.856
1349 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010104 | F05-LM-WIND-POWER | INDUSTRIAL | DLMS Meter | 6.5358 | 6.4978 | 0.015 | 6.5208 | 0.35322 | 0.35633
1350 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902020301 | F07-MANNE | AGRI | DLMS Meter | 1.5438 | 1.3482 | 0 | 1.5438 | 12.6707 | 17.5986
1351 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902020302 | F08-BILANAKOTE | AGRI | DLMS Meter | 1.1619 | 1.0458 | 0 | 1.1619 | 9.9932 | 10.8079
1352 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902020303 | F09-SHIVAGANGE | AGRI | DLMS Meter | 1.268 | 1.1413 | 0 | 1.268 | 9.9946 | 9.9946
1353 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902020305 | F11-EMMVE-SOLOAR | INDUSTRIAL | DLMS Meter | 3.4199 | 3.28 | 0 | 3.4199 | 4.0913 | 4.0913
1354 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902020306 | F12-TDPS | INDUSTRIAL | DLMS Meter | 1.208 | 1.1684 | 0 | 1.208 | 3.2735 | 4.064
1355 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902020307 | F13-S.K-STEELS | INDUSTRIAL | DLMS Meter | 4.247 | 2.0909 | 2.11 | 2.137 | 2.1595 | 4.402
1356 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010105 | F14-BIOGEN | INDUSTRIAL | DLMS Meter | 3.6183 | 3.0546 | 0.467 | 3.1513 | 3.0692 | 10.7267
1357 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010106 | F15-KAMATH | INDUSTRIAL | DLMS Meter | 3.2922 | 3.1567 | 0.045 | 3.2472 | 2.7876 | 3.9476
1358 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010107 | F16-OLD-NIJAGAL-NJY | NJY | DLMS Meter | 0.71656 | 0.33351 | 0.3455 | 0.37106 | 10.1188 | 26.57
1359 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010108 | F17-HEGGUNDA--NJY | NJY | DLMS Meter | 4.39 | 3.9364 | 0.045 | 4.345 | 9.4029 | 18.5432
1360 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010109 | F18-TDPS-UNIT | INDUSTRIAL | DLMS Meter | 2.7648 | 1.56 | 1.191 | 1.5738 | 0.87275 | 0.87275
1361 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010113 | F19-DODDERI-NJY | NJY | DLMS Meter | 2.3886 | 1.1427 | 1.1711 | 1.2175 | 6.1381 | 25.9874
1362 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010112 | F20-BARAGENAHALLI | NJY | DLMS Meter | 1.5994 | 1.3522 | 0.16866 | 1.4308 | 5.4903 | 32.6787
1363 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902010114 | F21-AVERAHALLI INDUSTRIAL AREA | INDUSTRIAL | DLMS Meter | 1.156 | 0.068906 | 1.0867 | 0.069252 | 0.49962 | 4.2387
1364 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | DALSANUR_66 | 1230103903010102 | F01-HOOHALLI | AGRI | DLMS Meter | 1.0866 | 0.97811 | 0 | 1.0866 | 9.9848 | 9.9848
1365 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | DALSANUR_66 | 1230103903010301 | F02-SHETTIHALLI | AGRI | DLMS Meter | 1.2986 | 1.1684 | 0 | 1.2986 | 10.0224 | 10.0224
1366 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | DALSANUR_66 | 1230103903010103 | F03-CHIRUVANAHALLI | AGRI | DLMS Meter | 0.3462 | 0.31144 | 0 | 0.3462 | 10.0407 | 10.0407
1367 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | DALSANUR_66 | 1230103903010104 | F04-KODICHERUVU | AGRI | DLMS Meter | 0.43316 | 0.38996 | 0 | 0.43316 | 9.9728 | 9.9728
1368 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | DALSANUR_66 | 1230103903020301 | F05-HOLLUR | AGRI | DLMS Meter | 0.9136 | 0.81986 | 0 | 0.9136 | 10.2602 | 10.2602
1369 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | DALSANUR_66 | 1230103903010106 | F06-TERNHALLI | NJY | DLMS Meter | 0.78341 | 0.69649 | 0 | 0.78341 | 11.0949 | 76.1232
1370 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | DALSANUR_66 | 1230103903020302 | F07-GATTAHALLI | AGRI | DLMS Meter | 0.88334 | 0.78796 | 0 | 0.88334 | 10.7975 | 10.7975
1371 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | DALSANUR_66 | 1230103903010302 | F08-DALSNUR | AGRI | DLMS Meter | 0.76822 | 0.69111 | 0 | 0.76822 | 10.0371 | 10.0371
1372 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | DALSANUR_66 | 1230103903020303 | F09-NJY-MARENAHALLI | NJY | DLMS Meter | 1.0324 | 0.9188 | 0 | 1.0324 | 11.0035 | 74.4551
1373 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | DALSANUR_66 | 1230103903010101 | F10-GANDLAHALLI NJY | NJY | DLMS Meter | 1.4502 | 1.3465 | 0 | 1.4502 | 7.146 | 76.2201
1374 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | DASHAVARA_66 | 1220106901010101 | F01-MAKALI | AGRI | DLMS Meter | 0.9358 | 0.8419 | 0 | 0.9358 | 10.034 | 10.034
1375 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | DASHAVARA_66 | 1220106901010102 | F02-HOSAHALLI NJY | NJY | DLMS Meter | 0.583 | 0.30386 | 0.2497 | 0.3333 | 8.8341 | 10.4286
1376 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | DASHAVARA_66 | 1220106901010103 | F03-YELEHOSHALLI | AGRI | DLMS Meter | 0.7275 | 0.65467 | 0 | 0.7275 | 10.0113 | 10.0113
1377 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | DASHAVARA_66 | 1220106901010104 | F04-KMF | INDUSTRIAL | DLMS Meter | 2.5472 | 2.5355 | 0 | 2.5472 | 0.45844 | 0.45844
1378 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | DASHAVARA_66 | 1220106901010105 | F06-MI KANVA | LIFT IRRIGATION | DLMS Meter | 0.576 | 0.57318 | 0 | 0.576 | 0.48889 | 43.1665
1379 | CTAZ | TUMKUR | TIPTUR | CN HALLY | DASUDI_66 | 1320203903010101 | F01-GURUVAPURA | AGRI | DLMS Meter | 5.5663 | 0.16776 | 5.3799 | 0.1864 | 10 | 10
1380 | CTAZ | TUMKUR | TIPTUR | CN HALLY | DASUDI_66 | 1320203903010102 | F02-DASUDI | AGRI | DLMS Meter | 2.0112 | 1.7392 | 0 | 2.0112 | 13.5239 | 13.5239
1381 | CTAZ | TUMKUR | TIPTUR | CN HALLY | DASUDI_66 | 1320203903010103 | F03-THAMMANANA GUDDE | AGRI | DLMS Meter | 1.044 | 0.91595 | 0 | 1.044 | 12.2639 | 12.2639
1382 | CTAZ | TUMKUR | TIPTUR | CN HALLY | DASUDI_66 | 1320203903010104 | F04-BORANAKANIVE | AGRI | DLMS Meter | 1.1885 | 1.0699 | 0 | 1.1885 | 9.9797 | 9.9797
1383 | CTAZ | TUMKUR | TIPTUR | CN HALLY | DASUDI_66 | 1320203903010105 | F05-DABBAGUNTE-NJY | NJY | DLMS Meter | 0.76233 | 0.66213 | 0 | 0.76233 | 13.1442 | 61.4346
1384 | CTAZ | TUMKUR | TIPTUR | CN HALLY | DASUDI_66 | 1320203903010106 | F06-YAGACHIHALLI-NJY | NJY | DLMS Meter | 0.33471 | 0.28859 | 0 | 0.33471 | 13.7803 | 56.3796
1385 | CTAZ | TUMKUR | TIPTUR | CN HALLY | DASUDI_66 | 1320203903020301 | F07-KALLENAHALLI | AGRI | DLMS Meter | 0.83874 | 0.74186 | 0 | 0.83874 | 11.5501 | 11.5501
1386 | CTAZ | TUMKUR | TIPTUR | CN HALLY | DASUDI_66 | 1320203903020302 | F08-MELANAHALLI | AGRI | DLMS Meter | 1.265 | 1.1381 | 0 | 1.265 | 10.0375 | 10.0375
1387 | CTAZ | TUMKUR | TIPTUR | CN HALLY | DASUDI_66 | 1320203903020303 | F09-HONNAYYANAPALLYA | AGRI | DLMS Meter | 1.098 | 0.98822 | 0 | 1.098 | 10.0002 | 10.0002
1388 | CTAZ | TUMKUR | TIPTUR | CN HALLY | DASUDI_66 | 1320203903020304 | F10-MARENADU | AGRI | DLMS Meter | 1.0754 | 0.96737 | 0 | 1.0754 | 10.0476 | 10.0476
1389 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901010101 | F01-SVT | URBAN MIXED LOAD | DLMS Meter | 2.8038 | 2.6486 | 0 | 2.8038 | 5.5355 | 12.3181
1390 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901010102 | F02-MCCB | URBAN MIXED LOAD | DLMS Meter | 3.7454 | 3.4146 | 0.035 | 3.7104 | 7.9703 | 16.1552
1391 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | DAVANAGERE_66 | 1310101901010104 | F04-BT | URBAN MIXED LOAD | DLMS Meter | 1.5038 | 1.339 | 0.021594 | 1.4822 | 9.6629 | 9.6629
1392 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901010301 | F05-MOUNESHWARA | URBAN MIXED LOAD | DLMS Meter | 1.8226 | 1.6484 | 0.025 | 1.7976 | 8.3016 | 17.159
1393 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901010302 | F06-DCM | URBAN MIXED LOAD | DLMS Meter | 2.2909 | 2.0583 | 0.0117 | 2.2792 | 9.6949 | 19.3259
1394 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901010303 | F07-G&S | DOMESTIC | DLMS Meter | 1.8277 | 1.2212 | 0.50564 | 1.3221 | 7.6281 | 15.3457
1395 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901010304 | F08-KTJ | URBAN MIXED LOAD | DLMS Meter | 2.9916 | 2.7341 | 0 | 2.9916 | 8.6084 | 17.9199
1396 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901020501 | F09-PJ | URBAN MIXED LOAD | DLMS Meter | 1.5398 | 1.4608 | 0 | 1.5398 | 5.1307 | 14.931
1397 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901020502 | F10-CGH | URBAN MIXED LOAD | DLMS Meter | 2.7623 | 2.6312 | 0 | 2.7623 | 4.7441 | 15.2361
1398 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | DAVANAGERE_66 | 1310101901020503 | F11-LF1 | URBAN MIXED LOAD | DLMS Meter | 3.481 | 1.6442 | 1.7616 | 1.7194 | 4.3731 | 7.0893
1399 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901020504 | F12-BASAVESHWARA | URBAN MIXED LOAD | DLMS Meter | 2.7312 | 2.5398 | 0 | 2.7312 | 7.008 | 19.7244
1400 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901030701 | F13-TRISHUL | URBAN MIXED LOAD | DLMS Meter | 0.99992 | 0.90683 | 0 | 0.99992 | 9.3095 | 9.3095
1401 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901030702 | F14-JAYANAGARA | URBAN MIXED LOAD | DLMS Meter | 1.7043 | 1.4835 | 0.0971 | 1.6072 | 7.6988 | 16.3726
1402 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901030703 | F15-SWIMMINGPOOL | URBAN MIXED LOAD | DLMS Meter | 1.4942 | 1.4397 | 0 | 1.4942 | 3.6453 | 3.9022
1403 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901030704 | F16-NIJALINGAPPA | URBAN MIXED LOAD | DLMS Meter | 2.4813 | 2.314 | 0 | 2.4813 | 6.7408 | 16.0856
1404 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901030705 | F17-MAHANAGARAPALIKE | URBAN MIXED LOAD | DLMS Meter | 1.867 | 1.7469 | 0.015 | 1.852 | 5.6776 | 11.1394
1405 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | DAVANAGERE_66 | 1310101901030706 | F18-DURGAMBIKA | URBAN MIXED LOAD | DLMS Meter | 1.7507 | 1.6072 | 0 | 1.7507 | 8.2002 | 15.1093
1406 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901030707 | F19-E S I | HOSPITAL | DLMS Meter | 0.0971 | 0.09345 | 0 | 0.0971 | 3.759 | 3.759
1407 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902010101 | F01-HADADISRS | AGRI | DLMS Meter | 0.79606 | 0.71615 | 0 | 0.79606 | 10.0378 | 10.0378
1408 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902010102 | F02-THOLHUNSESRS | AGRI | DLMS Meter | 0.02442 | 0.022002 | 0 | 0.02442 | 9.9017 | 9.9017
1409 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902010103 | F03-KUKKAWADASRS | AGRI | DLMS Meter | 1.1041 | 0.98303 | 0 | 1.1041 | 10.9624 | 10.9624
1410 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902010104 | F04-YELLAMMA | AGRI | DLMS Meter | 0.49664 | 0.39938 | 0.05 | 0.44664 | 10.5803 | 10.5803
1411 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902010105 | F05-BELAVANUR | URBAN MIXED LOAD | DLMS Meter | 2.1689 | 1.6419 | 0.3085 | 1.8604 | 11.7419 | 19.1114
1412 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902010503 | F07-JARIKATTE | AGRI | DLMS Meter | 0.13418 | 0.12061 | 0 | 0.13418 | 10.1155 | 10.1155
1413 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902010504 | F08-TURUCHUGHATTA | AGRI | DLMS Meter | 1.2278 | 1.1049 | 0 | 1.2278 | 10.0089 | 10.0089
1414 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020301 | F09-SHAMNUR | URBAN MIXED LOAD | DLMS Meter | 1.5585 | 1.2728 | 0.125 | 1.4335 | 11.2135 | 15.0077
1415 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020302 | F10-SARASWATHI | URBAN MIXED LOAD | DLMS Meter | 1.6234 | 1.4938 | 0 | 1.6234 | 7.9845 | 12.8022
1416 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020303 | F11-WATERWORKS+AUX | WATER WORKS | DLMS Meter | 0.63689 | 0.60592 | 0 | 0.63689 | 4.8626 | 22.4569
1417 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020304 | F12-ATTIGERESRS | DOMESTIC | DLMS Meter | 1.0411 | 0.13694 | 0.89 | 0.15112 | 9.3826 | 42.9055
1418 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020305 | F13-INDUSTRIALSRS | INDUSTRIAL | DLMS Meter | 2.2847 | 2.131 | 0 | 2.2847 | 6.7302 | 8.2607
1419 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020306 | F14-VIDYANAGAR | URBAN MIXED LOAD | DLMS Meter | 1.6314 | 1.5141 | 0.011 | 1.6204 | 6.5611 | 13.0133
1420 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020307 | F15-RANGANATHA | URBAN MIXED LOAD | DLMS Meter | 2.3607 | 2.2662 | 0 | 2.3607 | 4.0028 | 14.1454
1421 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902010501 | F16-JHP2 | DOMESTIC | DLMS Meter | 0.75892 | 0.343 | 0.379 | 0.37992 | 9.7189 | 47.087
1422 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020101 | F17-JHP1 | URBAN MIXED LOAD | DLMS Meter | 2.0952 | 1.4757 | 0.45654 | 1.6387 | 9.945 | 18.587
1423 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020701 | F21-NJ TARALABALU | NJY | DLMS Meter | 1.393 | 1.0902 | 0.145 | 1.248 | 12.6404 | 32.1943
1424 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020702 | F22-S S HIGHTECH | DOMESTIC | DLMS Meter | 2.4082 | 2.225 | 0 | 2.4082 | 7.6057 | 13.1975
1425 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANGERE_SRS_220 | 1310101902020703 | F23-VIVEKANANDA | DOMESTIC | DLMS Meter | 2.3343 | 2.1763 | 0.008 | 2.3263 | 6.4499 | 9.5326
1426 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906010101 | F01-LOCAL | DOMESTIC | DLMS Meter | 3.5765 | 3.2918 | 0 | 3.5765 | 7.9597 | 12.8691
1427 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020101 | F02-RAGHUNATHAPURA | AGRI | DLMS Meter | 0.8339 | 0.75053 | 0 | 0.8339 | 9.9977 | 9.9977
1428 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020102 | F03-THALAGAWARA | AGRI | DLMS Meter | 1.0149 | 0.91348 | 0 | 1.0149 | 9.9967 | 9.9967
1429 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906010301 | F04-HANABE | AGRI | DLMS Meter | 1.8133 | 1.6316 | 0 | 1.8133 | 10.0199 | 10.6116
1430 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906010302 | F05-ANTHARAHALLI | AGRI | DLMS Meter | 1.1886 | 1.071 | 0 | 1.1886 | 9.8901 | 9.9928
1431 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020103 | F06-TELEPHONE-EXCHANGE | DOMESTIC | DLMS Meter | 3.5074 | 3.0423 | 0 | 3.5074 | 13.2616 | 21.872
1432 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020104 | F07-LOCAL | URBAN MIXED LOAD | DLMS Meter | 4.3861 | 3.8917 | 0 | 4.3861 | 11.2715 | 28.4291
1433 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906010303 | F08-SS-GHATTI | AGRI | DLMS Meter | 1.1357 | 1.022 | 0 | 1.1357 | 10.0115 | 10.0115
1434 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906010304 | F09-RAJAGHATTA | AGRI | DLMS Meter | 1.4585 | 1.3118 | 0 | 1.4585 | 10.0552 | 10.0552
1435 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906010102 | F10-VASAVI | DOMESTIC | DLMS Meter | 2.5164 | 2.2114 | 0 | 2.5164 | 12.1226 | 23.782
1436 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020105 | F12-HEGGADIHALLI | AGRI | DLMS Meter | 1.1285 | 1.0154 | 0 | 1.1285 | 10.0277 | 10.0277
1437 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020106 | F13-MELEKOTE | AGRI | DLMS Meter | 0.57606 | 0.51842 | 0 | 0.57606 | 10.0061 | 10.0061
1438 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020107 | F14-SCOUT-CAMP | URBAN MIXED LOAD | DLMS Meter | 1.4193 | 1.1864 | 0.085 | 1.3343 | 11.0809 | 31.8333
1439 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020108 | F15-TROPICAL-FLAVOURS | URBAN MIXED LOAD | DLMS Meter | 2.1252 | 0.85765 | 1.1613 | 0.96389 | 11.0217 | 29.1511
1440 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906010104 | F16-KANTANAKUNTE | NJY | DLMS Meter | 1.2755 | 0.92579 | 0.231 | 1.0445 | 11.3664 | 41.3404
1441 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906010305 | F17-NANDHI-MORI | NJY | DLMS Meter | 0.89612 | 0.78816 | 0 | 0.89612 | 12.0479 | 53.9451
1442 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020109 | F18-BEEDIKERE | NJY | DLMS Meter | 0.68028 | 0.59231 | 0 | 0.68028 | 12.9308 | 51.0373
1443 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020301 | F20-THIPPURU | AGRI | DLMS Meter | 1.2052 | 1.0847 | 0 | 1.2052 | 9.9978 | 9.9978
1444 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906010110 | F21-KVN INFOCITY | URBAN MIXED LOAD | DLMS Meter | 1.3448 | 0.56658 | 0.69916 | 0.64568 | 12.2495 | 12.2495
1445 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DCROSS_66 | 1210101906020304 | F22-NERALEGHATTA | NJY | DLMS Meter | 1.2575 | 0.7776 | 0.371 | 0.88655 | 12.2895 | 48.2115
1446 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020302 | F23-HADONAHALLI | NJY | DLMS Meter | 0.6313 | 0.45227 | 0.117 | 0.5143 | 12.0602 | 34.0947
1447 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | DCROSS_66 | 1210101906020303 | F24-PLANT LIPIDS | INDUSTRIAL | DLMS Meter | 0.9306 | 0.9137 | 0 | 0.9306 | 1.8166 | 1.8166
1448 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010101 | F01-LOCAL DEVANAHALLI | DOMESTIC | DLMS Meter | 4.1263 | 3.5462 | 0.21814 | 3.9082 | 9.2607 | 10.316
1449 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020101 | F02-BHUVANAHALLI | DOMESTIC | DLMS Meter | 1.3832 | 1.2432 | 0 | 1.3832 | 10.1208 | 17.3977
1450 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020301 | F03-VISHWANATHPURA | AGRI | DLMS Meter | 1.1728 | 1.0602 | 0 | 1.1728 | 9.6033 | 11.4336
1451 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020302 | F04-AVATHI | AGRI | DLMS Meter | 1.8756 | 1.6885 | 0 | 1.8756 | 9.9775 | 9.9775
1452 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010103 | F05-YELIYUR | AGRI | DLMS Meter | 1.1192 | 1.0077 | 0 | 1.1192 | 9.9639 | 10.2068
1453 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010112 | F06-OLD TOWN | DOMESTIC | DLMS Meter | 2.4807 | 2.273 | 0 | 2.4807 | 8.3709 | 15.6559
1454 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010104 | F07-GANGAVARA | AGRI | DLMS Meter | 1.2389 | 1.1148 | 0 | 1.2389 | 10.0158 | 10.1386
1455 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020303 | F08-KARAHALLI | AGRI | DLMS Meter | 1.6976 | 1.5282 | 0 | 1.6976 | 9.9774 | 10.7609
1456 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010105 | F10-SADAHALLI | DOMESTIC | DLMS Meter | 3.144 | 2.0804 | 0.77403 | 2.37 | 12.2169 | 20.4458
1457 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010106 | F11-THARABANAHALLI | DOMESTIC | DLMS Meter | 5.896 | 4.3218 | 0.8461 | 5.0499 | 14.4177 | 20.765
1458 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020309 | F12-KOIRA | NJY | DLMS Meter | 1.3133 | 1.1191 | 0.09108 | 1.2223 | 8.4393 | 43.942
1459 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010107 | F13-KANNAMANGALA | AGRI | DLMS Meter | 0.3736 | 0.33415 | 0 | 0.3736 | 10.5596 | 10.5596
1460 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020304 | F14-GOVT HOSPITAL | HOSPITAL | DLMS Meter | 0.2686 | 0.20965 | 0.032881 | 0.23572 | 11.0574 | 37.5272
1461 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010108 | F15-CHANNARAYAPATNA | AGRI | DLMS Meter | 0.8116 | 0.73109 | 0 | 0.8116 | 9.9202 | 10.2619
1462 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020305 | F16-KORAMANGALA | AGRI | DLMS Meter | 1.99 | 1.7915 | 0 | 1.99 | 9.9748 | 9.9748
1463 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020308 | F17-RENASISSANCE | DOMESTIC | DLMS Meter | 2.469 | 1.8223 | 0.44411 | 2.0249 | 10.0028 | 26.1841
1464 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010109 | F18-ISRO | DOMESTIC | DLMS Meter | 0.053836 | 0.053836 | 0 | 0.053836 | 0 | 0.3658
1465 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020306 | F19-KUNDANNA | AGRI | DLMS Meter | 0.3 | 0.27011 | 0 | 0.3 | 9.9637 | 10.1244
1466 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010110 | F20-SOBHA | DOMESTIC | DLMS Meter | 0.34611 | 0.30319 | 0 | 0.34611 | 12.4003 | 38.9142
1467 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010111 | F21-NJY-CHEEMACHANAHALLI | NJY | DLMS Meter | 1.281 | 0.99605 | 0.20212 | 1.0789 | 7.6752 | 45.9502
1468 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020307 | F22-NJY-BOMMAWARA | NJY | DLMS Meter | 2.1182 | 1.7367 | 0.20712 | 1.9111 | 9.1253 | 36.3548
1469 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020310 | F23-BIDALURU | AGRI | DLMS Meter | 1.2484 | 1.1151 | 0 | 1.2484 | 10.6788 | 10.6788
1470 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010102 | F24-HOSAHUDYA | AGRI | DLMS Meter | 0.52308 | 0.47051 | 0 | 0.52308 | 10.0505 | 10.0505
1471 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903020311 | F25- INDUSTRIAL | INDUSTRIAL | DLMS Meter | 2.26 | 1.9114 | 0.053997 | 2.206 | 13.3552 | 14.2619
1472 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903030501 | F26-GOBBARAGUNTE NJY | NJY | DLMS Meter | 0.7042 | 0.6316 | 0.009637 | 0.69456 | 9.0654 | 50.7697
1473 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903030506 | F27-SAIBABA NJY | NJY | DLMS Meter | 1.6435 | 1.4323 | 0.063397 | 1.5801 | 9.3512 | 49.2766
1474 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903030507 | F28-THYLAGERE NJY | NJY | DLMS Meter | 2.037 | 1.8281 | 0 | 2.037 | 10.2566 | 34.3769
1475 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903030503 | F29 -VILLA HIRANANDANI | DOMESTIC | DLMS Meter | 0.22616 | 0.20024 | 0 | 0.22616 | 11.4619 | 12.2709
1476 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903010113 | F30-PRESTIGE GOLFSHIRE | DOMESTIC | DLMS Meter | 4.6964 | 4.5294 | 0 | 4.6964 | 3.5566 | 3.5566
1477 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903030502 | F31- NITESH ESTATE | DOMESTIC | DLMS Meter | 0.000111 | 0.000104 | 0 | 0.000111 | 6.3063 | 68.171
1478 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903030504 | F32-AJMAL LAYOUT | DOMESTIC | DLMS Meter | 0.010705 | 0.00954 | 0 | 0.010705 | 10.8828 | 89.6029
1479 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903030505 | F33-APARTMENT LAKEPOINT | DOMESTIC | DLMS Meter | 0.506 | 0.32887 | 0.13616 | 0.36984 | 11.0782 | 11.0782
1480 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | DEVANAHALLI_66 | 1210202903030601 | F36- BRIGADE ATMOSPHERE | DOMESTIC | DLMS Meter | 0.096398 | 0.088543 | 0 | 0.096398 | 8.148 | 8.148
1481 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | DEVANGUNDI_66 | 1210201903010101 | F01-K.AGRAHARA | AGRI | DLMS Meter | 2.0441 | 1.8396 | 0 | 2.0441 | 10.0037 | 10.4342
1482 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | DEVANGUNDI_66 | 1210201903010102 | F02-SHIVANAPURA | NJY | DLMS Meter | 3.3592 | 2.0431 | 1.0514 | 2.3079 | 11.4718 | 25.4604
1483 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | DEVANGUNDI_66 | 1210201903010104 | F03-K AREHALLI NJY | RURAL MIXED LOAD | DLMS Meter | 4.4633 | 3.9694 | 0 | 4.4633 | 11.0662 | 14.4539
1484 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | DEVANGUNDI_66 | 1210201903010301 | F06-NARAYANAKERE | RURAL MIXED LOAD | DLMS Meter | 3.4537 | 3.1081 | 0 | 3.4537 | 10.0062 | 10.0062
1485 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | DEVANGUNDI_66 | 1210201903010108 | F07-ITC | INDUSTRIAL | DLMS Meter | 2.7216 | 2.1744 | 0.42087 | 2.3008 | 5.4924 | 5.8546
1486 | BMASZ | SOUTH | KORAMANGALA | S7 | DEVARABISANAHALLI_66 | 1110203907010101 | F02-RMZ | COMMERCIAL | DLMS Meter | 1.3674 | 1.361 | 0 | 1.3674 | 0.47004 | 3.6001
1487 | BMASZ | SOUTH | HSR | S11 | DEVARABISANAHALLI_66 | 1110203907010102 | F03-BELANDUR | URBAN MIXED LOAD | DLMS Meter | 3.9953 | 3.7814 | 0 | 3.9953 | 5.3541 | 5.3541
1488 | BMASZ | SOUTH | KORAMANGALA | S17 | DEVARABISANAHALLI_66 | 1110203907010103 | F04-K-AGRAHARA | URBAN MIXED LOAD | DLMS Meter | 3.6764 | 3.5186 | 0 | 3.6764 | 4.2918 | 4.2918
1489 | BMASZ | SOUTH | KORAMANGALA | S7 | DEVARABISANAHALLI_66 | 1110203907010104 | F05-RMZ | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1490 | BMASZ | SOUTH | HSR | S11 | DEVARABISANAHALLI_66 | 1110203907010105 | F06-KAIKONDANAHALLI | URBAN MIXED LOAD | DLMS Meter | 7.1454 | 6.7384 | 0 | 7.1454 | 5.6963 | 12.7563
1491 | BMASZ | SOUTH | HSR | S11 | DEVARABISANAHALLI_66 | 1110203907010106 | F07-GREEN-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.672 | 1.5847 | 0 | 1.672 | 5.2192 | 5.2192
1492 | BMASZ | SOUTH | KORAMANGALA | S7 | DEVARABISANAHALLI_66 | 1110203907010301 | F08-DEVARABISANAHALLI | URBAN MIXED LOAD | DLMS Meter | 0.26051 | 0.24154 | 0.003 | 0.25751 | 6.199 | 8.3822
1493 | BMASZ | SOUTH | KORAMANGALA | S7 | DEVARABISANAHALLI_66 | 1110203907010302 | F09-RMZ | COMMERCIAL | DLMS Meter | 2.1011 | 1.9813 | 0.07 | 2.0311 | 2.4526 | 19.2711
1494 | BMASZ | SOUTH | KORAMANGALA | S17 | DEVARABISANAHALLI_66 | 1110203907010107 | F10-SALAPURIA | COMMERCIAL | DLMS Meter | 1.1135 | 0.60945 | 0.45979 | 0.65367 | 6.765 | 6.765
1495 | BMASZ | SOUTH | KORAMANGALA | S7 | DEVARABISANAHALLI_66 | 1110203907010303 | F11-RMZ | COMMERCIAL | DLMS Meter | 0.95321 | 0.9466 | 0 | 0.95321 | 0.69368 | 4.4815
1496 | BMASZ | SOUTH | HSR | S11 | DEVARABISANAHALLI_66 | 1110203907010304 | F12-BELANDOOR-GATE | URBAN MIXED LOAD | DLMS Meter | 6.856 | 6.4453 | 0 | 6.856 | 5.99 | 10.7676
1497 | BMASZ | SOUTH | HSR | S11 | DEVARABISANAHALLI_66 | 1110203907010305 | F13-ANUPAMA-FLOORING-AREA | COMMERCIAL | DLMS Meter | 3.8146 | 2.4567 | 1.19 | 2.6246 | 6.3952 | 10.332
1498 | BMASZ | SOUTH | KORAMANGALA | S7 | DEVARABISANAHALLI_66 | 1110203907010306 | F14-RMZ-&-ECOSPACE | COMMERCIAL | DLMS Meter | 1.9502 | 1.9373 | 0 | 1.9502 | 0.66429 | 3.5172
1499 | BMASZ | SOUTH | HSR | S11 | DEVARABISANAHALLI_66 | 1110203907010307 | F15-TOTAL-MALL | COMMERCIAL | DLMS Meter | 3.8952 | 3.6395 | 0.062 | 3.8332 | 5.0515 | 5.0515
1500 | BMASZ | SOUTH | KORAMANGALA | S17 | DEVARABISANAHALLI_66 | 1110203907010308 | F16-SHOBA-IRIS | COMMERCIAL | DLMS Meter | 0.90762 | 0.83536 | 0.025132 | 0.88249 | 5.3401 | 5.3401
1501 | BMASZ | SOUTH | HSR | S11 | DEVARABISANAHALLI_66 | 1110203907010108 | F18-WIPRO | COMMERCIAL | DLMS Meter | 3.6754 | 0.5173 | 3.136 | 0.53939 | 4.0951 | 4.0951
1502 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903010101 | F01-GANGURU | AGRI | DLMS Meter | 1.4797 | 1.3315 | 0 | 1.4797 | 10.0153 | 10.0153
1503 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903010102 | F02-UDUGIRI | NJY | DLMS Meter | 1.0133 | 0.23475 | 0.749 | 0.26426 | 11.1685 | 29.3114
1504 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903010103 | F03-DEVARAHALLI | AGRI | DLMS Meter | 0.90778 | 0.81705 | 0 | 0.90778 | 9.995 | 9.995
1505 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903010104 | F04-GULLAHALLI | AGRI | DLMS Meter | 0.94578 | 0.79256 | 0.065 | 0.88078 | 10.0163 | 10.0163
1506 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903010105 | F05-NAVODAYA | NJY | DLMS Meter | 0.04481 | 0.044444 | 0 | 0.04481 | 0.81678 | 0.81678
1507 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903020301 | F06-YARAGATTAHALLI | AGRI | DLMS Meter | 1.0902 | 0.98098 | 0 | 1.0902 | 10.0183 | 10.0183
1508 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903020302 | F07-NUGGIHALI | AGRI | DLMS Meter | 1.1124 | 1.0009 | 0 | 1.1124 | 10.026 | 10.026
1509 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903021501 | F08-NEETHIGERE | AGRI | DLMS Meter | 0.79168 | 0.60796 | 0.116 | 0.67568 | 10.0219 | 10.0219
1510 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903021502 | F09-K.MATTI | AGRI | DLMS Meter | 0.807 | 0.72621 | 0 | 0.807 | 10.0115 | 10.0115
1511 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903021503 | F10-NEETIGERE NJY | NJY | DLMS Meter | 0.45735 | 0.4059 | 0 | 0.45735 | 11.2492 | 34.8754
1512 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | DEVARAHALLI_66 | 1310107903021504 | F11-YARAGATTIHALLI NJY | NJY | DLMS Meter | 0.4055 | 0.1272 | 0.263 | 0.1425 | 10.7354 | 23.5431
1513 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | DEVARBELAKERE_66 | 1310301909010201 | F01-MYLARALINGESHWARA | NJY | DLMS Meter | 0.5384 | 0.45743 | 0.0355 | 0.5029 | 9.0416 | 33.792
1514 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | DEVARBELAKERE_66 | 1310301909010202 | F02-KADLEGONDI | AGRI | DLMS Meter | 1.1194 | 0.6475 | 0.4 | 0.7194 | 9.9942 | 9.9942
1515 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | DEVARBELAKERE_66 | 1310301909010203 | F03-KARIYAMMA | NJY | DLMS Meter | 0.1628 | 0.12118 | 0.0317 | 0.1311 | 7.5675 | 34.0296
1516 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | DEVARBELAKERE_66 | 1310301909010204 | F04-SALAKATTE | AGRI | DLMS Meter | 0.876 | 0.78863 | 0 | 0.876 | 9.9739 | 9.9739
1517 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | DEVARBELAKERE_66 | 1310301909020201 | F05-MITLAKATTE INDUSTRIAL | INDUSTRIAL | DLMS Meter | 0.665 | 0.60312 | 0.0042 | 0.6608 | 8.7283 | 12.506
1518 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | DEVARBELAKERE_66 | 1310301909020202 | F07-SHIVAJI | AGRI | DLMS Meter | 0.461 | 0.41428 | 0 | 0.461 | 10.1351 | 10.1351
1519 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | DEVARBELAKERE_66 | 1310301909020203 | F08-MUDAHADADI | AGRI | DLMS Meter | 1.1608 | 0.67122 | 0.415 | 0.7458 | 10.0004 | 10.0004
1520 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906010101 | F01-E-THIMMASANDRA | AGRI | DLMS Meter | 0.89264 | 0.75825 | 0.05 | 0.84264 | 10.0155 | 10.0155
1521 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906010102 | F02-KORALPARTHI | AGRI | DLMS Meter | 1.0299 | 0.9268 | 0 | 1.0299 | 10.0145 | 10.0145
1522 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906010103 | F03-ANEMADUGU | AGRI | DLMS Meter | 1.0455 | 0.9408 | 0 | 1.0455 | 10.0152 | 10.0152
1523 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906010104 | F04-BASHETTAHALLI | AGRI | DLMS Meter | 1.3655 | 1.2287 | 0 | 1.3655 | 10.0216 | 10.0216
1524 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906010105 | F05-DODDATEKHALLI | AGRI | DLMS Meter | 1.5277 | 1.3118 | 0.07 | 1.4577 | 10.0098 | 10.0098
1525 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906020302 | F06-DIBBURAHALLI | AGRI | DLMS Meter | 1.593 | 1.4338 | 0 | 1.593 | 9.9926 | 9.9926
1526 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906020303 | F07-DYAVAPPANAGUDI | AGRI | DLMS Meter | 1.2688 | 0.82889 | 0.3479 | 0.92086 | 9.9872 | 9.9872
1527 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906020304 | F08-SADALI | AGRI | DLMS Meter | 0.59608 | 0.44638 | 0.1 | 0.49608 | 10.0195 | 10.0195
1528 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906020305 | F09-DYAVARAHALLI | NJY | DLMS Meter | 0.91199 | 0.80229 | 0 | 0.91199 | 12.0278 | 75.1608
1529 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906010109 | F11-RAYAPPANAHALLI | NJY | DLMS Meter | 0.60418 | 0.5285 | 0 | 0.60418 | 12.5266 | 67.5586
1530 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906010106 | F12-BYRAGANAHALLI | NJY | DLMS Meter | 0.63436 | 0.54656 | 0.009 | 0.62536 | 12.6018 | 73.3507
1531 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906010110 | F13-NJY-THALAKAYALABETTA | NJY | DLMS Meter | 1.0028 | 0.87815 | 0 | 1.0028 | 12.4295 | 64.3446
1532 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | DIBBURAHALLI_66 | 1230404906010111 | F14-BAYYAPPANAHALLI | NJY | DLMS Meter | 0.058312 | 0.050984 | 0 | 0.058312 | 12.5669 | 45.1337
1533 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903020101 | F01-MRS-TECHPARK | COMMERCIAL | DLMS Meter | 0.74871 | 0.75075 | 0 | 0.74871 | -0.2728 | -0.2728
1534 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903020102 | F02-HUAWEI | COMMERCIAL | DLMS Meter | 2.9454 | 2.9491 | 0 | 2.9454 | -0.12591 | 2.8699
1535 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903020103 | F03-CHILLER-PLANT | COMMERCIAL | DLMS Meter | 1.0847 | 1.0913 | 0 | 1.0847 | -0.6069 | -0.6069
1536 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903010101 | F04-THUBARAHALLI | URBAN MIXED LOAD | DLMS Meter | 4.6443 | 4.1119 | 0.28 | 4.3643 | 5.7836 | 16.4953
1537 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903020104 | F05-AECS-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.5386 | 2.1966 | 1.216 | 2.3226 | 5.4264 | 10.8042
1538 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903020105 | F06-BEML-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 6.5505 | 6.3116 | 0 | 6.5505 | 3.6475 | 3.6475
1539 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903020301 | F07-HUAWEI-2 | COMMERCIAL | DLMS Meter | 1.2093 | 1.2094 | 0 | 1.2093 | -0.0093019 | 2.3007
1540 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903020303 | F09-GREEN-GARDEN-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.106 | 3.8752 | 0.03 | 4.076 | 4.9246 | 13.8769
1541 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903020304 | F10-SIDDAPURA | URBAN MIXED LOAD | DLMS Meter | 7.306 | 6.8031 | 0.18169 | 7.1243 | 4.5079 | 10.0194
1542 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903020305 | F11-KALYANI | COMMERCIAL | DLMS Meter | 4.8702 | 4.5758 | 0 | 4.8702 | 6.0433 | 6.0433
1543 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903010108 | F13-C1 BUILDING | COMMERCIAL | DLMS Meter | 0.33125 | 0.33291 | 0 | 0.33125 | -0.49897 | 1.9599
1544 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903010107 | F14-ROW PHASE-1 | DOMESTIC | DLMS Meter | 0.92902 | 0.88796 | 0.03 | 0.89902 | 1.2301 | 2.8679
1545 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903010106 | F15-ROW PHASE-2 | IDLE | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1546 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903010115 | F16-KUNDALAHALLI VILLAGE | URBAN MIXED LOAD | DLMS Meter | 4.8549 | 3.8765 | 0.70398 | 4.1509 | 6.6111 | 6.6111
1547 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903010104 | F17-A5 BLOCK | DOMESTIC | DLMS Meter | 0.89732 | 0.90053 | 0 | 0.89732 | -0.35737 | -0.35737
1548 | BMASZ | SOUTH | KORAMANGALA | S7 | DIVYASREE_66 | 1110203903010103 | F18-A4 BLOCK | COMMERCIAL | DLMS Meter | 0.3878 | 0.38985 | 0 | 0.3878 | -0.52754 | -0.52754
1549 | BMASZ | SOUTH | HSR | S10 | DLF_66 | 1110302903020101 | F01-CLUB HOUSE | URBAN MIXED LOAD | DLMS Meter | 0.54701 | 0.42741 | 0.095441 | 0.45157 | 5.3486 | 6.2605
1550 | BMASZ | SOUTH | HSR | S10 | DLF_66 | 1110302903020102 | F02-D BLOCK TC SUB STN 01 | URBAN MIXED LOAD | DLMS Meter | 0.19294 | 0.18636 | 0 | 0.19294 | 3.4135 | 4.1566
1551 | BMASZ | SOUTH | HSR | S10 | DLF_66 | 1110302903010101 | F07-B BLOCK SUB STN 07 | URBAN MIXED LOAD | DLMS Meter | 0.66154 | 0.64189 | 0 | 0.66154 | 2.9697 | 3.6752
1552 | BMASZ | SOUTH | HSR | S10 | DLF_66 | 1110302903010103 | F10-NAGALINGESHWARA TEMPLE | URBAN MIXED LOAD | DLMS Meter | 0.69445 | 0.67641 | 0 | 0.69445 | 2.5979 | 6.5263
1553 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | DODDA SARANGI_66 | 1320104904010101 | F01-NANDIHALLI | AGRI | DLMS Meter | 0.9686 | 0.87166 | 0 | 0.9686 | 10.0086 | 10.0086
1554 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | DODDA SARANGI_66 | 1320104904010102 | F02-DODDASARANGI-IP | AGRI | DLMS Meter | 1.0561 | 0.95047 | 0 | 1.0561 | 9.9998 | 9.9998
1555 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | DODDA SARANGI_66 | 1320104904010103 | F03-HOSAHALLI--NJY | NJY | DLMS Meter | 0.44538 | 0.38553 | 0 | 0.44538 | 13.4369 | 48.678
1556 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | DODDA SARANGI_66 | 1320104904010104 | F04-ADLAPURA | AGRI | DLMS Meter | 1.0069 | 0.90168 | 0 | 1.0069 | 10.446 | 10.446
1557 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | DODDA SARANGI_66 | 1320104904010106 | F05-KHB-01 | URBAN MIXED LOAD | DLMS Meter | 0.85278 | 0.75083 | 0 | 0.85278 | 11.9554 | 11.9554
1558 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | DODDA SARANGI_66 | 1320104904010107 | F06-KHB-02 | URBAN MIXED LOAD | DLMS Meter | 1.2565 | 0 | 1.2565 | 0 | 0 | #DIV/0!
1559 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | DODDA SARANGI_66 | 1320104904020301 | F07-CHIKKASARANGI NJY | NJY | DLMS Meter | 0.8874 | 0.72274 | 0.053 | 0.8344 | 13.3826 | 47.5554
1560 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | DODDA SARANGI_66 | 1320104904020302 | F08-HETTENAHALLI IP | AGRI | DLMS Meter | 0.7624 | 0.66826 | 0 | 0.7624 | 12.3476 | 12.3476
1561 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903010101 | F01-HADRIPURA | AGRI | DLMS Meter | 1.4623 | 1.3162 | 0 | 1.4623 | 9.9926 | 14.3602
1562 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903010102 | F02-DODDABELVANGALA | AGRI | DLMS Meter | 1.2701 | 1.1433 | 0 | 1.2701 | 9.9895 | 9.9895
1563 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903010103 | F03-NICHOLUS | AGRI | DLMS Meter | 1.0312 | 0.82006 | 0.12 | 0.91118 | 10.0002 | 10.0002
1564 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903020101 | F04-HULIKUNTE | AGRI | DLMS Meter | 1.7088 | 1.5382 | 0 | 1.7088 | 9.9833 | 9.9833
1565 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903010301 | F05-HUSKUR | AGRI | DLMS Meter | 0.67814 | 0.61022 | 0 | 0.67814 | 10.0159 | 10.0159
1566 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903010302 | F06-SASALU | AGRI | DLMS Meter | 1.7556 | 1.5799 | 0 | 1.7556 | 10.0117 | 10.0117
1567 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903010303 | F07-SAKKAREGOLLAHALLI | AGRI | DLMS Meter | 1.9244 | 1.7319 | 0 | 1.9244 | 10.0056 | 10.0056
1568 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903010304 | F08-KOLIGERE | AGRI | DLMS Meter | 1.7432 | 1.569 | 0 | 1.7432 | 9.9934 | 10.0506
1569 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903020301 | F09-NARANAHALLI | NJY | DLMS Meter | 1.5936 | 1.1695 | 0.262 | 1.3316 | 12.1729 | 33.0386
1570 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903010305 | F10-KHANIMATA | NJY | DLMS Meter | 1.3946 | 0.98028 | 0.285 | 1.1096 | 11.656 | 37.3905
1571 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903020302 | F11-SONNENAHALLI | NJY | DLMS Meter | 1.5789 | 1.139 | 0.285 | 1.2939 | 11.9691 | 37.8
1572 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903020303 | F12-RAMPURA | AGRI | DLMS Meter | 0.994 | 0.89455 | 0 | 0.994 | 10.005 | 10.005
1573 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | DODDABELAVANGALA_66 | 1210101903020304 | F13-NAGALAPURA | AGRI | DLMS Meter | 1.2632 | 1.1369 | 0 | 1.2632 | 9.9972 | 9.9972
1574 | CTAZ | TUMKUR | TUMKUR | NITTUR | DODDAGUNI_110 | 1320107901010101 | F01-QUARRY | INDUSTRIAL | DLMS Meter | 0.54891 | 0.19816 | 0.321 | 0.22791 | 13.053 | 13.053
1575 | CTAZ | TUMKUR | TUMKUR | NITTUR | DODDAGUNI_110 | 1320107901010102 | F02-KONDLY | AGRI | DLMS Meter | 1.1793 | 1.0338 | 0.008 | 1.1713 | 11.7388 | 11.7388
1576 | CTAZ | TUMKUR | TUMKUR | NITTUR | DODDAGUNI_110 | 1320107901010103 | F03-BADAVANPALYA | AGRI | DLMS Meter | 0.89204 | 0.80298 | 0 | 0.89204 | 9.9838 | 9.9838
1577 | CTAZ | TUMKUR | TUMKUR | NITTUR | DODDAGUNI_110 | 1320107901010104 | F04-DODDAGUNI | WATER WORKS | DLMS Meter | 0.52668 | 0.11237 | 0.397 | 0.12968 | 13.3521 | 18.2134
1578 | CTAZ | TUMKUR | TUMKUR | NITTUR | DODDAGUNI_110 | 1320107901010105 | F05-NERELEKERE | AGRI | DLMS Meter | 0.5004 | 0.45029 | 0 | 0.5004 | 10.0146 | 10.0146
1579 | CTAZ | TUMKUR | TUMKUR | NITTUR | DODDAGUNI_110 | 1320107901010106 | F06-TAGIHALLY | AGRI | DLMS Meter | 0.80908 | 0.72847 | 0 | 0.80908 | 9.9627 | 9.9627
1580 | CTAZ | TUMKUR | TUMKUR | NITTUR | DODDAGUNI_110 | 1320107901010107 | F07-BADENAHALLY(NJY) | NJY | DLMS Meter | 0.23678 | 0.21133 | 0.0025 | 0.23428 | 9.7945 | 48.5484
1581 | CTAZ | TUMKUR | TUMKUR | NITTUR | DODDAGUNI_110 | 1320107901010108 | F08-SHIVASANDRA-NJY | NJY | DLMS Meter | 0.27812 | 0.25282 | 0 | 0.27812 | 9.0979 | 55.9417
1582 | CTAZ | TUMKUR | TUMKUR | NITTUR | DODDAGUNI_110 | 1320107901010109 | F09-G.OBLAPURA-NJY | NJY | DLMS Meter | 0.5213 | 0.45399 | 0 | 0.5213 | 12.9111 | 33.7478
1583 | CTAZ | TUMKUR | TUMKUR | NITTUR | DODDAGUNI_110 | 1320107901010110 | F10-HARENAHALLI | NJY | DLMS Meter | 0.07082 | 0.063889 | 0 | 0.07082 | 9.7868 | 38.448
1584 | BRAZ | KOLAR | KGF | BETHAMANGLA | DODDAKARI_66 | 1230203906020201 | F01-GUTTAHALLI | AGRI | DLMS Meter | 0.7591 | 0.67088 | 0 | 0.7591 | 11.6214 | 11.6214
1585 | BRAZ | KOLAR | KGF | BETHAMANGLA | DODDAKARI_66 | 1230203906020202 | F02-BETHAMANGALA TOWN | DOMESTIC | DLMS Meter | 0.8526 | 0.73681 | 0 | 0.8526 | 13.5811 | 36.6216
1586 | BRAZ | KOLAR | KGF | BETHAMANGLA | DODDAKARI_66 | 1230203906010205 | F03-BATARKUPPA | AGRI | DLMS Meter | 0.7096 | 0.63852 | 0 | 0.7096 | 10.0168 | 10.0168
1587 | BRAZ | KOLAR | KGF | BETHAMANGLA | DODDAKARI_66 | 1230203906020203 | F04-BETKURU | NJY | DLMS Meter | 0.6568 | 0.5245 | 0.0541 | 0.6027 | 12.9747 | 68.4722
1588 | BRAZ | KOLAR | KGF | BETHAMANGLA | DODDAKARI_66 | 1230203906020204 | F05-VRS TEMPLE | DOMESTIC | DLMS Meter | 1.2776 | 1.1157 | 0 | 1.2776 | 12.675 | 49.2331
1589 | BRAZ | KOLAR | KGF | BETHAMANGLA | DODDAKARI_66 | 1230203906010206 | F08-HANGALA | AGRI | DLMS Meter | 1.1474 | 1.0325 | 0 | 1.1474 | 10.0139 | 10.132
1590 | BRAZ | KOLAR | KGF | BETHAMANGLA | DODDAKARI_66 | 1230203906010201 | F09-NALLUR | AGRI | DLMS Meter | 0.8756 | 0.777 | 0 | 0.8756 | 11.2606 | 11.2606
1591 | BRAZ | KOLAR | KGF | BETHAMANGLA | DODDAKARI_66 | 1230203906010204 | F10-HULKUR NJY | NJY | DLMS Meter | 1.4203 | 1.2124 | 0.0416 | 1.3787 | 12.0593 | 60.5044
1592 | BRAZ | KOLAR | KGF | BETHAMANGLA | DODDAKARI_66 | 1230203906010202 | F11-VADDRAHALLI | AGRI | DLMS Meter | 0.6806 | 0.61271 | 0 | 0.6806 | 9.9756 | 9.9756
1593 | BRAZ | KOLAR | KGF | BETHAMANGLA | DODDAKARI_66 | 1230203906010203 | F12-NERNAHALLI | AGRI | DLMS Meter | 0.7202 | 0.64804 | 0 | 0.7202 | 10.0201 | 10.0201
1594 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | DODDALAHALLI_66 | 1220303903010101 | F01-DKS | NJY | DLMS Meter | 0.46382 | 0.35653 | 0.07 | 0.39382 | 9.4695 | 36.3896
1595 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | DODDALAHALLI_66 | 1220303903010102 | F02-OM-SHANTHIDHAMA | NJY | DLMS Meter | 0.44588 | 0.24125 | 0.179 | 0.26688 | 9.6029 | 40.5257
1596 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | DODDALAHALLI_66 | 1220303903010103 | F03-CHUNCHI | AGRI | DLMS Meter | 1.7877 | 1.6088 | 0 | 1.7877 | 10.0082 | 10.0082
1597 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | DODDALAHALLI_66 | 1220303903010104 | F04-MADIVALA | AGRI | DLMS Meter | 1.1936 | 1.0741 | 0 | 1.1936 | 10.0089 | 10.0089
1598 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | DODDALAHALLI_66 | 1220303903020303 | F05-MAHIMANAHALLI | AGRI | DLMS Meter | 1.2658 | 1.1393 | 0 | 1.2658 | 9.9918 | 11.0294
1599 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | DODDALAHALLI_66 | 1220303903020302 | F06-PVD NJY | NJY | DLMS Meter | 0.43878 | 0.26339 | 0.147 | 0.29178 | 9.7308 | 53.7202
1600 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | DODDALAHALLI_66 | 1220303903020301 | F07-CHIKKALAHALLI NJY | NJY | DLMS Meter | 0.30044 | 0.22461 | 0.0526 | 0.24784 | 9.3743 | 45.4109
1601 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | DODDALAHALLI_66 | 1220303903020304 | F08-YELAGALLI NJY | NJY | DLMS Meter | 0.494 | 0.2949 | 0.17 | 0.324 | 8.9817 | 49.0382
1602 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | DODDALAHALLI_66 | 1220303903010105 | F09-NAGARASANAKOTE | AGRI | DLMS Meter | 1.0018 | 0.64044 | 0.29 | 0.71178 | 10.0229 | 10.0229
1603 | BMASZ | SOUTH | HSR | S11 | DOMMASANDRA_66 (SULIKUNTE) | 1110303903010101 | F03-AGARA | DOMESTIC | DLMS Meter | 3.2709 | 3.0359 | 0.04 | 3.2309 | 6.0346 | 12.104
1604 | BMASZ | SOUTH | HSR | S11 | DOMMASANDRA_66 (SULIKUNTE) | 1110303903010301 | F10-WIPRO | DOMESTIC | DLMS Meter | 7.2554 | 6.8039 | 0 | 7.2554 | 6.2223 | 11.6022
1605 | BMASZ | SOUTH | HSR | S11 | DOMMASANDRA_66 (SULIKUNTE) | 1110303903010102 | F13-AHAD_BUILDERS | DOMESTIC | DLMS Meter | 3.2984 | 0.86948 | 2.37 | 0.92841 | 6.3475 | 9.4351
1606 | BMASZ | SOUTH | HSR | S11 | DOMMASANDRA_66 (SULIKUNTE) | 1110303903020301 | F16-WIPRO SEZ | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1607 | BMASZ | SOUTH | HSR | S11 | DOMMASANDRA_66 (SULIKUNTE) | 1110303903010103 | F17-APG INTELLIHOMES | URBAN MIXED LOAD | DLMS Meter | 0.73112 | 0.15091 | 0.572 | 0.15912 | 5.1591 | 13.515
1608 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903010101 | F01-V.KALLAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.9378 | 2.2463 | 0.528 | 2.4098 | 6.7845 | 12.5541
1609 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903010102 | F02-DOMMASANDRA | URBAN MIXED LOAD | DLMS Meter | 4.3647 | 3.9769 | 0 | 4.3647 | 8.8845 | 13.3819
1610 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903010103 | F04-SOMPURA | AGRI | DLMS Meter | 0.09065 | 0.081772 | 0 | 0.09065 | 9.7935 | 9.7935
1611 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903010104 | F05-NERIGA | AGRI | DLMS Meter | 1.5893 | 1.4314 | 0 | 1.5893 | 9.9327 | 9.9887
1612 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903020301 | F06-SOMPURAGATE | URBAN MIXED LOAD | DLMS Meter | 6.2367 | 5.8948 | 0 | 6.2367 | 5.4831 | 8.0841
1613 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903020302 | F07-VAKIL-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0.28228 | 0.25158 | 0.0104 | 0.27188 | 7.4665 | 7.4665
1614 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903020303 | F09-CHAMBENAHALLI | AGRI | DLMS Meter | 1.9798 | 1.7816 | 0 | 1.9798 | 10.0073 | 10.0073
1615 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903010105 | F11-NIRANTHARA-JYOTHI | NJY | DLMS Meter | 2.999 | 1.79 | 1.039 | 1.96 | 8.6711 | 25.227
1616 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903010106 | F12-TRINITY-SUNRISE | URBAN MIXED LOAD | DLMS Meter | 2.1034 | 0.63065 | 1.408 | 0.69536 | 9.3065 | 16.7131
1617 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903020305 | F14-DOMMASANDRA AGRI | AGRI | DLMS Meter | 0.5613 | 0.50517 | 0 | 0.5613 | 9.9995 | 9.9995
1618 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | DOMMASANDRA_66 | 1220202903010112 | F15-T C HALLI NJY | URBAN MIXED LOAD | DLMS Meter | 1.6922 | 1.0657 | 0.53 | 1.1622 | 8.3021 | 8.3021
1619 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | DUNDANAHALLI_66 | 1220104902020301 | F02-KUMBARAKATTE | AGRI | DLMS Meter | 0.61977 | 0.55788 | 0 | 0.61977 | 9.9863 | 9.9863
1620 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905010101 | F01-DEVARAMARIKUNTTE | AGRI | DLMS Meter | 1.0454 | 0.92688 | 0 | 1.0454 | 11.3372 | 11.3372
1621 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905010102 | F02-DODDERI | AGRI | DLMS Meter | 0.88806 | 0.79936 | 0 | 0.88806 | 9.9885 | 9.9885
1622 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905010103 | F03-MEERASABHIHALLY | AGRI | DLMS Meter | 0.61182 | 0.55019 | 0 | 0.61182 | 10.0732 | 10.0732
1623 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905010104 | F04-KARIKERE | AGRI | DLMS Meter | 0.5756 | 0.51781 | 0 | 0.5756 | 10.0407 | 10.0407
1624 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905010105 | F05- PURLAHALLY NJY | NJY | DLMS Meter | 0.35881 | 0.31157 | 0 | 0.35881 | 13.1669 | 54.8282
1625 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905010106 | F06-JAJUR NJY | NJY | DLMS Meter | 0.66666 | 0.58479 | 0 | 0.66666 | 12.2811 | 65.2466
1626 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905010107 | F07-BHARAMASAGARA NJY | NJY | DLMS Meter | 0.6782 | 0.58197 | 0 | 0.6782 | 14.1889 | 66.8075
1627 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905010108 | F08-RANIKERE NJY | NJY | DLMS Meter | 0.2035 | 0.17633 | 0 | 0.2035 | 13.3489 | 51.9324
1628 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905020301 | F09-SURANAHALLI | AGRI | DLMS Meter | 0.7724 | 0.69523 | 0 | 0.7724 | 9.9907 | 14.3483
1629 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905020302 | F10-VADERAHALLI | AGRI | DLMS Meter | 1.1408 | 1.015 | 0 | 1.1408 | 11.0295 | 11.0295
1630 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905020304 | F11-CHANNAMMANAGATHI HALLI | AGRI | DLMS Meter | 1.968 | 1.7717 | 0 | 1.968 | 9.9724 | 9.9724
1631 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | DYAVARANAHALLI_66 | 1310402905020303 | F12-MATSAMUDRA | AGRI | DLMS Meter | 0.4664 | 0.41965 | 0 | 0.4664 | 10.0236 | 10.0236
1632 | BMANZ | EAST | INDIRA NAGAR | E3 | EASTDIVCOMP_220 | 1130201901030101 | F02-CEARS-PLAZA | URBAN MIXED LOAD | DLMS Meter | 2.4276 | 2.265 | 0.07484 | 2.3528 | 3.7337 | 3.7337
1633 | BMANZ | EAST | INDIRA NAGAR | E3 | EASTDIVCOMP_220 | 1130201901030102 | F03-RAMA-HOTEL-RMU | URBAN MIXED LOAD | DLMS Meter | 4.225 | 4.0712 | 0 | 4.225 | 3.6402 | 4.1128
1634 | BMANZ | EAST | INDIRA NAGAR | E3 | EASTDIVCOMP_220 | 1130201901030103 | F04-WALTON-ROAD | URBAN MIXED LOAD | DLMS Meter | 4.1149 | 3.9727 | 0 | 4.1149 | 3.4554 | 6.7613
1635 | BMANZ | EAST | INDIRA NAGAR | E3 | EASTDIVCOMP_220 | 1130201901030104 | F05-SPENCERS-BUILDING | URBAN MIXED LOAD | DLMS Meter | 1.7013 | 1.6449 | 0 | 1.7013 | 3.3133 | 6.0727
1636 | BMANZ | EAST | INDIRA NAGAR | E3 | EASTDIVCOMP_220 | 1130201901020302 | F07-FPRESTIGE-EMARALD-RMU | URBAN MIXED LOAD | DLMS Meter | 2.3184 | 2.2446 | 0 | 2.3184 | 3.1848 | 5.8832
1637 | BMANZ | EAST | INDIRA NAGAR | E3 | EASTDIVCOMP_220 | 1130201901020303 | F08-KAPOOR-BUILDING-RMU | URBAN MIXED LOAD | DLMS Meter | 1.6664 | 1.1328 | 0.49456 | 1.1718 | 3.3351 | 10.4036
1638 | BMANZ | EAST | INDIRA NAGAR | E3 | EASTDIVCOMP_220 | 1130201901020304 | F09-SAMUKTHA-KARNATAKA | URBAN MIXED LOAD | DLMS Meter | 1.9315 | 1.8707 | 0 | 1.9315 | 3.1508 | 4.8723
1639 | BMANZ | EAST | INDIRA NAGAR | E3 | EASTDIVCOMP_220 | 1130201901020305 | F11-ITC-GARDENIA | COMMERCIAL | DLMS Meter | 2.5967 | 2.4914 | 0.077633 | 2.519 | 1.0973 | 1.0973
1640 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020101 | F01-SYSCON | INDUSTRIAL | DLMS Meter | 2.7012 | 2.6029 | 0 | 2.7012 | 3.6401 | 3.6401
1641 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | ELECTRONIC_CITY_66 | 1110301902020102 | F02-KONAPANAAGRAHARA | URBAN MIXED LOAD | DLMS Meter | 2.3884 | 1.9476 | 0.37 | 2.0184 | 3.5099 | 3.5099
1642 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020301 | F03-CYBER-PARK | INDUSTRIAL | DLMS Meter | 1.2515 | 1.1886 | 0 | 1.2515 | 5.0261 | 5.0261
1643 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | ELECTRONIC_CITY_66 | 1110301902020103 | F04-HEBBAGODI | DOMESTIC | DLMS Meter | 3.4768 | 3.2004 | 0 | 3.4768 | 7.9486 | 7.9486
1644 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020501 | F05-YOKOGOVA | INDUSTRIAL | DLMS Meter | 1.9511 | 1.8668 | 0 | 1.9511 | 4.3225 | 4.3225
1645 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020104 | F06-FWIPRO-EC | INDUSTRIAL | DLMS Meter | 2.5954 | 2.5434 | 0 | 2.5954 | 2.0054 | 2.0054
1646 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020105 | F07-FMOOG-CONTROL | INDUSTRIAL | DLMS Meter | 2.6347 | 2.454 | 0.09808 | 2.5366 | 3.2557 | 22.4573
1647 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020302 | F08-NEELADRI-NAGAR | URBAN MIXED LOAD | DLMS Meter | 1.8432 | 1.7583 | 0 | 1.8432 | 4.605 | 4.605
1648 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020303 | F09-WIPRO-COMPLEX | INDUSTRIAL | DLMS Meter | 1.6215 | 1.592 | 0 | 1.6215 | 1.8201 | 2.8965
1649 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020304 | F10-WIPRO-EC | INDUSTRIAL | DLMS Meter | 0.87845 | 0.85015 | 0 | 0.87845 | 3.2219 | 3.2219
1650 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | ELECTRONIC_CITY_66 | 1110301902020502 | F11-VEERASANDRA-INDUSTRIAL-AREA | URBAN MIXED LOAD | DLMS Meter | 4.0856 | 3.7566 | 0.05 | 4.0356 | 6.9143 | 13.4196
1651 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | ELECTRONIC_CITY_66 | 1110301902020107 | F13-SURYA-PARK | INDUSTRIAL | DLMS Meter | 0.2305 | 0.22854 | 0 | 0.2305 | 0.85033 | 0.85033
1652 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITY_66 | 1110301902020305 | F14-KAMMASANDRA | URBAN MIXED LOAD | DLMS Meter | 0.15075 | 0.15075 | 0 | 0.15075 | 0 | 7.9018
1653 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020306 | F15-CONCORDE | INDUSTRIAL | DLMS Meter | 1.5759 | 1.5095 | 0 | 1.5759 | 4.2125 | 4.2125
1654 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020307 | F16-VELANKANI | INDUSTRIAL | DLMS Meter | 0.8048 | 0.70217 | 0.081241 | 0.72356 | 2.9561 | 4.0163
1655 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | ELECTRONIC_CITY_66 | 1110301902020308 | F17-INDIA BUILD REALITY | DOMESTIC | DLMS Meter | 0.1676 | 0.15498 | 0.006 | 0.1616 | 4.0968 | 4.0968
1656 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITY_66 | 1110301902020310 | F19-KSSIDC | URBAN MIXED LOAD | DLMS Meter | 2.8276 | 2.5816 | 0.04 | 2.7876 | 7.3912 | 11.9564
1657 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020503 | F20-WIPRO-EC | INDUSTRIAL | DLMS Meter | 3.1289 | 3.1088 | 0 | 3.1289 | 0.64189 | 0.64189
1658 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020504 | F21-STPI | INDUSTRIAL | DLMS Meter | 4.7509 | 4.7106 | 0 | 4.7509 | 0.84773 | 0.84773
1659 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020505 | F22-AJMEERA-INFINITY | INDUSTRIAL | DLMS Meter | 1.6496 | 1.2174 | 0.3786 | 1.271 | 4.2119 | 4.2119
1660 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020506 | F23-WIPRO-EC-SEZ | INDUSTRIAL | DLMS Meter | 5.3501 | 5.3325 | 0 | 5.3501 | 0.32878 | 0.32878
1661 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020507 | F24-ITTINA-MAHAVEER | INDUSTRIAL | DLMS Meter | 3.7729 | 2.3804 | 1.2729 | 2.5 | 4.7859 | 4.7859
1662 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020508 | F25-HCL | INDUSTRIAL | DLMS Meter | 2.3426 | 0.02295 | 2.3196 | 0.023094 | 0.6226 | 0.6226
1663 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020509 | F26-SIEMENS | INDUSTRIAL | DLMS Meter | 1.6089 | 1.4298 | 0.085214 | 1.5237 | 6.1635 | 6.5709
1664 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020510 | F27-SYMBIOSIS | INDUSTRIAL | DLMS Meter | 1.7229 | 1.6656 | 0 | 1.7229 | 3.3299 | 3.3299
1665 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | ELECTRONIC_CITY_66 | 1110301902020311 | F28-GOLLAHALLI | DOMESTIC | DLMS Meter | 2.9056 | 2.3183 | 0.398 | 2.5076 | 7.5479 | 7.5479
1666 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020108 | F29-NET-MAGIC-IT-SERVICES | INDUSTRIAL | DLMS Meter | 10.3718 | 9.9964 | 0 | 10.3718 | 3.6196 | 80.5855
1667 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITY_66 | 1110301902020312 | F30-NSDL | INDUSTRIAL | DLMS Meter | 3.2649 | 3.2456 | 0 | 3.2649 | 0.58939 | 0.58939
1668 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | ELECTRONIC_CITY_66 | 1110301902020313 | F31-SHRIRAM PROPERTIES | DOMESTIC | DLMS Meter | 0.6008 | 0.57486 | 0 | 0.6008 | 4.3184 | 4.3184
1669 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | ELECTRONIC_CITY_66 | 1110301902030101 | F32-PRESTIGE BIRCHWOOD | DOMESTIC | DLMS Meter | 1.2982 | 0.73587 | 0.525 | 0.7732 | 4.8276 | 5.2263
1670 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903020102 | F02-SALARPURIA | INDUSTRIAL | DLMS Meter | 5.1308 | 4.9434 | 0 | 5.1308 | 3.6528 | 4.326
1671 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903020103 | F03-TIMKIN | INDUSTRIAL | DLMS Meter | 2.0906 | 1.9363 | 0.12655 | 1.964 | 1.4127 | 1.4127
1672 | BMASZ | SOUTH | HSR | S8 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903020104 | F04-GARVEBAVIPALYA | DOMESTIC | DLMS Meter | 4.4092 | 4.078 | 0 | 4.4092 | 7.5111 | 7.5111
1673 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903010301 | F06-FVELANKANI | INDUSTRIAL | DLMS Meter | 2.5038 | 2.4912 | 0 | 2.5038 | 0.50502 | 1.011
1674 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903010302 | F07-FBHEL | INDUSTRIAL | DLMS Meter | 4.7098 | 4.2876 | 0.20327 | 4.5065 | 4.8582 | 4.8582
1675 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903010303 | F08-DODDATHOGUR | DOMESTIC | DLMS Meter | 1.7229 | 1.5278 | 0.14533 | 1.5776 | 3.1567 | 6.5254
1676 | BMASZ | SOUTH | HSR | S8 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903010304 | F09-NGR-LAYOUT | INDUSTRIAL | DLMS Meter | 5.2107 | 4.8535 | 0.002 | 5.2087 | 6.8199 | 9.4371
1677 | BMASZ | SOUTH | HSR | S8 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903010305 | F10-BOMMANAHALLI-MN-RD | INDUSTRIAL | DLMS Meter | 3.8773 | 3.4842 | 0.105 | 3.7723 | 7.6391 | 17.8909
1678 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903020106 | F11-HOTEL-OTTERA | COMMERCIAL | DLMS Meter | 2.8966 | 2.8892 | 0 | 2.8966 | 0.25598 | 8.2405
1679 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903010306 | F12-BSNL-TELEPHONE-EXCHANGE | INDUSTRIAL | DLMS Meter | 3.2322 | 3.2006 | 0 | 3.2322 | 0.97611 | 0.97611
1680 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903010307 | F13-WIPRO-SEZ | INDUSTRIAL | DLMS Meter | 0.52717 | 0.47632 | 0.046101 | 0.48107 | 0.9862 | 0.9862
1681 | BMASZ | SOUTH | HSR | S8 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903030501 | F14-BEGUR ROAD | URBAN MIXED LOAD | DLMS Meter | 3.3636 | 3.0865 | 0.0043 | 3.3593 | 8.1207 | 11.12
1682 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903030503 | F15-UNIVERSAL-BUILDER | URBAN MIXED LOAD | DLMS Meter | 4.119 | 2.0003 | 2.019 | 2.1 | 4.7506 | 4.7506
1683 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903030504 | F16-CELEBRITY-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.4902 | 2.3053 | 0.08012 | 2.4101 | 4.3472 | 4.3472
1684 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903030505 | F17-KONAPPANA-AGRAHARA | URBAN MIXED LOAD | DLMS Meter | 0.41161 | 0.25982 | 0.13463 | 0.27698 | 6.195 | 7.9196
1685 | BMASZ | SOUTH | HSR | S10 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903030507 | F19-VITTASANDRA | URBAN MIXED LOAD | DLMS Meter | 2.9087 | 1.7314 | 0.8558 | 2.0529 | 15.6574 | 22.3327
1686 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903030508 | F20-CHIKKATHOGURU | URBAN MIXED LOAD | DLMS Meter | 3.0584 | 2.1081 | 0.87247 | 2.1859 | 3.5604 | 3.5736
1687 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903030101 | F21-STPI | INDUSTRIAL | DLMS Meter | 0.40027 | 0.3925 | 0 | 0.40027 | 1.942 | 1.942
1688 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC1_66 | 1110301903030502 | F22-INFOSYS | INDUSTRIAL | DLMS Meter | 0.28696 | 0.28416 | 0 | 0.28696 | 0.97676 | 0.97676
1689 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020101 | F02-TATA-B.P-SOLAR | URBAN MIXED LOAD | DLMS Meter | 3.3733 | 2.9127 | 0.35675 | 3.0165 | 3.4414 | 3.4414
1690 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020102 | F03-MALGUDI | INDUSTRIAL | DLMS Meter | 1.1816 | 1.1376 | 0 | 1.1816 | 3.7207 | 3.7207
1691 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020103 | F04-BBMP | INDUSTRIAL | DLMS Meter | 0.42532 | 0.38352 | 0.036142 | 0.38917 | 1.453 | 1.453
1692 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020104 | F05-DODDANAGAMANGALA | INDUSTRIAL | DLMS Meter | 4.649 | 2.2099 | 2.3028 | 2.3462 | 5.8113 | 6.8697
1693 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020105 | F06-FIDLE | INDUSTRIAL | DLMS Meter | 2.5014 | 2.3042 | 0.11486 | 2.3865 | 3.4491 | 3.969
1694 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020301 | F07-FSATHYAM | INDUSTRIAL | DLMS Meter | 1.2374 | 1.158 | 0.006325 | 1.2311 | 5.9317 | 6.1476
1695 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020302 | F08-MOOG | INDUSTRIAL | DLMS Meter | 3.2426 | 2.9924 | 0.16621 | 3.0764 | 2.7292 | 2.7292
1696 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020303 | F09-VIA | INDUSTRIAL | DLMS Meter | 5.7686 | 5.4163 | 0 | 5.7686 | 6.1067 | 6.3803
1697 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020304 | F10-VEERASANDRA | INDUSTRIAL | DLMS Meter | 3.4499 | 3.1665 | 0.072 | 3.3779 | 6.2578 | 6.8663
1698 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020305 | F11-ITTINA | DOMESTIC | DLMS Meter | 3.921 | 2.9595 | 0.7027 | 3.2183 | 8.0399 | 27.5653
1699 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020306 | F12-ANATH-NAGAR-PHASE | DOMESTIC | DLMS Meter | 0.63231 | 0.63231 | 0 | 0.63231 | 0 | 0.85102
1700 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020106 | F13-GOLBAL-TECH-PARK | INDUSTRIAL | DLMS Meter | 1.0454 | 1.0373 | 0 | 1.0454 | 0.78359 | 0.95661
1701 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020107 | F14-GOLD-HILL-SQUARE | INDUSTRIAL | DLMS Meter | 2.8948 | 2.8735 | 0 | 2.8948 | 0.73439 | 0.73439
1702 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901020307 | F15-EQUINOX INFOSYS | INDUSTRIAL | DLMS Meter | 1.7368 | 1.5527 | 0.12928 | 1.6075 | 3.411 | 3.411
1703 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901010109 | F16-BBMP | URBAN MIXED LOAD | DLMS Meter | 0.05832 | 0.057649 | 0 | 0.05832 | 1.1505 | 1.1586
1704 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901030501 | F17-SNN APARTMENT | DOMESTIC | DLMS Meter | 4.3092 | 4.1082 | 0 | 4.3092 | 4.664 | 4.664
1705 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901030502 | F18-MICROLABS | INDUSTRIAL | DLMS Meter | 3.1824 | 3.1809 | 0 | 3.1824 | 0.048423 | 0.052984
1706 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901030503 | F19-ANANTHANAGARA | URBAN MIXED LOAD | DLMS Meter | 2.4458 | 1.9846 | 0.293 | 2.1528 | 7.8131 | 8.2804
1707 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901030504 | F21-GLASS FACTORY LAYOUT | DOMESTIC | DLMS Meter | 2.5692 | 2.34 | 0.05 | 2.5192 | 7.1141 | 7.26
1708 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901030509 | F22-DADDY'S GARDEN | URBAN MIXED LOAD | DLMS Meter | 2.8244 | 1.7851 | 0.8681 | 1.9563 | 8.7511 | 22.5602
1709 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901030507 | F23-SHANTHIPURA | DOMESTIC | DLMS Meter | 1.7882 | 1.6423 | 0.0303 | 1.7579 | 6.5786 | 11.8854
1710 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | 1110301901030506 | F25-NSDL | INDUSTRIAL | DLMS Meter | 0.91735 | 0 | 0.91735 | -3.0631e-07 | 0 | #DIV/0!
1711 | BRAZ | RAMANAGAR | CHANDAPURA | VEERASANDRA | ELECTRONIC_CITYPH2SEC2_66 | 1110301901030508 | F26-MINDCOMP | INDUSTRIAL | DLMS Meter | 1.8132 | 1.8118 | 0 | 1.8132 | 0.077212 | 0.10286
1712 | BMASZ | SOUTH | HSR | S13 | ELECTRONIC_CITYPH2SEC2_66 | #N/A | F27-Venkateshwara-Industries | #N/A | DLMS Meter | 2.2416 | 2.2203 | 0 | 2.2416 | 0.952 | 0.952
1713 | BMASZ | SOUTH | JAYANAGAR | S6 | ELITE_PROMRNDE_66 | 1110104902010101 | F01-PHASE-I-A | DOMESTIC | DLMS Meter | 0.50201 | 0.47458 | 0.002325 | 0.49969 | 5.024 | 5.024
1714 | BMASZ | SOUTH | JAYANAGAR | S6 | ELITE_PROMRNDE_66 | 1110104902010102 | F02-K.R-LAYOUT | DOMESTIC | DLMS Meter | 3.9221 | 3.6878 | 0.094008 | 3.8281 | 3.663 | 9.9303
1715 | BMASZ | SOUTH | JAYANAGAR | S6 | ELITE_PROMRNDE_66 | 1110104902010103 | F03-SHARADA-NAGAR | DOMESTIC | DLMS Meter | 2.0024 | 1.8545 | 0.069012 | 1.9334 | 4.0773 | 15.3765
1716 | BMASZ | SOUTH | JAYANAGAR | S6 | ELITE_PROMRNDE_66 | 1110104902010104 | F04-PHASE--B | DOMESTIC | DLMS Meter | 0.49144 | 0.46357 | 0.000825 | 0.49062 | 5.5125 | 5.8681
1717 | BMASZ | SOUTH | JAYANAGAR | S6 | ELITE_PROMRNDE_66 | 1110104902010105 | F05-ELITAPH | DOMESTIC | DLMS Meter | 0.62464 | 0.58437 | 0.00809 | 0.61655 | 5.2199 | 5.2199
1718 | BMASZ | SOUTH | KORAMANGALA | S7 | EMBASSY | #N/A | F03-Parcel 9 C Block | #N/A | DLMS Meter | 0.026839 | 0.02648 | 0 | 0.026839 | 1.337 | 1.337
1719 | BMASZ | SOUTH | KORAMANGALA | S7 | EMBASSY | #N/A | F04- Parcel 9 A&B Block | #N/A | DLMS Meter | 0.26318 | 0.26348 | 0 | 0.26318 | -0.11091 | -0.11091
1720 | BMASZ | SOUTH | KORAMANGALA | S7 | EMBASSY | #N/A | F1- 2A Cisco Block | #N/A | DLMS Meter | 1.8919 | 1.8947 | 0 | 1.8919 | -0.14751 | -0.14751
1721 | BMASZ | SOUTH | KORAMANGALA | S7 | EMBASSY | #N/A | F2 - 2C & 2D Block | #N/A | DLMS Meter | 2.7063 | 2.7107 | 0 | 2.7063 | -0.16381 | 39.1094
1722 | BMASZ | SOUTH | KORAMANGALA | S7 | EMBASSY | #N/A | F24 - 2A & 2B Block | #N/A | DLMS Meter | 2.3957 | 2.4108 | 0 | 2.3957 | -0.62976 | 42.0804
1723 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907010101 | F02-WHITEFIELD | INDUSTRIAL | DLMS Meter | 3.5774 | 3.1852 | 0.22 | 3.3574 | 5.1312 | 5.1312
1724 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907010102 | F03-SPLENDER | COMMERCIAL | DLMS Meter | 0.58122 | 0.55098 | 0 | 0.58122 | 5.2025 | 11.0056
1725 | BMASZ | SOUTH | KORAMANGALA | S7 | EPIP_66 | 1130202907010103 | F04-THUBARAHALLI | DOMESTIC | DLMS Meter | 2.9591 | 2.7289 | 0.05 | 2.9091 | 6.1952 | 10.4244
1726 | BMASZ | SOUTH | KORAMANGALA | S7 | EPIP_66 | 1130202907020301 | F05-BEML-LAYOUT | DOMESTIC | DLMS Meter | 2.0886 | 1.9526 | 0 | 2.0886 | 6.5113 | 14.058
1727 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907020302 | F06-L-&-T | INDUSTRIAL | DLMS Meter | 0.56661 | 0.55607 | 0 | 0.56661 | 1.8607 | 1.8607
1728 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907010104 | F07-RMZ-NEXT | URBAN MIXED LOAD | DLMS Meter | 2.2595 | 2.0157 | 0.088624 | 2.1709 | 7.1489 | 7.6581
1729 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907020304 | F09-EPIP-L/OII | INDUSTRIAL | DLMS Meter | 2.6876 | 2.6676 | 0 | 2.6876 | 0.74385 | 3.6279
1730 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907020305 | F10-EPIPI | INDUSTRIAL | DLMS Meter | 3.4807 | 3.3419 | 0 | 3.4807 | 3.9884 | 3.9884
1731 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907020306 | F11-TCS | INDUSTRIAL | DLMS Meter | 2.9671 | 2.9547 | 0 | 2.9671 | 0.41972 | 37.9939
1732 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907030501 | F12-P.OZONE-LAYOUT-/--VARTHUR | DOMESTIC | DLMS Meter | 3.3887 | 0.10254 | 3.2858 | 0.10286 | 0.31084 | 0.31084
1733 | BMASZ | SOUTH | KORAMANGALA | S7 | EPIP_66 | 1130202907020308 | F14-KNIGHT-BRIDGE | DOMESTIC | DLMS Meter | 3.4573 | 1.051 | 2.4 | 1.0573 | 0.59827 | 3.4471
1734 | BMASZ | SOUTH | KORAMANGALA | S7 | EPIP_66 | 1130202907020309 | F15-PURVANKARA | DOMESTIC | DLMS Meter | 3.5167 | 2.6841 | 0.606 | 2.9107 | 7.7842 | 14.5821
1735 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907030502 | F16-SJR-TECH-PARK,-EPIP-L/O | INDUSTRIAL | DLMS Meter | 2.6931 | 2.6732 | 0 | 2.6931 | 0.73838 | 0.73838
1736 | BMASZ | SOUTH | KORAMANGALA | S7 | EPIP_66 | 1130202907010105 | F17-PURVANKARA | DOMESTIC | DLMS Meter | 4.264 | 2.9999 | 1.05 | 3.214 | 6.6639 | 10.3726
1737 | BMASZ | SOUTH | KORAMANGALA | S7 | EPIP_66 | 1130202907010106 | F18-ROHAN-VASANTHA | DOMESTIC | DLMS Meter | 2.9436 | 2.1368 | 0.61243 | 2.3311 | 8.3373 | 12.2872
1738 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907020310 | F20-SAP-LABS,-EPIP-L/O | INDUSTRIAL | DLMS Meter | 1.8236 | 1.7845 | 0 | 1.8236 | 2.1425 | 2.1425
1739 | BMASZ | SOUTH | KORAMANGALA | S7 | EPIP_66 | 1130202907010108 | F21-STEERLING-APPARTMENT | DOMESTIC | DLMS Meter | 3.5078 | 2.572 | 0.69291 | 2.8149 | 8.6278 | 8.6278
1740 | BMASZ | SOUTH | KORAMANGALA | S7 | EPIP_66 | 1130202907010109 | F22-DIVYASHREE-TECH-PARK | INDUSTRIAL | DLMS Meter | 1.9303 | 1.255 | 0.64204 | 1.2882 | 2.5792 | 2.5792
1741 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907010201 | F23-VSNL-CO,-EPIP-L/O | COMMERCIAL | DLMS Meter | 5.8559 | 0 | 5.8559 | 4.0824e-10 | 0 | #DIV/0!
1742 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907010202 | F24-RELIANCE-(BIG-BAZAR) | INDUSTRIAL | DLMS Meter | 2.0393 | 2.011 | 0 | 2.0393 | 1.3865 | 1.3865
1743 | BMASZ | SOUTH | KORAMANGALA | S7 | EPIP_66 | 1130202907030601 | F25-DIVYASHREE-TECH-PARK | INDUSTRIAL | DLMS Meter | 1.8746 | 1.4997 | 0.37 | 1.5046 | 0.32514 | 0.32514
1744 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907030602 | F26-ORIENTAL-HOTEL | URBAN MIXED LOAD | DLMS Meter | 3.4293 | 3.3542 | 0 | 3.4293 | 2.1922 | 2.1922
1745 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907010203 | F27-AIRTEL-CO,-EPIP-L/O | COMMERCIAL | DLMS Meter | 13.8388 | 13.51 | 0 | 13.8388 | 2.3759 | 2.3759
1746 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907010204 | F28-BUSHRA-TECH-PARK,-EPIP-L/O | HOSPITAL | DLMS Meter | 0.99157 | 0.88224 | 0.082581 | 0.90899 | 2.9425 | 2.9425
1747 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907030603 | F30-GOPALAN-ENTERPRISES | INDUSTRIAL | DLMS Meter | 4.3926 | 3.8522 | 0.39853 | 3.9941 | 3.5519 | 4.5935
1748 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907020311 | F31-SADA-TECH-PARK,-EPIP-L/O | COMMERCIAL | DLMS Meter | 0.80553 | 0.63184 | 0.134 | 0.67153 | 5.9106 | 10.1588
1749 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907030503 | F32-QUALCOMM | INDUSTRIAL | DLMS Meter | 5.8501 | 5.8501 | 0 | 5.8501 | 0 | 0
1750 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | #N/A | F33-QUALCOMM-2 | #N/A | DLMS Meter | 7.2758 | 3.997 | 3.1521 | 4.1238 | 3.0742 | 3.0742
1751 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907020402 | F34-GEBE | INDUSTRIAL | DLMS Meter | 5.4355 | 3.6256 | 1.8 | 3.6355 | 0.27311 | 0.27311
1752 | BMANZ | EAST | WHITEFIELD | E12 | EPIP_66 | 1130202907030604 | F35-NEON BLOCK | COMMERCIAL | DLMS Meter | 0.81772 | 0.81319 | 0 | 0.81772 | 0.55424 | 0.55424
1753 | BMASZ | SOUTH | KORAMANGALA | S7 | ETV_66 | 1110203911040101 | F25-FLIPKART GROUP 1 | COMMERCIAL | DLMS Meter | 1.693 | 1.703 | 0 | 1.693 | -0.58992 | -0.58992
1754 | BMASZ | SOUTH | KORAMANGALA | S7 | ETV_66 | 1110203911040102 | F26-7B MLCP | COMMERCIAL | DLMS Meter | 2.0467 | 2.0604 | 0 | 2.0467 | -0.66713 | -0.66713
1755 | BMASZ | SOUTH | KORAMANGALA | S7 | ETV_66 | 1110203911040103 | F27-FLIPKART GROUP 2 | COMMERCIAL | DLMS Meter | 3.3078 | 3.3288 | 0 | 3.3078 | -0.63606 | -0.63606
1756 | BMASZ | SOUTH | KORAMANGALA | S7 | ETV_66 | 1110203911040104 | F28-FLIPKART GROUP 3 | COMMERCIAL | DLMS Meter | 1.0259 | 1.0311 | 0 | 1.0259 | -0.50673 | -0.50673
1757 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010108 | F01-PLATINA BLOCK III | COMMERCIAL | DLMS Meter | 1.4118 | 1.3596 | 0 | 1.4118 | 3.6957 | 3.6957
1758 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010114 | F02-PLATINA BLOCK-1 | COMMERCIAL | DLMS Meter | 0.70898 | 0.69698 | 0 | 0.70898 | 1.6938 | 1.6938
1759 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010101 | F03-ELECTRO-BLOCK | COMMERCIAL | DLMS Meter | 9.5997 | 9.6135 | 0 | 9.5997 | -0.14411 | -0.14411
1760 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010112 | F04-KARIYAMMANA AGRAHARA NEW | DOMESTIC | DLMS Meter | 0.77793 | 0.57834 | 0.16655 | 0.61139 | 5.4057 | 12.7878
1761 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010102 | F05-EXCELSIOR-BLOCK | COMMERCIAL | DLMS Meter | 3.0622 | 3.0676 | 0 | 3.0622 | -0.17825 | -0.17825
1762 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010103 | F06-F-EXORA-RIGHT-WING-BLOCK | COMMERCIAL | DLMS Meter | 5.1645 | 5.1762 | 0 | 5.1645 | -0.22558 | -0.22558
1763 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010104 | F07-FMLCT | COMMERCIAL | DLMS Meter | 1.6979 | 1.6817 | 0 | 1.6979 | 0.95524 | 0.95524
1764 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010113 | F08-VALDEL | COMMERCIAL | DLMS Meter | 1.1378 | 1.1422 | 0 | 1.1378 | -0.38255 | -0.38255
1765 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904020304 | F09- SALARPURIA SATTVA | COMMERCIAL | DLMS Meter | 5.5118 | 5.5212 | 0 | 5.5118 | -0.16962 | 0.55176
1766 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904020302 | F10-MLCP BLOCK VALDEL | COMMERCIAL | DLMS Meter | 0.85567 | 0.8584 | 0 | 0.85567 | -0.3187 | -0.3187
1767 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010110 | F11-EXORA BLOCK A LEFT WING | COMMERCIAL | DLMS Meter | 5.3503 | 5.3685 | 0 | 5.3503 | -0.34109 | -0.34109
1768 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010106 | F12-EXORA MLCP BLOCK | COMMERCIAL | DLMS Meter | 3.5543 | 3.5622 | 0 | 3.5543 | -0.22352 | -0.22352
1769 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904020305 | F13-YAMALUR | DOMESTIC | DLMS Meter | 0.28767 | 0.27767 | 0 | 0.28767 | 3.4762 | 5.6938
1770 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904010107 | F14-PLATINA BLOCK-2 | COMMERCIAL | DLMS Meter | 1.8762 | 1.8607 | 0 | 1.8762 | 0.82474 | 0.82474
1771 | BMASZ | SOUTH | KORAMANGALA | S17 | EXORA_66 | 1110203904020303 | F15-KARIYAMMANA AGRAHARA NEW | DOMESTIC | DLMS Meter | 2.6035 | 2.1833 | 0.25788 | 2.3457 | 6.9202 | 7.2894
1772 | BMANZ | NORTH | HEBBAL | C5 | HEBBAL_220 | 1120301901010501 | F16-BABU-REDDY-LAYOUT | DOMESTIC | DLMS Meter | 2.95 | 2.6112 | 0 | 2.95 | 11.4834 | 24.9584
1773 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901010101 | F01-VEMAGAL | AGRI | DLMS Meter | 1.1363 | 1.0223 | 0 | 1.1363 | 10.0403 | 10.0403
1774 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901010102 | F02-CHANDRAHALLI | AGRI | DLMS Meter | 1.3773 | 1.2398 | 0 | 1.3773 | 9.9779 | 9.9779
1775 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901010103 | F03-NELAMACHANHALLI | AGRI | DLMS Meter | 1.1563 | 1.0407 | 0 | 1.1563 | 9.9983 | 9.9983
1776 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901010104 | F04-NJY-GANJIGUNTE | NJY | DLMS Meter | 0.43607 | 0.3819 | 0 | 0.43607 | 12.4231 | 64.3966
1777 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901020305 | F05-MUMMANAHALLI | AGRI | DLMS Meter | 1.2388 | 1.1148 | 0 | 1.2388 | 10.0036 | 10.0036
1778 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901020301 | F06-CHOKKANAHALLI | AGRI | DLMS Meter | 1.6112 | 1.0769 | 0.41462 | 1.1966 | 9.9983 | 9.9983
1779 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901020302 | F07-KORALAPARTHI | AGRI | DLMS Meter | 1.1546 | 1.0391 | 0 | 1.1546 | 10.002 | 10.002
1780 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901020303 | F08-NANDANA-HOSAHALLI | AGRI | DLMS Meter | 1.0747 | 0.83225 | 0.15 | 0.92466 | 9.994 | 9.994
1781 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901010105 | F09-SEETTIHALI | AGRI | DLMS Meter | 0.80284 | 0.72263 | 0 | 0.80284 | 9.9913 | 9.9913
1782 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901020101 | F10-NJY G KURUBARAHALLI | NJY | DLMS Meter | 0.47977 | 0.41982 | 0 | 0.47977 | 12.4953 | 68.3425
1783 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901020304 | F11-PAPATHIMMANAHALLI-(NJY) | NJY | DLMS Meter | 0.5771 | 0.45955 | 0.044977 | 0.53213 | 13.6395 | 65.9687
1784 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901020102 | F12-NJY PALENAHALLI | NJY | DLMS Meter | 0.4975 | 0.45057 | 0 | 0.4975 | 9.4339 | 49.3884
1785 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901010106 | F13-DWARAPALLI | AGRI | DLMS Meter | 0.91716 | 0.82541 | 0 | 0.91716 | 10.0037 | 10.0037
1786 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | GANJIGUNTE_66 | 1230404901020308 | F14-K DEVAGANAHALLI | AGRI | DLMS Meter | 1.1224 | 1.0099 | 0 | 1.1224 | 10.0197 | 10.0197
1787 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901010101 | F01-SOMENAHALII | AGRI | DLMS Meter | 0.4766 | 0.42903 | 0 | 0.4766 | 9.9813 | 9.9813
1788 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901010102 | F02-SRIRAMPURA | NJY | DLMS Meter | 0.62198 | 0.52956 | 0.005 | 0.61698 | 14.1684 | 35.2006
1789 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901010103 | F03-SNERALAKER | AGRI | DLMS Meter | 0.55884 | 0.50303 | 0 | 0.55884 | 9.9864 | 9.9864
1790 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901010104 | F04-KABBLA | AGRI | DLMS Meter | 0.68658 | 0.61806 | 0 | 0.68658 | 9.9796 | 9.9796
1791 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901020301 | F05-BALLALASAMUDRA | NJY | DLMS Meter | 0.8549 | 0.37234 | 0.42 | 0.4349 | 14.3845 | 36.944
1792 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901020302 | F06-GARGA | AGRI | DLMS Meter | 1.1861 | 1.0675 | 0 | 1.1861 | 10.0001 | 10.0001
1793 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901020303 | F07-BELAGUR | NJY | DLMS Meter | 1.0769 | 0.87733 | 0.062 | 1.0149 | 13.5587 | 24.4384
1794 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901020304 | F08-KODIHALLI | AGRI | DLMS Meter | 0.58228 | 0.52388 | 0 | 0.58228 | 10.029 | 10.029
1795 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901010106 | F09-KALKERE | AGRI | DLMS Meter | 1.2466 | 1.1216 | 0 | 1.2466 | 10.0282 | 10.0282
1796 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901010105 | F10-THONACHENAHALLI | AGRI | DLMS Meter | 0.40962 | 0.36881 | 0 | 0.40962 | 9.9629 | 9.9629
1797 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | GARAGA_66 | 1310204901020305 | F11-GAVIRANGAPURA | NJY | DLMS Meter | 0.77092 | 0.66077 | 0 | 0.77092 | 14.2886 | 31.2662
1798 | BMANZ | EAST | SHIVAJINAGAR | E9 | GEDDALAHALLI | 1130305903010103 | F03-HENNUR BANDE | URBAN MIXED LOAD | DLMS Meter | 2.8721 | 2.5641 | 0.21249 | 2.6596 | 3.5911 | 3.5911
1799 | BMANZ | EAST | SHIVAJINAGAR | E9 | GEDDALAHALLI | 1130305903010101 | F04-KRISTHUJAYANTHI COLLEGE | URBAN MIXED LOAD | DLMS Meter | 3.5355 | 3.2629 | 0 | 3.5355 | 7.7096 | 12.6299
1800 | BMANZ | EAST | SHIVAJINAGAR | E8 | GEDDALAHALLI | 1130305903010104 | F05-HANUMANTHA NAGARA | URBAN MIXED LOAD | DLMS Meter | 6.7657 | 5.6927 | 0.52316 | 6.2425 | 8.8071 | 15.7138
1801 | BMANZ | EAST | SHIVAJINAGAR | E9 | GEDDALAHALLI | 1130305903010105 | F06-KOTHANUR | URBAN MIXED LOAD | DLMS Meter | 6.8262 | 6.1147 | 0.22916 | 6.597 | 7.3107 | 11.233
1802 | BMANZ | EAST | SHIVAJINAGAR | E9 | GEDDALAHALLI | 1130305903010201 | F07-BYRATHI | URBAN MIXED LOAD | DLMS Meter | 3.365 | 2.9767 | 0.077686 | 3.2873 | 9.4499 | 21.6501
1803 | BMANZ | EAST | SHIVAJINAGAR | E9 | GEDDALAHALLI | 1130305903010202 | F08-GEDDAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.5522 | 2.1795 | 0.19104 | 2.3612 | 7.693 | 15.1727
1804 | BMANZ | EAST | SHIVAJINAGAR | E9 | GEDDALAHALLI | 1130305903010204 | F09-VADDARAPALYA | URBAN MIXED LOAD | DLMS Meter | 2.8294 | 2.6619 | 0 | 2.8294 | 5.9198 | 15.2957
1805 | BMANZ | EAST | SHIVAJINAGAR | E8 | GEDDALAHALLI | 1130305903010206 | F11-JPNRI | URBAN MIXED LOAD | DLMS Meter | 3.543 | 2.7014 | 0.58312 | 2.9599 | 8.7332 | 15.7286
1806 | BMANZ | EAST | SHIVAJINAGAR | E8 | GEDDALAHALLI | 1130305903010207 | F12-AGARA | URBAN MIXED LOAD | DLMS Meter | 3.612 | 2.6709 | 0.68698 | 2.925 | 8.6853 | 16.4207
1807 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | GEDDALAHALLI | 1130305903010210 | F13-PRESTIGE AUGUSTA | DOMESTIC | DLMS Meter | 0.50828 | 0.4515 | 0.03643 | 0.47185 | 4.3122 | 4.5348
1808 | BMANZ | EAST | SHIVAJINAGAR | E9 | GEDDALAHALLI | 1130305903010209 | F14-MANTRI WEBCITY | DOMESTIC | DLMS Meter | 0.27672 | 0.2566 | 0 | 0.27672 | 7.2682 | 12.4167
1809 | BMANZ | EAST | SHIVAJINAGAR | E9 | GEDDALAHALLI | 1130305903010208 | F15-BWSSB | WATER WORKS | DLMS Meter | 2.9981 | 2.996 | 0 | 2.9981 | 0.070727 | 0.070727
1810 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | GODURU_66 | 1220304909010101 | F01-KANIVE MADAPURA | NJY | DLMS Meter | 0.4029 | 0.20065 | 0.181 | 0.2219 | 9.5777 | 63.7751
1811 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | GODURU_66 | 1220304909010102 | F02-THATTEKERE | AGRI | DLMS Meter | 0.581 | 0.41938 | 0.115 | 0.466 | 10.0045 | 10.0045
1812 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | GODURU_66 | 1220304909010103 | F03-ATTIKUPPE | AGRI | DLMS Meter | 0.481 | 0.3652 | 0.075 | 0.406 | 10.049 | 10.049
1813 | BMANZ | NORTH | JALAHALLI | C3 | GOKULA_66 | 1120203901020301 | F01-K-G-HALLI | URBAN MIXED LOAD | DLMS Meter | 2.3274 | 1.7558 | 0.44 | 1.8874 | 6.9753 | 19.2624
1814 | BMANZ | NORTH | JALAHALLI | C3 | GOKULA_66 | 1120203901020302 | F02-D-B-SANDRA | URBAN MIXED LOAD | DLMS Meter | 2.8426 | 2.5069 | 0.11 | 2.7326 | 8.2611 | 17.1164
1815 | BMANZ | NORTH | JALAHALLI | C3 | GOKULA_66 | 1120203901020303 | F03-BEL-COLONY | URBAN MIXED LOAD | DLMS Meter | 0.7961 | 0.76369 | 0 | 0.7961 | 4.0716 | 4.0716
1816 | BMANZ | NORTH | JALAHALLI | C3 | GOKULA_66 | 1120203901020304 | F04-RAMACHANDRAPURA | URBAN MIXED LOAD | DLMS Meter | 3.1756 | 2.7435 | 0.19 | 2.9856 | 8.1101 | 14.6658
1817 | BMANZ | NORTH | JALAHALLI | C3 | GOKULA_66 | 1120203901010101 | F05-MES-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.3726 | 3.2155 | 0 | 3.3726 | 4.6568 | 7.8705
1818 | BMANZ | NORTH | JALAHALLI | C3 | GOKULA_66 | 1120203901010102 | F06-HMT-INDL-AREA | URBAN MIXED LOAD | DLMS Meter | 1.6987 | 1.4308 | 0.16674 | 1.532 | 6.606 | 7.4212
1819 | BMANZ | NORTH | JALAHALLI | C3 | GOKULA_66 | 1120203901010103 | F07-MK-NAGAR | URBAN MIXED LOAD | DLMS Meter | 1.2344 | 1.0628 | 0.08 | 1.1544 | 7.9356 | 11.3939
1820 | BMANZ | NORTH | PEENYA | N5 | GOKULA_66 | 1120203901010104 | F08-ISRO-LAYOUT | DOMESTIC | DLMS Meter | 0.52105 | 0.32639 | 0.186 | 0.33505 | 2.5832 | 2.5832
1821 | BMANZ | NORTH | JALAHALLI | C3 | GOKULA_66 | 1120203901010105 | F10-CHAMUNDESHWARI-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.4353 | 2.1364 | 0.1634 | 2.2719 | 5.9681 | 14.9174
1822 | BMANZ | NORTH | JALAHALLI | C3 | GOKULA_66 | 1120203901010106 | F11-GOKULA | URBAN MIXED LOAD | DLMS Meter | 1.1202 | 0.94091 | 0.148 | 0.97219 | 3.2175 | 3.2175
1823 | BMANZ | NORTH | JALAHALLI | C9 | GOKULA_66 | 1120203901020305 | F12-PRESTIGE-APPARTMENTS | DOMESTIC | DLMS Meter | 1.9437 | 1.7844 | 0.01 | 1.9337 | 7.7186 | 13.134
1824 | BMANZ | NORTH | JALAHALLI | C3 | GOKULA_66 | 1120203901020306 | F13:MTRDC | COMMERCIAL | DLMS Meter | 0.13213 | 0.13412 | 0 | 0.13213 | -1.5056 | -1.5056
1825 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901010101 | F01-TEXAS-PARK | COMMERCIAL | DLMS Meter | 3.8973 | 3.2846 | 0.4836 | 3.4137 | 3.7822 | 6.1049
1826 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901010102 | F02-MISYS | INDUSTRIAL | DLMS Meter | 0.45037 | 0.31374 | 0.11711 | 0.33326 | 5.8556 | 5.8556
1827 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901010103 | F03-RAMAIHA-REDDY | COMMERCIAL | DLMS Meter | 2.8765 | 2.6576 | 0.1 | 2.7765 | 4.2809 | 5.5466
1828 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901010104 | F04-FIDELITY | INDUSTRIAL | DLMS Meter | 0.79119 | 0.43983 | 0.33733 | 0.45386 | 3.092 | 3.092
1829 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901010105 | F05-IBM-D'-BLOCK | INDUSTRIAL | DLMS Meter | 1.7475 | 1.5455 | 0.14415 | 1.6034 | 3.6112 | 3.6112
1830 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901010106 | F06-FSRIRAM-PROPERTIES | COMMERCIAL | DLMS Meter | 0.40157 | 0.35556 | 0.030258 | 0.37132 | 4.2439 | 4.2439
1831 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901010107 | F07-FDELL | INDUSTRIAL | DLMS Meter | 1.95 | 1.8965 | 0 | 1.95 | 2.7415 | 2.7415
1832 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901020301 | F08-YAHOO | INDUSTRIAL | DLMS Meter | 0.7649 | 0.74241 | 0 | 0.7649 | 2.9411 | 2.9411
1833 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901020302 | F09-24/7 | INDUSTRIAL | DLMS Meter | 2.6157 | 1.5282 | 1.0271 | 1.5887 | 3.8058 | 3.8058
1834 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901020303 | F10-MARUTI-INFOTECH | INDUSTRIAL | DLMS Meter | 1.823 | 1.4605 | 0.30572 | 1.5173 | 3.7448 | 3.7448
1835 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901020304 | F11-COVANSYS | INDUSTRIAL | DLMS Meter | 0.77886 | 0.67033 | 0.086024 | 0.69284 | 3.2484 | 3.2484
1836 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901020305 | F12-CHERRY-HILL | INDUSTRIAL | DLMS Meter | 0.9631 | 0.93021 | 0 | 0.9631 | 3.4146 | 3.4146
1837 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901020306 | F13-SUN-RIVER | INDUSTRIAL | DLMS Meter | 0.58399 | 0.57043 | 0 | 0.58399 | 2.3209 | 2.3209
1838 | BMASZ | SOUTH | KORAMANGALA | S3 | GOLF_LINKS_66 | 1110201901020307 | F15-NET-APP | INDUSTRIAL | DLMS Meter | 0.13907 | 8.3e-05 | 0.13899 | 8.4716e-05 | 2.0251 | 45.6972
1839 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905010101 | F01-PANDOMATTI | AGRI | DLMS Meter | 1.5728 | 1.4145 | 0 | 1.5728 | 10.0649 | 10.0649
1840 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905010102 | F02-MARVANJI | AGRI | DLMS Meter | 1.5026 | 1.1183 | 0.259 | 1.2436 | 10.0763 | 10.0763
1841 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905010103 | F03-SAVEDLU(PANDOMATTINJY) | NJY | DLMS Meter | 1.4197 | 0.63434 | 0.709 | 0.71066 | 10.739 | 38.9638
1842 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905010104 | F04-SAVEHADLU | AGRI | DLMS Meter | 1.4818 | 1.0421 | 0.322 | 1.1598 | 10.1458 | 10.1458
1843 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905020101 | F05-MALAHAL | AGRI | DLMS Meter | 3.2776 | 2.9452 | 0 | 3.2776 | 10.1418 | 10.1418
1844 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905020301 | F06-GOPPENAHALLI | AGRI | DLMS Meter | 1.1382 | 1.0224 | 0 | 1.1382 | 10.1739 | 10.1739
1845 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905020302 | F07-KANCHIGANAL | AGRI | DLMS Meter | 1.4302 | 1.2826 | 0 | 1.4302 | 10.3168 | 10.3168
1846 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905020303 | F08-VADNAL NJY | NJY | DLMS Meter | 0.30228 | 0.18269 | 0.1015 | 0.20078 | 9.0094 | 41.1111
1847 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905020304 | F09-GOPPENAHALLINJY | NJY | DLMS Meter | 2.573 | 0.45232 | 2.065 | 0.50804 | 10.9672 | 43.8538
1848 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905020102 | F10-MARAVANJI TANDA | AGRI | DLMS Meter | 1.0187 | 0.89619 | 0.025 | 0.99372 | 9.8146 | 9.8146
1849 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905020305 | F11-MEDAGUNDANAHALLI | AGRI | DLMS Meter | 1.1548 | 0.84325 | 0.216 | 0.93879 | 10.1772 | 10.1772
1850 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | GOPPENAHALLI_66 | 1310106905010105 | F12-VADNAL | AGRI | DLMS Meter | 2.0985 | 1.8848 | 0 | 2.0985 | 10.1844 | 10.1844
1851 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | GOWNIPALLI_66 | 1230103908010103 | F01-HOSAHUDYA | NJY | DLMS Meter | 0.45413 | 0.41528 | 0 | 0.45413 | 8.5541 | 81.2759
1852 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | GOWNIPALLI_66 | 1230103908010102 | F02-GOWNIPALLI TOWN NJY | NJY | DLMS Meter | 1.8916 | 1.7007 | 0 | 1.8916 | 10.0921 | 71.1031
1853 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | GOWNIPALLI_66 | 1230103908020102 | F04-AVAGANAPALLI | AGRI | DLMS Meter | 0.969 | 0.87224 | 0 | 0.969 | 9.9858 | 9.9858
1854 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | GOWNIPALLI_66 | 1230103908020101 | F09-MARAMPALLI | AGRI | DLMS Meter | 0.4292 | 0.38806 | 0 | 0.4292 | 9.586 | 54.8521
1855 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | GOWNIPALLI_66 | 1230103908010101 | F10-ADHIRAJAPALLI | AGRI | DLMS Meter | 0.6166 | 0.55486 | 0 | 0.6166 | 10.013 | 10.013
1856 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | GOWNIPALLI_66 | 1230103908020103 | F11-BYKOTHURU | AGRI | DLMS Meter | 0.9772 | 0.87958 | 0 | 0.9772 | 9.9899 | 9.9899
1857 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | GOWRASAMUDRA_66 | 1310403901020101 | F02-GOWRASAMUDRA | AGRI | DLMS Meter | 1.1926 | 1.0734 | 0 | 1.1926 | 9.9895 | 9.9895
1858 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | GOWRASAMUDRA_66 | 1310403901020102 | F03-MALLASAMUDRA | AGRI | DLMS Meter | 1.1071 | 0.9751 | 0 | 1.1071 | 11.9195 | 11.9195
1859 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | GOWRASAMUDRA_66 | 1310403901020103 | F04-BUKKAMBUDI | AGRI | DLMS Meter | 1.1214 | 0.99617 | 0 | 1.1214 | 11.1653 | 12.2392
1860 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | GOWRASAMUDRA_66 | 1310403901020104 | F06-NJY BANDETHIMMALAPURA | NJY | DLMS Meter | 0.76963 | 0.58468 | 0.11807 | 0.65156 | 10.2649 | 71.5672
1861 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | GOWRASAMUDRA_66 | 1310403901010301 | F07-HANUMANTHANAHALLI | AGRI | DLMS Meter | 0.5405 | 0.47852 | 0 | 0.5405 | 11.4681 | 11.4681
1862 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | GOWRASAMUDRA_66 | 1310403901010302 | F08-UDEV | AGRI | DLMS Meter | 0.9669 | 0.8368 | 0 | 0.9669 | 13.4551 | 13.4551
1863 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | GOWRASAMUDRA_66 | 1310403901010102 | F11-NJY HONNURU | NJY | DLMS Meter | 0.38631 | 0.34041 | 0 | 0.38631 | 11.8816 | 62.4852
1864 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902010101 | F01-G.B-SANDRA | AGRI | DLMS Meter | 1.1719 | 1.0544 | 0 | 1.1719 | 10.0247 | 10.0247
1865 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902010102 | F02-KADALAVENI | AGRI | DLMS Meter | 1.2685 | 1.1417 | 0 | 1.2685 | 9.9908 | 10.688
1866 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902010103 | F03-MALLASANDRA | AGRI | DLMS Meter | 1.2557 | 0.98618 | 0.16 | 1.0957 | 9.9974 | 9.9974
1867 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902010104 | F04-RAMAPURA | AGRI | DLMS Meter | 0.73852 | 0.66465 | 0 | 0.73852 | 10.0022 | 10.0022
1868 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902010105 | F05-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 1.5907 | 1.4107 | 0.035 | 1.5557 | 9.3192 | 9.3192
1869 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902010106 | F06-V.H-HALLY | AGRI | DLMS Meter | 0.37042 | 0.33329 | 0 | 0.37042 | 10.0246 | 10.0246
1870 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902020302 | F07-CHANDANDUR | AGRI | DLMS Meter | 1.4953 | 1.3457 | 0 | 1.4953 | 10.0051 | 10.0051
1871 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902020303 | F09-NAMAGONDLU | AGRI | DLMS Meter | 0.54868 | 0.16767 | 0.3624 | 0.18628 | 9.9914 | 9.9914
1872 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902020304 | F10-LOCAL | URBAN MIXED LOAD | DLMS Meter | 4.7117 | 4.1355 | 0 | 4.7117 | 12.2287 | 12.2287
1873 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902020305 | F11-KURUBARAHALLY | AGRI | DLMS Meter | 1.0304 | 0.92715 | 0 | 1.0304 | 10.0169 | 10.0169
1874 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902010107 | F13-LOCAL | URBAN MIXED LOAD | DLMS Meter | 4.1525 | 3.582 | 0.0206 | 4.1319 | 13.3091 | 13.3091
1875 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902010108 | F14-NJY-MUDUGERE | NJY | DLMS Meter | 1.0421 | 0.92768 | 0 | 1.0421 | 10.976 | 35.4717
1876 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902010109 | F15-NJY-ALAKAPURA | NJY | DLMS Meter | 1.1833 | 0.95018 | 0.087 | 1.0963 | 13.3271 | 38.0084
1877 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | GOWRIBIDANUR_220 | 1230303902010110 | F16- NJY GEDERE | NJY | DLMS Meter | 0.80098 | 0.70679 | 0 | 0.80098 | 11.759 | 60.8512
1878 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903010101 | F01-GOPALAPURA | AGRI | DLMS Meter | 2.6791 | 2.3611 | 0.021 | 2.6581 | 11.1732 | 11.1732
1879 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903010102 | F02-G.HOSAHALLI | AGRI | DLMS Meter | 2.5064 | 2.2128 | 0 | 2.5064 | 11.711 | 11.711
1880 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903010103 | F03-THIPPUR-NJY | NJY | DLMS Meter | 0.42098 | 0.36033 | 0 | 0.42098 | 14.4066 | 48.2048
1881 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903010104 | F04-SINGONAHALLI | AGRI | DLMS Meter | 1.2081 | 0.98878 | 0.10852 | 1.0996 | 10.0745 | 10.0745
1882 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903010105 | F05-THOREHALLI | AGRI | DLMS Meter | 2.7889 | 2.3797 | 0.089564 | 2.6994 | 11.8426 | 11.8426
1883 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903020301 | F06-IDLE | IDLE | DLMS Meter | 0 | 0.002501 | 0 | 0 | 0 | #DIV/0!
1884 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903020302 | F07-KODIGEHALLI | AGRI | DLMS Meter | 1.9202 | 1.519 | 0.20874 | 1.7114 | 11.245 | 11.245
1885 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903020303 | F08-KOPPA | AGRI | DLMS Meter | 1.745 | 1.4853 | 0.060426 | 1.6846 | 11.8293 | 11.8293
1886 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903020304 | F09-HERUR | AGRI | DLMS Meter | 1.7856 | 1.4372 | 0.16087 | 1.6247 | 11.5441 | 11.5441
1887 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903020305 | F10-M.H.PATNA | AGRI | DLMS Meter | 1.0534 | 0.9456 | 0 | 1.0534 | 10.2331 | 11.4531
1888 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903030501 | F11-UDDEHOSAKERE | AGRI | DLMS Meter | 1.3521 | 1.2166 | 0 | 1.3521 | 10.0202 | 10.0202
1889 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903030502 | F12-HONNAVALLI | AGRI | DLMS Meter | 0.78728 | 0.65715 | 0.040241 | 0.74704 | 12.033 | 13.0422
1890 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903030503 | F13-BIDARE | AGRI | DLMS Meter | 1.5853 | 0.96408 | 0.46875 | 1.1165 | 13.6541 | 13.6541
1891 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903030504 | F14-AMMANAGATTA | AGRI | DLMS Meter | 1.9148 | 1.6941 | 0.025423 | 1.8893 | 10.3342 | 10.3342
1892 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903030505 | F15-GUBBI TOWN | URBAN MIXED LOAD | DLMS Meter | 3.5995 | 2.5864 | 0.58874 | 3.0108 | 14.0956 | 17.8094
1893 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903030506 | F16-KMF | URBAN MIXED LOAD | DLMS Meter | 1.2541 | 1.2317 | 0 | 1.2541 | 1.7837 | 9.1555
1894 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903010106 | F17-THONGNAHALLY NJY | NJY | DLMS Meter | 0.96852 | 0.84187 | 0 | 0.96852 | 13.0764 | 51.0877
1895 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903030507 | F18-DODDKATIGENAHALLI | NJY | DLMS Meter | 0.98347 | 0.90883 | 0 | 0.98347 | 7.5893 | 29.2598
1896 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903030509 | F20-BESCOM SUBDIVISION | URBAN MIXED LOAD | DLMS Meter | 1.0666 | 0.68195 | 0.27652 | 0.79008 | 13.6859 | 16.4888
1897 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903030510 | F21-VADALURU KERE | AGRI | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1898 | CTAZ | TUMKUR | TUMKUR | GUBBI | GUBBI_110 | 1320106903010701 | F24-MADAPURA NJY | NJY | DLMS Meter | 1.076 | 0.95731 | 0 | 1.076 | 11.0306 | 46.7262
1899 | BRAZ | RAMANAGAR | MAGADI | KUDUR | GUDEMARANAHALLI_66 | 1210103903010101 | F01-SOLLUR-. | URBAN MIXED LOAD | DLMS Meter | 1.7584 | 1.2621 | 0.35 | 1.4084 | 10.3916 | 19.098
1900 | BRAZ | RAMANAGAR | MAGADI | KUDUR | GUDEMARANAHALLI_66 | 1210103903010102 | F02-LAKKENAHALLI | AGRI | DLMS Meter | 1.6318 | 1.4686 | 0 | 1.6318 | 9.998 | 9.998
1901 | BRAZ | RAMANAGAR | MAGADI | KUDUR | GUDEMARANAHALLI_66 | 1210103903010103 | F03-GUDEMARANAHALLI | AGRI | DLMS Meter | 1.2918 | 1.1463 | 0 | 1.2918 | 11.2599 | 11.2599
1902 | BRAZ | RAMANAGAR | MAGADI | KUDUR | GUDEMARANAHALLI_66 | 1210103903020301 | F05-SOLLUR-CHILLING-CENTRE | INDUSTRIAL | DLMS Meter | 2.2935 | 2.0636 | 0.012 | 2.2815 | 9.5508 | 9.5508
1903 | BRAZ | RAMANAGAR | MAGADI | KUDUR | GUDEMARANAHALLI_66 | 1210103903020302 | F06-BANAVADI | AGRI | DLMS Meter | 1.5048 | 1.2644 | 0.1 | 1.4048 | 9.9937 | 9.9937
1904 | BRAZ | RAMANAGAR | MAGADI | KUDUR | GUDEMARANAHALLI_66 | 1210103903010105 | F07-CHANNUVALLI | NJY | DLMS Meter | 0.58844 | 0.31451 | 0.24 | 0.34844 | 9.7383 | 45.7194
1905 | BRAZ | RAMANAGAR | MAGADI | KUDUR | GUDEMARANAHALLI_66 | 1210103903020303 | F08-BITTASANDRA | AGRI | DLMS Meter | 1.12 | 0.99062 | 0 | 1.12 | 11.5529 | 11.5529
1906 | BRAZ | RAMANAGAR | MAGADI | KUDUR | GUDEMARANAHALLI_66 | 1210103903010106 | F09-YENNEGERE | NJY | DLMS Meter | 0.5466 | 0.23588 | 0.285 | 0.2616 | 9.8314 | 31.3473
1907 | BRAZ | RAMANAGAR | MAGADI | KUDUR | GUDEMARANAHALLI_66 | 1210103903010104 | F10-HAKKINALU | NJY | DLMS Meter | 0.4764 | 0.42972 | 0.004 | 0.4724 | 9.0338 | 25.1286
1908 | BRAZ | RAMANAGAR | MAGADI | KUDUR | GUDEMARANAHALLI_66 | 1210103903020304 | F11-KORAMANGALA | NJY | DLMS Meter | 0.7034 | 0.43961 | 0.217 | 0.4864 | 9.6191 | 21.7535
1909 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904010101 | F01-HAMPASANDRA | AGRI | DLMS Meter | 1.1263 | 1.0018 | 0.013 | 1.1133 | 10.0153 | 10.0153
1910 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904010102 | F02-BEECHAGANAHALLY | AGRI | DLMS Meter | 0.96558 | 0.86894 | 0 | 0.96558 | 10.0085 | 10.5234
1911 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904010103 | F03-GARUDACHARLAHALLY(NJY) | NJY | DLMS Meter | 1.2027 | 1.0695 | 0.0012 | 1.2015 | 10.9859 | 57.9733
1912 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904010104 | F04-LOCAL | URBAN MIXED LOAD | DLMS Meter | 0.97729 | 0.87318 | 0.016 | 0.96129 | 9.1654 | 11.2422
1913 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904020301 | F05-THIRUMANI NJY | NJY | DLMS Meter | 1.2421 | 0.92899 | 0.19063 | 1.0514 | 11.6452 | 57.7957
1914 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904020302 | F06-POLAMPALLY | AGRI | DLMS Meter | 0.86422 | 0.77784 | 0 | 0.86422 | 9.9947 | 9.9947
1915 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904020303 | F07-RAMAPATNA-NEW | AGRI | DLMS Meter | 0.92282 | 0.83054 | 0 | 0.92282 | 9.9996 | 9.9996
1916 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904020304 | F08-BOGENAHALLY | AGRI | DLMS Meter | 1.34 | 1.206 | 0 | 1.34 | 9.9974 | 9.9974
1917 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904020305 | F09-WATER-WORKS | WATER WORKS | DLMS Meter | 0.25202 | 0.11785 | 0.121 | 0.13102 | 10.0545 | 19.4697
1918 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904020306 | F10-JANGALAHALLI NJY | NJY | DLMS Meter | 0.74572 | 0.60474 | 0.068 | 0.67772 | 10.7682 | 50.9441
1919 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUDIBANDE_66 | 1230304904020307 | F11-VABASANDRA | AGRI | DLMS Meter | 0.36515 | 0.315 | 0.015 | 0.35015 | 10.0388 | 10.0388
1920 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902010101 | F01-YARAGUNTE | AGRI | DLMS Meter | 0.89896 | 0.80911 | 0 | 0.89896 | 9.9948 | 9.9948
1921 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902010102 | F02-CHANNANKUNTE | AGRI | DLMS Meter | 1.0908 | 0.88723 | 0.074818 | 1.016 | 12.6742 | 12.6742
1922 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902010103 | F03-HONNAGONDANAHALLI | AGRI | DLMS Meter | 1.153 | 1.0375 | 0 | 1.153 | 10.0149 | 10.0149
1923 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902010104 | F04-MAGODU | AGRI | DLMS Meter | 0.8663 | 0.7796 | 0 | 0.8663 | 10.0085 | 10.0085
1924 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902020301 | F05-JAVANNAHALLI | AGRI | DLMS Meter | 1.0791 | 0.73985 | 0.22818 | 0.8509 | 13.0508 | 13.0508
1925 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902020101 | F06-GULIGENAHALLI | AGRI | DLMS Meter | 1.1076 | 0.73396 | 0.2669 | 0.84074 | 12.7006 | 12.7006
1926 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902020302 | F07-MUGANAHALLI | AGRI | DLMS Meter | 1.1992 | 0.9145 | 0.15438 | 1.0449 | 12.477 | 12.477
1927 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902020303 | F08-RATHNASANDRA | AGRI | DLMS Meter | 1.8254 | 1.1112 | 0.55378 | 1.2716 | 12.612 | 12.612
1928 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902010105 | F09-AREHALLI-NJY | NJY | DLMS Meter | 0.505 | 0.45498 | 0 | 0.505 | 9.9055 | 54.9601
1929 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902020304 | F10-ANUPANAHALLI-NJY | NJY | DLMS Meter | 0.46994 | 0.41828 | 0 | 0.46994 | 10.9937 | 56.0719
1930 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902020305 | F11-DG-HALLI-NJY | NJY | DLMS Meter | 0.27036 | 0.24265 | 0.003507 | 0.26685 | 9.069 | 57.7546
1931 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902020306 | F12-GUMMANAHALLI | AGRI | DLMS Meter | 0.6542 | 0.57809 | 0 | 0.6542 | 11.6339 | 11.6339
1932 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | GULIGENAHALLI_66 | 1320302902010106 | F13-GIRINATHANAHALLY | AGRI | DLMS Meter | 0.2612 | 0.22992 | 0 | 0.2612 | 11.9774 | 11.9774
1933 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | GUNDAMGERE_66 | 1210101905020101 | F01-GUNDAMGERE | AGRI | DLMS Meter | 0.6871 | 0.61849 | 0 | 0.6871 | 9.9853 | 9.9853
1934 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | GUNDAMGERE_66 | 1210101905010104 | F02-KAMENAHALLI | AGRI | DLMS Meter | 1.1294 | 1.0166 | 0 | 1.1294 | 9.9869 | 9.9869
1935 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | GUNDAMGERE_66 | 1210101905020102 | F03-NELLUKUNTE | AGRI | DLMS Meter | 0.94326 | 0.84878 | 0 | 0.94326 | 10.0163 | 10.0163
1936 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | GUNDAMGERE_66 | 1210101905020103 | F04-SULAKUNTE | AGRI | DLMS Meter | 1.1788 | 1.061 | 0 | 1.1788 | 9.993 | 9.993
1937 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | GUNDAMGERE_66 | 1210101905010101 | F05-UJJANI | AGRI | DLMS Meter | 0.93246 | 0.83933 | 0 | 0.93246 | 9.9872 | 9.9872
1938 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | GUNDAMGERE_66 | 1210101905010102 | F06-HOSAHALLI | AGRI | DLMS Meter | 0.84498 | 0.76121 | 0 | 0.84498 | 9.9138 | 10.7672
1939 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | GUNDAMGERE_66 | 1210101905010103 | F07-AROODI | AGRI | DLMS Meter | 0.94172 | 0.84685 | 0 | 0.94172 | 10.0745 | 10.0745
1940 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | GUNDAMGERE_66 | 1210101905020301 | F08-BANAVATHI | NJY | DLMS Meter | 1.4061 | 0.82805 | 0.465 | 0.94106 | 12.0087 | 50.7292
1941 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | GUNDAMGERE_66 | 1210101905010107 | F09-MAKALI | AGRI | DLMS Meter | 0.7288 | 0.65592 | 0 | 0.7288 | 9.9995 | 9.9995
1942 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | GUNDAMGERE_66 | 1210101905020302 | F10-HANUMANTHAPURA | AGRI | DLMS Meter | 0.9558 | 0.86023 | 0 | 0.9558 | 9.9993 | 9.9993
1943 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUNDLUKOTTUR_66 | 1230304901010101 | F01-KODIHALLI | AGRI | DLMS Meter | 0.96228 | 0.86611 | 0 | 0.96228 | 9.9938 | 9.9938
1944 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUNDLUKOTTUR_66 | 1230304901010102 | F02-NAGARAGERE | AGRI | DLMS Meter | 0.73962 | 0.66565 | 0 | 0.73962 | 10.0004 | 10.0004
1945 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUNDLUKOTTUR_66 | 1230304901010103 | F03-GUDUPALLI | AGRI | DLMS Meter | 0.37306 | 0.33576 | 0 | 0.37306 | 9.9981 | 9.9981
1946 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUNDLUKOTTUR_66 | 1230304901010104 | F04-BANDARLAHALLI NJY | NJY | DLMS Meter | 0.69603 | 0.58425 | 0.046 | 0.65003 | 10.1192 | 56.5187
1947 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUNDLUKOTTUR_66 | 1230304901020301 | F07-YELLODU | AGRI | DLMS Meter | 1.0947 | 0.98504 | 0 | 1.0947 | 10.0179 | 10.0179
1948 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUNDLUKOTTUR_66 | 1230304901020302 | F08-NILUGUMBA NJY | NJY | DLMS Meter | 0.73614 | 0.62462 | 0.039687 | 0.69645 | 10.3143 | 71.5698
1949 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUNDLUKOTTUR_66 | 1230304901020303 | F09-G.KOTHURU NJY | NJY | DLMS Meter | 0.6109 | 0.56443 | 0.0009 | 0.61 | 7.471 | 77.2604
1950 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | GUNDLUKOTTUR_66 | 1230304901020304 | F10-CHOLASHETTYHALLI | AGRI | DLMS Meter | 0.95656 | 0.86083 | 0 | 0.95656 | 10.0075 | 10.0075
1951 | CTAZ | TUMKUR | TIPTUR | TIPTUR | GUNGURUMALE_110 | 1320201903010101 | F01-MUDDANAHALLI | AGRI | DLMS Meter | 0.7374 | 0.5558 | 0.12 | 0.6174 | 9.9765 | 9.9765
1952 | CTAZ | TUMKUR | TIPTUR | TIPTUR | GUNGURUMALE_110 | 1320201903010104 | F02-KASAVANAHALLI | AGRI | DLMS Meter | 0.7472 | 0.56457 | 0.12 | 0.6272 | 9.9855 | 9.9855
1953 | CTAZ | TUMKUR | TIPTUR | TIPTUR | GUNGURUMALE_110 | 1320201903010102 | F03-GUNGURUMALE_NJY | NJY | DLMS Meter | 0.3632 | 0.1862 | 0.149 | 0.2142 | 13.071 | 27.966
1954 | CTAZ | TUMKUR | TIPTUR | TIPTUR | GUNGURUMALE_110 | 1320201903010103 | F04-KALLAHALLI | AGRI | DLMS Meter | 0.7146 | 0.58013 | 0.07 | 0.6446 | 10.0008 | 10.0008
1955 | CTAZ | TUMKUR | TIPTUR | TIPTUR | GUNGURUMALE_110 | 1320201903010105 | F05-ANCHE KOPPALU | AGRI | DLMS Meter | 0.2788 | 0.22285 | 0.031 | 0.2478 | 10.069 | 10.069
1956 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | GURUVINAPURA_66 | 1220303905010101 | F01-BHIMESHWARA | AGRI | DLMS Meter | 1.0746 | 0.82747 | 0.155 | 0.9196 | 10.0187 | 10.0187
1957 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | GURUVINAPURA_66 | 1220303905010102 | F02-GURUVINAPURA NJY | NJY | DLMS Meter | 0.1697 | 0.13408 | 0.0217 | 0.148 | 9.4082 | 56.7551
1958 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | GURUVINAPURA_66 | 1220303905010103 | F03-KUWSSB | WATER WORKS | DLMS Meter | 0.69 | 0.67104 | 0 | 0.69 | 2.7478 | 2.7478
1959 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | GURUVINAPURA_66 | 1220303905010104 | F04-BYADARAHALLI | AGRI | DLMS Meter | 1.594 | 1.4047 | 0.035 | 1.559 | 9.8968 | 9.8968
1960 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | GURUVINAPURA_66 | 1220303905010105 | F05-YALIYURU | AGRI | DLMS Meter | 0.8786 | 0.7677 | 0.02 | 0.8586 | 10.5876 | 10.5876
1961 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | GUTTUR_66 | 1310301902010101 | F02-DOGGALLI | AGRI | DLMS Meter | 0.3166 | 0.28472 | 0 | 0.3166 | 10.0692 | 10.0692
1962 | CTAZ | DAVANAGERE | Harihara | Harihara | GUTTUR_66 | 1310301902010103 | F09-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 2.1619 | 2.0013 | 0 | 2.1619 | 7.4263 | 8.586
1963 | CTAZ | DAVANAGERE | Harihara | Harihara | GUTTUR_66 | 1310301902010302 | F10-HARIHAR | DOMESTIC | DLMS Meter | 2.9977 | 2.6405 | 0.1345 | 2.8632 | 7.7778 | 14.2934
1964 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | GUTTUR_66 | 1310301902020501 | F13-SARATHI | AGRI | DLMS Meter | 0.7609 | 0.68463 | 0 | 0.7609 | 10.0231 | 10.0231
1965 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | GUTTUR_66 | 1310301902020502 | F14-DEETTUR | AGRI | DLMS Meter | 1.265 | 1.1384 | 0 | 1.265 | 10.006 | 10.006
1966 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | GUTTUR_66 | 1310301902020503 | F15-KARLAHALLI | NJY | DLMS Meter | 0.4078 | 0.32375 | 0.056 | 0.3518 | 7.9736 | 47.3766
1967 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | GUTTUR_66 | 1310301902020504 | F16-GANGANARASI | AGRI | DLMS Meter | 0.9246 | 0.8321 | 0 | 0.9246 | 10.0045 | 10.0045
1968 | BRAZ | KOLAR | KGF | MULABAGILU | H_GOLAHALLI_66 | 1230202901010101 | F02-KALKIRE | AGRI | DLMS Meter | 0.81538 | 0.73386 | 0 | 0.81538 | 9.9973 | 9.9973
1969 | BRAZ | KOLAR | KGF | MULABAGILU | H_GOLAHALLI_66 | 1230202901010102 | F03-GUKUNTE | AGRI | DLMS Meter | 0.93918 | 0.84481 | 0 | 0.93918 | 10.0482 | 12.4658
1970 | BRAZ | KOLAR | KGF | MULABAGILU | H_GOLAHALLI_66 | 1230202901010103 | F04-VOMMASANDRA | AGRI | DLMS Meter | 1.2471 | 1.1223 | 0 | 1.2471 | 10.0078 | 10.0078
1971 | BRAZ | KOLAR | KGF | MULABAGILU | H_GOLAHALLI_66 | 1230202901010106 | F05-DUGGASANDRA | AGRI | DLMS Meter | 0.59392 | 0.34536 | 0.2102 | 0.38372 | 9.9961 | 9.9961
1972 | BRAZ | KOLAR | KGF | MULABAGILU | H_GOLAHALLI_66 | 1230202901020304 | F06-MANDIKAL | AGRI | DLMS Meter | 1.0368 | 0.93322 | 0 | 1.0368 | 9.9941 | 9.9941
1973 | BRAZ | KOLAR | KGF | MULABAGILU | H_GOLAHALLI_66 | 1230202901020301 | F07-BISSANAHALLI | AGRI | DLMS Meter | 0.9666 | 0.73127 | 0.154 | 0.8126 | 10.0091 | 10.0091
1974 | BRAZ | KOLAR | KGF | MULABAGILU | H_GOLAHALLI_66 | 1230202901020302 | F08-KOLADEVI-NJY | NJY | DLMS Meter | 1.1501 | 1.0389 | 0 | 1.1501 | 9.6713 | 68.3205
1975 | BRAZ | KOLAR | KGF | MULABAGILU | H_GOLAHALLI_66 | 1230202901020303 | F09-LINGAPURA-NJY | NJY | DLMS Meter | 1.4998 | 1.1229 | 0.2576 | 1.2422 | 9.6091 | 79.0474
1976 | CTAZ | TUMKUR | TUMKUR | NITTUR | HAGALAWADI_66 | 1320107906010201 | F01-MATHIKERE | AGRI | DLMS Meter | 0.75444 | 0.11981 | 0.619 | 0.13544 | 11.538 | 11.538
1977 | CTAZ | TUMKUR | TUMKUR | NITTUR | HAGALAWADI_66 | 1320107906010203 | F02-KUREHALLY | AGRI | DLMS Meter | 1.1853 | 0.78458 | 0.3 | 0.88528 | 11.3745 | 11.3745
1978 | CTAZ | TUMKUR | TUMKUR | NITTUR | HAGALAWADI_66 | 1320107906010202 | F03-HAGALAWADI | NJY | DLMS Meter | 0.72004 | 0.63024 | 0 | 0.72004 | 12.4718 | 53.9239
1979 | BMANZ | EAST | INDIRA NAGAR | E6 | HAL_220 | 1110203905010501 | F01-GEETANJALI | URBAN MIXED LOAD | DLMS Meter | 4.3434 | 3.6915 | 0.46109 | 3.8823 | 4.9157 | 7.194
1980 | BMASZ | SOUTH | KORAMANGALA | S17 | HAL_220 | 1110203905020101 | F02-MARATHAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.4455 | 2.217 | 0.048457 | 2.3971 | 7.5135 | 9.5923
1981 | BMASZ | SOUTH | KORAMANGALA | S17 | HAL_220 | 1110203905020102 | F03-BEML--I. | INDUSTRIAL | DLMS Meter | 0.88563 | 0.88391 | 0 | 0.88563 | 0.19405 | 2.8337
1982 | BMANZ | EAST | INDIRA NAGAR | E6 | HAL_220 | 1110203905010502 | F04-INDRANAGAR | URBAN MIXED LOAD | DLMS Meter | 4.6237 | 3.0734 | 1.3994 | 3.2243 | 4.6783 | 6.378
1983 | BMASZ | SOUTH | KORAMANGALA | S17 | HAL_220 | 1110203905010301 | F05-BEML | INDUSTRIAL | DLMS Meter | 0.10911 | 0.10816 | 0 | 0.10911 | 0.86845 | 0.86845
1984 | BMANZ | EAST | INDIRA NAGAR | E6 | HAL_220 | 1110203905010302 | F06 JB-NAGAR | URBAN MIXED LOAD | DLMS Meter | 5.0939 | 4.1557 | 0.7244 | 4.3695 | 4.8944 | 9.4391
1985 | BMASZ | SOUTH | KORAMANGALA | S3 | HAL_220 | 1110203905010303 | F07-AIRPORT-ROAD | URBAN MIXED LOAD | DLMS Meter | 2.8721 | 2.3175 | 0.46162 | 2.4105 | 3.8595 | 6.27
1986 | BMASZ | SOUTH | KORAMANGALA | S17 | HAL_220 | 1110203905010304 | F08-ADA | URBAN MIXED LOAD | DLMS Meter | 3.0469 | 2.7791 | 0.10787 | 2.939 | 5.4414 | 12.6514
1987 | BMASZ | SOUTH | KORAMANGALA | S3 | HAL_220 | 1110203905020103 | F11-AIRPORT | AIRPORT | DLMS Meter | 0.70536 | 0.66921 | 0.01 | 0.69536 | 3.7607 | 5.8561
1988 | BMASZ | SOUTH | KORAMANGALA | S17 | HAL_220 | 1110203905020104 | F12-TATAHOUSING | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
1989 | BMASZ | SOUTH | KORAMANGALA | S17 | HAL_220 | 1110203905010306 | F13-DODDANAKUNDI | URBAN MIXED LOAD | DLMS Meter | 4.5664 | 3.7229 | 0.51693 | 4.0495 | 8.0646 | 12.7249
1990 | BMASZ | SOUTH | KORAMANGALA | S17 | HAL_220 | 1110203905010307 | F14-MALLESHPALYA | URBAN MIXED LOAD | DLMS Meter | 3.9848 | 3.7741 | 0.010214 | 3.9746 | 5.0443 | 11.5028
1991 | BMASZ | SOUTH | KORAMANGALA | S17 | HAL_220 | 1110203905020105 | F15-DYNASTY | INDUSTRIAL | DLMS Meter | 5.1289 | 5.0336 | 0 | 5.1289 | 1.8574 | 1.8574
1992 | BMASZ | SOUTH | KORAMANGALA | S3 | HAL_220 | 1110203905020106 | F16-IAM-AIRFORCE-RESEARCH-CENTER | DEFENSE ESTABLISHMENT | DLMS Meter | 0.05472 | 0.05238 | 0.0005 | 0.05422 | 3.3943 | 3.3943
1993 | BMASZ | SOUTH | KORAMANGALA | S17 | HAL_220 | 1110203905020107 | F17-RAMESH-NAGAR | URBAN MIXED LOAD | DLMS Meter | 4.6676 | 4.2704 | 0.098574 | 4.569 | 6.5354 | 10.6006
1994 | BMASZ | SOUTH | KORAMANGALA | S17 | HAL_220 | 1110203905020308 | F18-DEFENSE | INDUSTRIAL | DLMS Meter | 1.3522 | 1.334 | 0 | 1.3522 | 1.3478 | 1.3478
1995 | BMANZ | EAST | INDIRA NAGAR | E6 | HAL_220 | 1110203905020307 | F19-LIC-COLONY | URBAN MIXED LOAD | DLMS Meter | 5.2781 | 4.2104 | 0.83366 | 4.4445 | 5.2658 | 9.165
1996 | BMANZ | EAST | INDIRA NAGAR | E10 | HAL_220 | 1110203905010108 | F20-JUDICIAL QUATERS | DOMESTIC | DLMS Meter | 0.2319 | 0.21752 | 0 | 0.2319 | 6.2013 | 19.612
1997 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HALKURKE_110 | 1320201909010102 | F03-IDLE | IDLE | DLMS Meter | 0.11772 | 0.017117 | 0.0987 | 0.01902 | 10.0053 | 10.0053
1998 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HALKURKE_110 | 1320201909010103 | F04-A-M-KAVAL | AGRI | DLMS Meter | 0.64446 | 0.33702 | 0.27 | 0.37446 | 9.9995 | 9.9995
1999 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HALKURKE_110 | 1320201909010104 | F05-HALENAHALLI | AGRI | DLMS Meter | 0.83682 | 0.75306 | 0 | 0.83682 | 10.0094 | 10.0094
2000 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HALKURKE_110 | 1320201909010105 | F06-GATAGINAKERE | AGRI | DLMS Meter | 0.68424 | 0.61572 | 0 | 0.68424 | 10.0143 | 10.4999
2001 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HALKURKE_110 | 1320201909010106 | F07-CHOWLIHALLI | NJY | DLMS Meter | 0.2033 | 0.1745 | 0.004 | 0.1993 | 12.4451 | 42.3944
2002 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HALKURKE_110 | 1320201909010107 | F08-IDLE | IDLE | DLMS Meter | 1.7907 | 1.5955 | 0 | 1.7907 | 10.8994 | 13.4442
2003 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HALKURKE_110 | 1320201909010101 | F09-MUDDENAHALLI | AGRI | DLMS Meter | 0.8578 | 0.772 | 0 | 0.8578 | 10.0024 | 13.1753
2004 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903010101 | F01-HUNAVINODU | AGRI | DLMS Meter | 0.7148 | 0.64332 | 0 | 0.7148 | 10.0001 | 10.0001
2005 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903010102 | F02-DODDAGHATTA | AGRI | DLMS Meter | 0.8546 | 0.76899 | 0 | 0.8546 | 10.0181 | 10.0181
2006 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903020301 | F03-JANKAL | AGRI | DLMS Meter | 1.346 | 1.2114 | 0 | 1.346 | 9.9955 | 9.9955
2007 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903010107 | F04-THANEGEKALLU | AGRI | DLMS Meter | 0.814 | 0.73236 | 0 | 0.814 | 10.03 | 10.03
2008 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903020302 | F05-KANTAPURA | AGRI | DLMS Meter | 0.5435 | 0.48912 | 0 | 0.5435 | 10.0052 | 10.0052
2009 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903010103 | F06-DEVAPURA | AGRI | DLMS Meter | 0.60228 | 0.54198 | 0 | 0.60228 | 10.0125 | 10.0125
2010 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903020303 | F07-RAMAJJANAHALLI | AGRI | DLMS Meter | 0.74794 | 0.67305 | 0 | 0.74794 | 10.0128 | 10.0128
2011 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903020304 | F08-ATTIMAGE | NJY | DLMS Meter | 0.49856 | 0.39495 | 0.051564 | 0.447 | 11.6433 | 27.1199
2012 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903010104 | F09-HONNENAHALLI | NJY | DLMS Meter | 0.401 | 0.25139 | 0.11909 | 0.28191 | 10.827 | 35.415
2013 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903010105 | F10-DUGGAVARA | NJY | DLMS Meter | 0.6564 | 0.20679 | 0.42407 | 0.23233 | 10.9931 | 46.6296
2014 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903010106 | F11-GULIHATTI | AGRI | DLMS Meter | 1.3187 | 1.1865 | 0 | 1.3187 | 10.0223 | 10.0223
2015 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HALURAMESHWARA_66 | 1310204903020305 | F12-BOCHENAHALLI | NJY | DLMS Meter | 0.894 | 0.47603 | 0.35809 | 0.53591 | 11.1742 | 36.2127
2016 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902010101 | F01-TBWS | WATER WORKS | DLMS Meter | 0.59518 | 0.56269 | 0 | 0.59518 | 5.4585 | 98.2818
2017 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902010102 | F03-GARBHAGUDI | AGRI | DLMS Meter | 0.887 | 0.79853 | 0 | 0.887 | 9.9743 | 9.9743
2018 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902010103 | F04-TAVARIGUNDI | AGRI | DLMS Meter | 0.5216 | 0.46925 | 0 | 0.5216 | 10.0368 | 10.0368
2019 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902020303 | F05-NANDYALA | AGRI | DLMS Meter | 1.1307 | 1.0175 | 0 | 1.1307 | 10.0115 | 10.0115
2020 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902020302 | F06-HALAVAGALU NJY | NJY | DLMS Meter | 0.60718 | 0.38271 | 0.1755 | 0.43168 | 11.343 | 43.0925
2021 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902020306 | F07-ANJINAYA IP | AGRI | DLMS Meter | 0.55366 | 0.51336 | 0 | 0.55366 | 7.2787 | 7.2787
2022 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902020304 | F08-MATTURU | AGRI | DLMS Meter | 0.5583 | 0.50226 | 0 | 0.5583 | 10.0374 | 10.0374
2023 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902030101 | F10-ARASANAL | AGRI | DLMS Meter | 0.55794 | 0.50214 | 0 | 0.55794 | 10.0002 | 10.0002
2024 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902030501 | F11-BASAVESHWARA IP | AGRI | DLMS Meter | 0.31516 | 0.28365 | 0 | 0.31516 | 9.9971 | 9.9971
2025 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902030504 | F12-N BASAPURA NJY | NJY | DLMS Meter | 0.33716 | 0.2616 | 0.0546 | 0.28256 | 7.418 | 65.6216
2026 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902030502 | F13-NITTURU | AGRI | DLMS Meter | 0.9359 | 0.84253 | 0 | 0.9359 | 9.9767 | 9.9767
2027 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902010104 | F14-MAHESWARA NJY | NJY | DLMS Meter | 0.70312 | 0.517 | 0.12 | 0.58312 | 11.3397 | 66.79
2028 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902030505 | F15-KUNCHURU IP | AGRI | DLMS Meter | 0.5402 | 0.48609 | 0 | 0.5402 | 10.017 | 10.017
2029 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906010104 | F01-IDLE1 | IDLE | DLMS Meter | 0.1444 | 0.12643 | 0 | 0.1444 | 12.4432 | 12.4432
2030 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906020301 | F02-MOLKALMURU | URBAN MIXED LOAD | DLMS Meter | 2.0082 | 1.7372 | 0 | 2.0082 | 13.4969 | 22.4841
2031 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906020302 | F03-BYRAPURA | AGRI | DLMS Meter | 1.0246 | 0.91174 | 0 | 1.0246 | 11.0153 | 12.5959
2032 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906020303 | F04-HANGAL | AGRI | DLMS Meter | 0.44908 | 0.40399 | 0 | 0.44908 | 10.0414 | 10.5315
2033 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906010101 | F05-MATADAJOGIHALLY | AGRI | DLMS Meter | 1.0116 | 0.85808 | 0.0225 | 0.98906 | 13.2425 | 13.2894
2034 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906010102 | F06-TUKURLAHALLI | AGRI | DLMS Meter | 1.1614 | 1.0454 | 0 | 1.1614 | 9.9867 | 9.9867
2035 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906010103 | F07-KONASAGARA | AGRI | DLMS Meter | 0.5567 | 0.50083 | 0 | 0.5567 | 10.0354 | 10.0354
2036 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906010105 | F08-MARLAHALLI | AGRI | DLMS Meter | 0.7273 | 0.65449 | 0 | 0.7273 | 10.0111 | 10.0111
2037 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906020304 | F09-RDPDAM | WATER WORKS | DLMS Meter | 0.06542 | 0.065653 | 0 | 0.06542 | -0.3554 | -0.3554
2038 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906020305 | F10-HANAGAL-NJY | NJY | DLMS Meter | 0.86678 | 0.76337 | 0 | 0.86678 | 11.9307 | 60.2557
2039 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | HANAGAL_66 | 1310403906010106 | F11-RAYAPURA NJY | NJY | DLMS Meter | 1.3166 | 1.1426 | 0 | 1.3166 | 13.2213 | 60.9842
2040 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906010101 | F02-PURADAKATTE | AGRI | DLMS Meter | 1.279 | 1.1449 | 0 | 1.279 | 10.4816 | 10.4816
2041 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906010102 | F03-BOMMENAHALLI | AGRI | DLMS Meter | 0.6686 | 0.60166 | 0 | 0.6686 | 10.0117 | 10.0117
2042 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906010103 | F04-YENNEGERE | AGRI | DLMS Meter | 1.1245 | 1.0116 | 0 | 1.1245 | 10.0373 | 10.0373
2043 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906010104 | F05-HANDANKERE | AGRI | DLMS Meter | 0.63042 | 0.56736 | 0 | 0.63042 | 10.0022 | 10.0022
2044 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906020301 | F06-KAMALAPURA | AGRI | DLMS Meter | 0.8972 | 0.80717 | 0 | 0.8972 | 10.035 | 10.035
2045 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906020302 | F07-BEVINAHALLI | AGRI | DLMS Meter | 0.8158 | 0.73415 | 0 | 0.8158 | 10.0083 | 10.0083
2046 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906020303 | F08-HARENAHALLI | AGRI | DLMS Meter | 1.0033 | 0.90322 | 0 | 1.0033 | 9.9719 | 9.9719
2047 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906020304 | F09-MATHIGATTA | AGRI | DLMS Meter | 1.6495 | 1.4326 | 0 | 1.6495 | 13.1519 | 13.1519
2048 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906010106 | F10-MALLIGERE-NJY | NJY | DLMS Meter | 0.31538 | 0.28304 | 0 | 0.31538 | 10.2552 | 46.8828
2049 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906020305 | F11-SABBENAHALLI-NJY | NJY | DLMS Meter | 0.42667 | 0.36899 | 0 | 0.42667 | 13.5178 | 48.6413
2050 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906010301 | F12-RANGENAHALLI | AGRI | DLMS Meter | 0.93928 | 0.84571 | 0 | 0.93928 | 9.9615 | 9.9615
2051 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906020306 | F13-RAMAGATTA NJY | NJY | DLMS Meter | 0.5155 | 0.27852 | 0.2 | 0.3155 | 11.7199 | 43.8204
2052 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HANDANKERE_110 | 1320203906020307 | F14-KAIMARA NJY | NJY | DLMS Meter | 0.5457 | 0.47179 | 0 | 0.5457 | 13.5444 | 49.4932
2053 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | HANUMANTHNAGAR_66 | 1220304901020101 | F02-JAIN-COLLAGE-F | URBAN MIXED LOAD | DLMS Meter | 1.0602 | 1.0431 | 0 | 1.0602 | 1.6164 | 1.6164
2054 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | HANUMANTHNAGAR_66 | 1220304901020102 | F03-TOWN | URBAN MIXED LOAD | DLMS Meter | 0.06887 | 0.058321 | 0.0064 | 0.06247 | 6.6416 | 67.2509
2055 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | HANUMANTHNAGAR_66 | 1220304901020104 | F04-THUNGANI | AGRI | DLMS Meter | 0.12852 | 0.11566 | 0 | 0.12852 | 10.0062 | 10.0062
2056 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | HANUMANTHNAGAR_66 | 1220304901020103 | F05-HANUMANTHA-NAGARA-F | AGRI | DLMS Meter | 0.673 | 0.60547 | 0 | 0.673 | 10.034 | 10.034
2057 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | HANUMANTHNAGAR_66 | 1220304901010103 | F06-KIADB PHASE-3 | INDUSTRIAL | DLMS Meter | 0.13544 | 0.12999 | 0 | 0.13544 | 4.0234 | 4.0234
2058 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | HANUMANTHNAGAR_66 | 1220304901010102 | F07-DAYANANDA SAGAR UNIVERSITY-F | HOSPITAL | DLMS Meter | 0.71824 | 0.70279 | 0 | 0.71824 | 2.1511 | 2.1511
2059 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | HANUMANTHNAGAR_66 | 1220304901010301 | F08-KIADB--F | INDUSTRIAL | DLMS Meter | 6.0002 | 3.8899 | 1.959 | 4.0412 | 3.744 | 4.0223
2060 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | HANUMANTHNAGAR_66 | 1220304901010302 | F09-KIADB-F | INDUSTRIAL | DLMS Meter | 5.2472 | 4.4804 | 0.5805 | 4.6667 | 3.9904 | 3.9981
2061 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | HANUMANTHNAGAR_66 | 1220304901010303 | F10-KIRANGERE-F | AGRI | DLMS Meter | 0.72974 | 0.65659 | 0 | 0.72974 | 10.0243 | 10.0243
2062 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | HANUMANTHNAGAR_66 | 1220304901020305 | F12-YADUVANAHALLI | NJY | DLMS Meter | 0.9268 | 0.83709 | 0 | 0.9268 | 9.6797 | 41.2543
2063 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907010101 | F01-BANDRI | AGRI | DLMS Meter | 0.54034 | 0.48615 | 0 | 0.54034 | 10.0283 | 10.0283
2064 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907010104 | F04-HARAKANALU | AGRI | DLMS Meter | 0.88744 | 0.7983 | 0 | 0.88744 | 10.0442 | 10.0442
2065 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907010106 | F06-HPHALLI-RURAL-I.P | AGRI | DLMS Meter | 0.8719 | 0.78495 | 0 | 0.8719 | 9.973 | 9.973
2066 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907010501 | F07-TBWS | WATER WORKS | DLMS Meter | 0.42848 | 0.40755 | 0 | 0.42848 | 4.8856 | 98.3208
2067 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907020301 | F08-KADABAGERINJY | NJY | DLMS Meter | 0.64738 | 0.38029 | 0.223 | 0.42438 | 10.3895 | 48.0288
2068 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907020302 | F09-BAGALI | AGRI | DLMS Meter | 0.99292 | 0.89354 | 0 | 0.99292 | 10.009 | 10.009
2069 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907020303 | F10-KUMARNAHALLI | AGRI | DLMS Meter | 0.98486 | 0.886 | 0 | 0.98486 | 10.0382 | 10.0382
2070 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907020304 | F11-KODIHALLINJY | NJY | DLMS Meter | 0.89456 | 0.64828 | 0.169 | 0.72556 | 10.6507 | 45.5919
2071 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907020305 | F12-KHANAHALLI | AGRI | DLMS Meter | 0.61854 | 0.55676 | 0 | 0.61854 | 9.988 | 9.988
2072 | CTAZ | DAVANAGERE | Harihara | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907010502 | F13-BUS-STAND | DOMESTIC | DLMS Meter | 2.1119 | 1.9949 | 0 | 2.1119 | 5.5396 | 22.9537
2073 | CTAZ | DAVANAGERE | Harihara | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907010503 | F14-I.BCIRCLE | DOMESTIC | DLMS Meter | 1.6244 | 1.5556 | 0.014397 | 1.61 | 3.3773 | 27.5226
2074 | CTAZ | DAVANAGERE | Harihara | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907010504 | F15-KOTTUR ROAD | DOMESTIC | DLMS Meter | 0.58171 | 0.53622 | 0 | 0.58171 | 7.8209 | 29.4412
2075 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907020306 | F16-NICHHAPURA | AGRI | DLMS Meter | 0.83072 | 0.71988 | 0.025 | 0.80572 | 10.6543 | 10.6543
2076 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907020307 | F17-KOOLAHALLI NJY | NJY | DLMS Meter | 0.5269 | 0.35628 | 0.127 | 0.3999 | 10.9087 | 32.349
2077 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | HARAPPANAHALLI_66 | 1310303907010505 | F18-HULIKATTE NJY | NJY | DLMS Meter | 1.3996 | 0.48279 | 0.8595 | 0.5401 | 10.6115 | 46.6109
2078 | CTAZ | DAVANAGERE | Harihara | Harihara | HARIHAR_66 | 1310301901010101 | F01-ANGJANEYA-AGROTECH | DOMESTIC | DLMS Meter | 0.030565 | 0.02877 | 0 | 0.030565 | 5.8746 | 5.8746
2079 | CTAZ | DAVANAGERE | Harihara | Harihara | HARIHAR_66 | 1310301901010102 | F02-BALAJI | INDUSTRIAL | DLMS Meter | 0.98 | 0.8257 | 0.076 | 0.904 | 8.6618 | 36.0791
2080 | CTAZ | DAVANAGERE | Harihara | Harihara | HARIHAR_66 | 1310301901010103 | F03-HARIHARESHWARA | DOMESTIC | DLMS Meter | 1.7801 | 1.3043 | 0.381 | 1.3991 | 6.7765 | 6.7765
2081 | CTAZ | DAVANAGERE | Harihara | Harihara | HARIHAR_66 | 1310301901010104 | F04-VIDYANAGARA | DOMESTIC | DLMS Meter | 3.4388 | 3.0917 | 0.0809 | 3.3579 | 7.9282 | 13.9766
2082 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | HARIHAR_66 | 1310301901020101 | F05-VEERABHADRESHWARA | AGRI | DLMS Meter | 0.8692 | 0.64716 | 0.15 | 0.7192 | 10.0162 | 10.0162
2083 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | HARIHAR_66 | #N/A | F06-IDLE1 | #N/A | DLMS Meter | 17.6447 | 17.6447 | 0 | 17.6447 | 0 | 0
2084 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | HARIHAR_66 | 1310301901020102 | F07-BASAVESHWARA | AGRI | DLMS Meter | 1.9918 | 1.7821 | 0 | 1.9918 | 10.5293 | 10.5293
2085 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | HARIHAR_66 | 1310301901020103 | F08-KIADB-HANAGAVADI | INDUSTRIAL | DLMS Meter | 0.6519 | 0.60409 | 0 | 0.6519 | 7.334 | 12.4219
2086 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | HARIHAR_66 | 1310301901020104 | F09-KNNL-LIFT-IRRIGATION | LIFT IRRIGATION | DLMS Meter | 0.0359 | 0.02195 | 0.013 | 0.0229 | 4.1485 | 4.1485
2087 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | HARIHAR-HOSPET_66 | 1310301907020301 | F05-HARAGANAHALLI | AGRI | DLMS Meter | 0.9867 | 0.8877 | 0 | 0.9867 | 10.0332 | 10.0332
2088 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | HARIHAR-HOSPET_66 | 1310301907020302 | F06-W/W-(RAJ) | WATER WORKS | DLMS Meter | 2.1 | 2.0354 | 0 | 2.1 | 3.0741 | 35.2234
2089 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | HARIHAR-HOSPET_66 | 1310301907020303 | F07-NANDIGAVI | AGRI | DLMS Meter | 1.0568 | 0.95102 | 0 | 1.0568 | 10.0094 | 10.0094
2090 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | HARIHAR-HOSPET_66 | 1310301907020304 | F08-RAJANHALLI | AGRI | DLMS Meter | 0.9928 | 0.6457 | 0.275 | 0.7178 | 10.0443 | 10.0443
2091 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | HARIHAR-HOSPET_66 | 1310301907020305 | F09-BILASANURU NJY | NJY | DLMS Meter | 0.7696 | 0.44702 | 0.2797 | 0.4899 | 8.7522 | 56.0724
2092 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906010101 | F02-CHILLAHALLY | AGRI | DLMS Meter | 1.5536 | 1.3797 | 0 | 1.5536 | 11.1932 | 11.1932
2093 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906010107 | F03-V.K.GUDDA | AGRI | DLMS Meter | 0.895 | 0.7598 | 0.03 | 0.865 | 12.1614 | 12.1614
2094 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906010102 | F04-DHARMAPURA | AGRI | DLMS Meter | 1.7726 | 1.5908 | 0 | 1.7726 | 10.2575 | 10.2575
2095 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906020301 | F05-SUGUR | AGRI | DLMS Meter | 1.5528 | 1.3886 | 0 | 1.5528 | 10.5721 | 10.5721
2096 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906020302 | F06-HOSAKERE | AGRI | DLMS Meter | 1.303 | 1.1678 | 0 | 1.303 | 10.3786 | 10.3786
2097 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906030501 | F07-HOOVINAHOLE | AGRI | DLMS Meter | 1.6539 | 1.4777 | 0 | 1.6539 | 10.6514 | 10.6514
2098 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906030502 | F08-SAKKARA | AGRI | DLMS Meter | 1.6476 | 1.4685 | 0 | 1.6476 | 10.8674 | 10.8674
2099 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906030503 | F09-NJY B.K.HATTY | NJY | DLMS Meter | 0.923 | 0.83473 | 0 | 0.923 | 9.5634 | 51.6439
2100 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906030504 | F10-KANDENAHALLI | AGRI | DLMS Meter | 0.824 | 0.74149 | 0 | 0.824 | 10.0132 | 10.0132
2101 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906010103 | F11-ESHWARAGERE | NJY | DLMS Meter | 0.8438 | 0.77388 | 0 | 0.8438 | 8.286 | 69.9112
2102 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906010104 | F12-NJY HOSAHALLY | NJY | DLMS Meter | 0.41 | 0.37372 | 0 | 0.41 | 8.8495 | 72.4227
2103 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HARIYABBE_66 | 1310401906020303 | F13-KHANAJANAHALLY NJY | NJY | DLMS Meter | 0.3558 | 0.32355 | 0 | 0.3558 | 9.0627 | 64.8704
2104 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902010102 | F01-KOKKAREHOSALLI | AGRI | DLMS Meter | 0.63836 | 0.57441 | 0 | 0.63836 | 10.0167 | 10.0167
2105 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902010105 | F02-HAROBELE | AGRI | DLMS Meter | 0.943 | 0.84867 | 0 | 0.943 | 10.0028 | 10.0028
2106 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902010106 | F03-MULLALLI | AGRI | DLMS Meter | 0.40302 | 0.24173 | 0.13414 | 0.26887 | 10.0929 | 10.0929
2107 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902010107 | F04-YADAMARANAHALLY | AGRI | DLMS Meter | 1.2251 | 1.1028 | 0 | 1.2251 | 9.9826 | 9.9826
2108 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902020301 | F05-SANGAMA | AGRI | DLMS Meter | 1.2752 | 1.1479 | 0 | 1.2752 | 9.9882 | 9.9882
2109 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902010108 | F07-KUNUR | AGRI | DLMS Meter | 0.54608 | 0.3547 | 0.152 | 0.39408 | 9.9916 | 9.9916
2110 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902020302 | F08-HAROBELE--DAM | LIFT IRRIGATION | DLMS Meter | 0.89532 | 0.78483 | 0.08 | 0.81532 | 3.7398 | 95.6554
2111 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902010111 | F09-THAVERGATTE | AGRI | DLMS Meter | 0.63262 | 0.54101 | 0.032 | 0.60062 | 9.9247 | 11.8031
2112 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902010101 | F10-KONTIGERE-DODDI | NJY | DLMS Meter | 0.16778 | 0.12126 | 0.033577 | 0.1342 | 9.6481 | 46.0675
2113 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902010103 | F11-NALLAHALLI-NJY | NJY | DLMS Meter | 0.53228 | 0.33747 | 0.1585 | 0.37378 | 9.7146 | 42.4054
2114 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HAROBELE_66 | 1220303902010104 | F12-MARALE-NJY | NJY | DLMS Meter | 0.42456 | 0.2974 | 0.0955 | 0.32906 | 9.6208 | 64.9842
2115 | BMANZ | EAST | SHIVAJINAGAR | E5 | HBRLAYOUT_66 | 1130305902010101 | F02-LRP-OFFICE | URBAN MIXED LOAD | DLMS Meter | 4.0607 | 3.7726 | 0 | 4.0607 | 7.0948 | 15.3688
2116 | BMANZ | EAST | SHIVAJINAGAR | E5 | HBRLAYOUT_66 | 1130305902020307 | F03-CHANDRIKA-SOAPFACTORY | URBAN MIXED LOAD | DLMS Meter | 2.9116 | 2.6911 | 0 | 2.9116 | 7.5731 | 15.7881
2117 | BMANZ | EAST | SHIVAJINAGAR | E5 | HBRLAYOUT_66 | 1130305902010102 | F04-JAYAKUMAR-RMU | URBAN MIXED LOAD | DLMS Meter | 2.6559 | 2.3241 | 0.16723 | 2.4887 | 6.6154 | 11.5868
2118 | BMANZ | EAST | SHIVAJINAGAR | E5 | HBRLAYOUT_66 | 1130305902010103 | F05-DIVYA-SHANTHI | URBAN MIXED LOAD | DLMS Meter | 3.5087 | 3.1143 | 0.17154 | 3.3372 | 6.6782 | 20.0741
2119 | BMANZ | EAST | SHIVAJINAGAR | E9 | HBRLAYOUT_66 | 1130305902010104 | F06-FGOVINDAPURA | URBAN MIXED LOAD | DLMS Meter | 5.4558 | 4.7694 | 0.29402 | 5.1618 | 7.6018 | 12.6946
2120 | BMANZ | EAST | SHIVAJINAGAR | E9 | HBRLAYOUT_66 | 1130305902020301 | F07-F-BRINDAVAN-NAGAR | URBAN MIXED LOAD | DLMS Meter | 1.1355 | 1.0045 | 0.048155 | 1.0873 | 7.6148 | 11.8046
2121 | BMANZ | EAST | SHIVAJINAGAR | E9 | HBRLAYOUT_66 | 1130305902020304 | F10-K.NARAYANAPURA | URBAN MIXED LOAD | DLMS Meter | 5.5517 | 5.1244 | 0 | 5.5517 | 7.6969 | 16.513
2122 | BMANZ | EAST | SHIVAJINAGAR | E5 | HBRLAYOUT_66 | 1130305902020305 | F11-BYRAVI--APARTMENT | URBAN MIXED LOAD | DLMS Meter | 2.7553 | 2.5889 | 0 | 2.7553 | 6.0423 | 16.136
2123 | BMANZ | EAST | SHIVAJINAGAR | E9 | HBRLAYOUT_66 | 1130305902020306 | F12-HEGDE-NAGAR | URBAN MIXED LOAD | DLMS Meter | 0.62053 | 0 | 0.62053 | 0 | 0 | #DIV/0!
2124 | BMANZ | EAST | SHIVAJINAGAR | E1 | HBRLAYOUT_66 | 1130305902010105 | F13-SHOBHA-CHRYSANTHEMUM | URBAN MIXED LOAD | DLMS Meter | 4.2503 | 3.2776 | 0.57512 | 3.6752 | 10.8201 | 20.205
2125 | BMANZ | EAST | SHIVAJINAGAR | E8 | HBRLAYOUT_66 | 1130305902030502 | F14-KULLAPPA CIRCLE | URBAN MIXED LOAD | DLMS Meter | 3.9184 | 3.2402 | 0.372 | 3.5464 | 8.6345 | 11.0305
2126 | BMANZ | EAST | SHIVAJINAGAR | E8 | HBRLAYOUT_66 | 1130305902030503 | F15-BANGALORE EAST CIRCLE OFFICECLE | URBAN MIXED LOAD | DLMS Meter | 2.9934 | 2.5456 | 0.225 | 2.7684 | 8.0472 | 9.3006
2127 | BMANZ | EAST | SHIVAJINAGAR | E9 | HBRLAYOUT_66 | 1130305902030504 | F16-KARLE | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
2128 | BMANZ | NORTH | HEBBAL | C5 | HBRLAYOUT_66 | 1130305902030505 | F17-GANDHI NAGARA | URBAN MIXED LOAD | DLMS Meter | 2.2453 | 1.9556 | 0 | 2.2453 | 12.9021 | 23.3011
2129 | BMANZ | EAST | SHIVAJINAGAR | E9 | HBRLAYOUT_66 | 1130305902030501 | F18-NAGENAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.8696 | 2.6292 | 0.020039 | 2.8496 | 7.7324 | 13.9761
2130 | BMANZ | NORTH | HEBBAL | C5 | HBRLAYOUT_66 | 1130305902030506 | F19-BMRCL | RAILWAYS OR METRO | DLMS Meter | 0.41141 | 0 | 0.41141 | 2.392e-07 | 0 | #DIV/0!
2131 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902010101 | F01-T-NULENUR | AGRI | DLMS Meter | 0.42172 | 0.38323 | 0 | 0.42172 | 9.1269 | 9.1269
2132 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902010102 | F02-UPPIRGENAHALLI | AGRI | DLMS Meter | 1.626 | 1.4632 | 0 | 1.626 | 10.0113 | 10.0113
2133 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902010103 | F03-BOODIPURA | AGRI | DLMS Meter | 0.97388 | 0.87628 | 0 | 0.97388 | 10.0221 | 10.0221
2134 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902010106 | F04-NALLIKATTE | AGRI | DLMS Meter | 0.67166 | 0.5504 | 0.0356 | 0.63606 | 13.4673 | 13.4673
2135 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902020301 | F05-TALYA | AGRI | DLMS Meter | 2.4032 | 2.1762 | 0 | 2.4032 | 9.4477 | 9.4477
2136 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902010104 | F06-MATHIGATTA | AGRI | DLMS Meter | 0.45538 | 0.40981 | 0 | 0.45538 | 10.0061 | 10.0061
2137 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902010107 | F07-KEREYAGALAHALLI | AGRI | DLMS Meter | 1.265 | 1.0985 | 0 | 1.265 | 13.1625 | 13.1625
2138 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902020302 | F08-CHOWDAGONDANAHALLY | AGRI | DLMS Meter | 0.52176 | 0.46961 | 0 | 0.52176 | 9.9958 | 9.9958
2139 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902020303 | F09-THEKALAVATTY | AGRI | DLMS Meter | 2.5367 | 2.1878 | 0 | 2.5367 | 13.7558 | 13.7558
2140 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902010105 | F10-HULIKERE NJY | NJY | DLMS Meter | 1.2909 | 0.33524 | 0.91213 | 0.37875 | 11.4882 | 37.8587
2141 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HDPURA_66 | 1310203902010108 | F11-KOLAL NJY | NJY | DLMS Meter | 1.5759 | 0.65871 | 0.82316 | 0.75276 | 12.4941 | 45.0352
2142 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010102 | F02-RT-NAGAR | DOMESTIC | DLMS Meter | 4.0722 | 2.9059 | 1 | 3.0722 | 5.4102 | 16.6726
2143 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010505 | F03-SULTAN-PALYA | DOMESTIC | DLMS Meter | 3.8598 | 3.2896 | 0.36 | 3.4998 | 6.0065 | 14.6621
2144 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010601 | F04-IISC | DOMESTIC | DLMS Meter | 4.4356 | 4.0337 | 0.16 | 4.2756 | 5.6576 | 11.5396
2145 | BMANZ | EAST | SHIVAJINAGAR | E1 | HEBBAL_220 | 1120301901010105 | F05-C-STATION | DOMESTIC | DLMS Meter | 5.2208 | 4.6741 | 0 | 5.2208 | 10.4728 | 12.399
2146 | BMANZ | EAST | SHIVAJINAGAR | E1 | HEBBAL_220 | 1120301901010106 | F06 C-STATION | DOMESTIC | DLMS Meter | 5.4033 | 4.6153 | 0.2399 | 5.1634 | 10.6151 | 13.3329
2147 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010107 | F07-GANGA-NAGAR | COMMERCIAL | DLMS Meter | 5.1877 | 4.8588 | 0.1 | 5.0877 | 4.5003 | 15.3716
2148 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010504 | F08-ASTRA-ZENECA | DOMESTIC | DLMS Meter | 3.1855 | 2.972 | 0.1 | 3.0855 | 3.6774 | 13.1828
2149 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010110 | F10-YELAHANKA-RURAL | DOMESTIC | DLMS Meter | 4.2684 | 4.1581 | 0 | 4.2684 | 2.5837 | 11.0501
2150 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010103 | F11-SANJAY-NAGAR | DOMESTIC | DLMS Meter | 2.8104 | 2.4185 | 0.238 | 2.5724 | 5.983 | 20.732
2151 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010503 | F12-BHOOPASANDRA | DOMESTIC | DLMS Meter | 2.1861 | 1.8408 | 0.225 | 1.9611 | 6.1343 | 14.6894
2152 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010113 | F13-VSNL | COMMERCIAL | DLMS Meter | 1.3955 | 1.3981 | 0 | 1.3955 | -0.18742 | 12.3821
2153 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010114 | F14-WHITE-HOUSE | DOMESTIC | DLMS Meter | 2.1676 | 1.6747 | 0.37 | 1.7976 | 6.8374 | 18.4211
2154 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010502 | F15-CHOLANAGAR | DOMESTIC | DLMS Meter | 2.4852 | 2.2477 | 0.07 | 2.4152 | 6.9343 | 17.0639
2155 | BMANZ | NORTH | HEBBAL | C5 | HEBBAL_220 | 1120301901010104 | F17-P&T QUARTERS | DOMESTIC | DLMS Meter | 3.5029 | 3.1456 | 0 | 3.5029 | 10.1999 | 22.8359
2156 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010111 | F18-PRESTIGE SOUTH CITY | URBAN MIXED LOAD | DLMS Meter | 2.7295 | 0.59522 | 2.09 | 0.63946 | 6.9179 | 6.9179
2157 | BMANZ | NORTH | MALLESHWARA | C2 | HEBBAL_220 | 1120301901030601 | F19-C V RAMAN ROAD | URBAN MIXED LOAD | DLMS Meter | 1.7977 | 1.7273 | 0.015 | 1.7827 | 3.1057 | 8.2155
2158 | BMANZ | NORTH | HEBBAL | C5 | HEBBAL_220 | 1120301901030603 | F20-PATEL MUNIYAPPA LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.8915 | 2.977 | 0.53092 | 3.3606 | 11.4144 | 19.6722
2159 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901030602 | F21-MUNESHWAR BLOCK | URBAN MIXED LOAD | DLMS Meter | 2.5688 | 2.2251 | 0.09 | 2.4788 | 10.2319 | 19.9784
2160 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901010112 | F22-EMMBASSY ONE DEVLOPERS | COMMERCIAL | DLMS Meter | 2.3125 | 2.328 | 0 | 2.3125 | -0.67162 | 1.2922
2161 | BMANZ | NORTH | HEBBAL | C4 | HEBBAL_220 | 1120301901030604 | F23-EMBASSY LAKE TERRACES | DOMESTIC | DLMS Meter | 2.8013 | 2.5453 | 0.1 | 2.7013 | 5.7735 | 18.5791
2162 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903010101 | F01-HONASIGERE | AGRI | DLMS Meter | 0.72848 | 0.64983 | 0 | 0.72848 | 10.796 | 10.796
2163 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903010102 | F02-GOVINDARAJAPURA | AGRI | DLMS Meter | 1.4243 | 1.2561 | 0 | 1.4243 | 11.8145 | 11.8145
2164 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903010103 | F03-C-S-PURA | AGRI | DLMS Meter | 1.0618 | 0.94458 | 0 | 1.0618 | 11.0363 | 11.0363
2165 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903020301 | F04-D.G.HALLI-NJY | NJY | DLMS Meter | 0.31908 | 0.27894 | 0 | 0.31908 | 12.5787 | 53.7808
2166 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903020302 | F05-THONDEGERE | AGRI | DLMS Meter | 1.4948 | 1.2281 | 0.105 | 1.3898 | 11.6308 | 11.6308
2167 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903020303 | F06-C-S-TEMPLE | AGRI | DLMS Meter | 1.1458 | 1.0053 | 0 | 1.1458 | 12.261 | 12.261
2168 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903010104 | F07-NAGAVALLI | AGRI | DLMS Meter | 0.94348 | 0.83268 | 0 | 0.94348 | 11.7438 | 11.7438
2169 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903020304 | F08-BEGUR | AGRI | DLMS Meter | 1.0565 | 0.85119 | 0.07 | 0.98652 | 13.7178 | 13.9941
2170 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903020305 | F09-BASAVANAGUDI | AGRI | DLMS Meter | 1.0683 | 0.94225 | 0 | 1.0683 | 11.8011 | 11.8011
2171 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903010105 | F10-SIRVARA-NJY | NJY | DLMS Meter | 1.0144 | 0.72324 | 0.177 | 0.8374 | 13.6321 | 56.1174
2172 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903010106 | F11-R-M-HALLI | AGRI | DLMS Meter | 1.5177 | 1.3362 | 0 | 1.5177 | 11.9573 | 11.9573
2173 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903010107 | F12-BOMMANAHALLI IP | AGRI | DLMS Meter | 1.2374 | 1.0871 | 0 | 1.2374 | 12.1493 | 12.1493
2174 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903020501 | F13-DASARAHALLI NJY | NJY | DLMS Meter | 0.31214 | 0.15724 | 0.13 | 0.18214 | 13.6681 | 55.492
2175 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903020502 | F14-KANAKUPPE | AGRI | DLMS Meter | 1.1554 | 1.0176 | 0 | 1.1554 | 11.9213 | 11.9213
2176 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903020503 | F15-NIDUVALALU -NJY | NJY | DLMS Meter | 0.46863 | 0.26674 | 0.1595 | 0.30913 | 13.7115 | 57.1668
2177 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903020504 | F16-HEBBUR | RURAL MIXED LOAD | DLMS Meter | 1.5445 | 1.3252 | 0 | 1.5445 | 14.1981 | 22.297
2178 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEBBUR_66 | 1320104903010502 | F17-RAYAPURA IP | AGRI | DLMS Meter | 0.9176 | 0.80388 | 0 | 0.9176 | 12.3937 | 12.3937
2179 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEGGERE_66 | 1320104901010101 | F01-VOKKODI | AGRI | DLMS Meter | 0.29324 | 0.26416 | 0 | 0.29324 | 9.9171 | 9.9171
2180 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEGGERE_66 | 1320104901010102 | F02-HEGGERE | RURAL MIXED LOAD | DLMS Meter | 2.0426 | 1.7551 | 0.0242 | 2.0184 | 13.0432 | 29.2553
2181 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEGGERE_66 | 1320104901010103 | F03-SSMC | HOSPITAL | DLMS Meter | 0.68452 | 0.68268 | 0 | 0.68452 | 0.26935 | 0.26935
2182 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEGGERE_66 | 1320104901010104 | F04-MUDIGERE | AGRI | DLMS Meter | 0.72942 | 0.65017 | 0 | 0.72942 | 10.8645 | 10.8645
2183 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEGGERE_66 | 1320104901020301 | F05-GOLLAHALLI COLONY IP | AGRI | DLMS Meter | 0.7847 | 0.69567 | 0 | 0.7847 | 11.3459 | 11.3459
2184 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEGGERE_66 | 1320104901020302 | F06-BHEEMASANDRA TOWN | URBAN MIXED LOAD | DLMS Meter | 1.7814 | 1.4805 | 0.075 | 1.7064 | 13.2384 | 25.6855
2185 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HEGGERE_66 | 1320104901020303 | F07-KANNENAHALLI | AGRI | DLMS Meter | 0.8881 | 0.77875 | 0 | 0.8881 | 12.313 | 12.313
2186 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | HEJJALA_66 | 1220101902010101 | F02-WONDERLA | URBAN MIXED LOAD | DLMS Meter | 1.2094 | 1.1244 | 0 | 1.2094 | 7.0285 | 12.2547
2187 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | HEJJALA_66 | 1220101902010102 | F03-HEJJALA | URBAN MIXED LOAD | DLMS Meter | 1.3304 | 1.2065 | 0 | 1.3304 | 9.3086 | 30.892
2188 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | HEJJALA_66 | 1220101902010103 | F04-BANNIKUPPE | URBAN MIXED LOAD | DLMS Meter | 1.9638 | 1.7792 | 0 | 1.9638 | 9.3969 | 22.4251
2189 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | HEJJALA_66 | 1220101902010104 | F05-GOMTHI | INDUSTRIAL | DLMS Meter | 4.5054 | 4.1191 | 0.1 | 4.4054 | 6.4981 | 6.4981
2190 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | HEJJALA_66 | 1220101902010105 | F06-KADUMANE | URBAN MIXED LOAD | DLMS Meter | 2.3266 | 2.1127 | 0 | 2.3266 | 9.1912 | 12.6993
2191 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | HEJJALA_66 | 1220101902010106 | F07-MANCHANAYAKANAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.9057 | 1.4254 | 0.3307 | 1.575 | 9.5023 | 12.4335
2192 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | HEJJALA_66 | 1220101902020302 | F08-HOSADODDI | AGRI | DLMS Meter | 2.1844 | 1.3622 | 0.67564 | 1.5087 | 9.7145 | 15.118
2193 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | HEJJALA_66 | 1220101902020301 | F10-AVARAGERE | URBAN MIXED LOAD | DLMS Meter | 1.1799 | 1.0772 | 0 | 1.1799 | 8.7059 | 20.5949
2194 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904010101 | F01-YELLADAKERE | AGRI | DLMS Meter | 1.1884 | 1.0695 | 0 | 1.1884 | 10.0078 | 10.0078
2195 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904010102 | F02-MAVINAMADU | AGRI | DLMS Meter | 1.0212 | 0.90233 | 0 | 1.0212 | 11.6404 | 11.6404
2196 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904010103 | F03-RANGAPURA | AGRI | DLMS Meter | 0.90754 | 0.81688 | 0 | 0.90754 | 9.9898 | 10.6524
2197 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904010104 | F04-SOMERAHALLY | AGRI | DLMS Meter | 1.2815 | 1.1534 | 0 | 1.2815 | 9.9915 | 9.9915
2198 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904020301 | F05-ARISHINAGUNDI | AGRI | DLMS Meter | 1.7716 | 1.5904 | 0 | 1.7716 | 10.2237 | 10.2237
2199 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904020302 | F06-V.V.PURA | AGRI | DLMS Meter | 0.9627 | 0.86388 | 0 | 0.9627 | 10.2646 | 10.2646
2200 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904020101 | F07-S.L.RSTEELS | GOVERNMENT OFFICES | DLMS Meter | 0.06408 | 0.059366 | 0 | 0.06408 | 7.3564 | 7.3564
2201 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904020303 | F08-KURUBARAHALLI | AGRI | DLMS Meter | 0.76056 | 0.68456 | 0 | 0.76056 | 9.9925 | 9.9925
2202 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904010105 | F09-NJYSOMERAHALLI | NJY | DLMS Meter | 0.40988 | 0.30992 | 0.064 | 0.34588 | 10.3968 | 35.1445
2203 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904010106 | F10-HULUGULAKUNTE | AGRI | DLMS Meter | 1.0025 | 0.89159 | 0 | 1.0025 | 11.0598 | 11.0598
2204 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904020304 | F11-NJYMAVINAMADU | NJY | DLMS Meter | 0.50946 | 0.45917 | 0 | 0.50946 | 9.8708 | 51.6044
2205 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904020305 | F12-NJYYALLADAKERE | NJY | DLMS Meter | 0.27243 | 0.24258 | 0 | 0.27243 | 10.9558 | 53.0249
2206 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904010107 | F13-CHIGALIKATTE | AGRI | DLMS Meter | 0.92604 | 0.81926 | 0 | 0.92604 | 11.5307 | 11.5307
2207 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HINDASGHATTA_66 | 1310401904010108 | F14-GOWDANAHALLY | AGRI | DLMS Meter | 2.4167 | 2.1396 | 0 | 2.4167 | 11.4657 | 11.4657
2208 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901010101 | F01-HUNASEKATTE | AGRI | DLMS Meter | 1.3697 | 0.96695 | 0.28214 | 1.0876 | 11.0918 | 11.0918
2209 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901010102 | F02-KODAGAVALLI | AGRI | DLMS Meter | 2.5446 | 2.1218 | 0.13869 | 2.4059 | 11.8098 | 11.8098
2210 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901010103 | F03-CHIKPURA | AGRI | DLMS Meter | 1.1982 | 1.0848 | 0 | 1.1982 | 9.4638 | 9.4638
2211 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901010104 | F04-HIREGUNTANUR | AGRI | DLMS Meter | 1.1811 | 1.0459 | 0 | 1.1811 | 11.4477 | 11.4477
2212 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901020301 | F05-BHEMASAMUDRA | AGRI | DLMS Meter | 0.6688 | 0.60177 | 0 | 0.6688 | 10.0218 | 10.0218
2213 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901020302 | F06-VADDARAPALYA | AGRI | DLMS Meter | 1.8827 | 0.67351 | 1.1186 | 0.76407 | 11.8526 | 11.8526
2214 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901020303 | F07-BHEEMESHWARATEMPLE | AGRI | DLMS Meter | 0.70936 | 0.6256 | 0 | 0.70936 | 11.8085 | 11.8085
2215 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901020304 | F08-TUREBAILU CAMP | AGRI | DLMS Meter | 0.73624 | 0.62564 | 0.031134 | 0.70511 | 11.2695 | 11.2695
2216 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901010105 | F09-SEEBARANJY | NJY | DLMS Meter | 1.263 | 0.62864 | 0.53923 | 0.72377 | 13.1436 | 33.3554
2217 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901020305 | F10-BERAVARA--NJY | NJY | DLMS Meter | 0.70631 | 0.33585 | 0.32031 | 0.386 | 12.9922 | 41.0159
2218 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901020308 | F11-N BALLEKATTE | AGRI | DLMS Meter | 1.0671 | 0.61634 | 0.37808 | 0.68904 | 10.5516 | 10.5516
2219 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901020307 | F12-HOSALLI | NJY | DLMS Meter | 0.5232 | 0.12463 | 0.37927 | 0.14393 | 13.4079 | 32.2643
2220 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | HIREGUNTANUR_66 | 1310202901020306 | F13-MALALI | NJY | DLMS Meter | 1.2868 | 0.69928 | 0.48083 | 0.80597 | 13.238 | 29.7799
2221 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902010101 | F01-CIPSA | INDUSTRIAL | DLMS Meter | 1.2355 | 1.1638 | 0 | 1.2355 | 5.8081 | 5.8081
2222 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902010102 | F02-HONNENAHALLI | AGRI | DLMS Meter | 0.76586 | 0.68908 | 0 | 0.76586 | 10.0251 | 11.5903
2223 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902010103 | F03-HARALURU | AGRI | DLMS Meter | 0.60158 | 0.51775 | 0.0254 | 0.57618 | 10.1413 | 16.8472
2224 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902010106 | F04-INCAP | INDUSTRIAL | DLMS Meter | 2.8402 | 2.5654 | 0.0695 | 2.7707 | 7.4099 | 11.1197
2225 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902010104 | F05-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 3.7761 | 3.3011 | 0.181 | 3.5951 | 8.1785 | 11.7866
2226 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902020301 | F06-K-M-HALLI | AGRI | DLMS Meter | 0.88206 | 0.75052 | 0.04815 | 0.83391 | 10 | 10
2227 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902020302 | F07-CARMOBILES | INDUSTRIAL | DLMS Meter | 4.245 | 3.1766 | 0.7317 | 3.5133 | 9.5859 | 12.6642
2228 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902020303 | F08-HIREHALLI | AGRI | DLMS Meter | 0.85884 | 0.73685 | 0.0401 | 0.81874 | 10.0024 | 10.0024
2229 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902020305 | F10-SIDDAGANGA-MATA | COMMERCIAL | DLMS Meter | 0.45054 | 0.15811 | 0.2798 | 0.17074 | 7.396 | 7.396
2230 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902020306 | F11-RAITHARAPALYA | NJY | DLMS Meter | 1.3449 | 1.0297 | 0.2251 | 1.1198 | 8.0446 | 20.6992
2231 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902010105 | F12-NANDIHALLI-NJY | NJY | DLMS Meter | 3.1324 | 2.0591 | 0.8913 | 2.2411 | 8.1218 | 11.8291
2232 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902010108 | F14-RANE WALES | INDUSTRIAL | DLMS Meter | 1.4825 | 1.4262 | 0 | 1.4825 | 3.7989 | 3.7989
2233 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901010101 | F01-CMHOLE | AGRI | DLMS Meter | 0.31541 | 0.28363 | 0 | 0.31541 | 10.0764 | 10.0764
2234 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901010102 | F02-KANAKATTE | AGRI | DLMS Meter | 0.60784 | 0.54699 | 0 | 0.60784 | 10.0105 | 10.0105
2235 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901010104 | F03-SIDDIHALLI | AGRI | DLMS Meter | 0.68673 | 0.61784 | 0 | 0.68673 | 10.0322 | 10.0322
2236 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901010103 | F04-MALLAPURA | AGRI | DLMS Meter | 0.6308 | 0.5675 | 0 | 0.6308 | 10.0355 | 10.0355
2237 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901020301 | F05-KALADEVPURA | AGRI | DLMS Meter | 0.86158 | 0.75123 | 0 | 0.86158 | 12.8075 | 12.8075
2238 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901020302 | F06-BENNEHALLI | AGRI | DLMS Meter | 0.53342 | 0.48015 | 0 | 0.53342 | 9.9856 | 9.9856
2239 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901020303 | F07-BHARAMASAMUDRA | AGRI | DLMS Meter | 0.82836 | 0.74533 | 0 | 0.82836 | 10.024 | 10.024
2240 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901020304 | F08-HOSAHATTI | AGRI | DLMS Meter | 0.35364 | 0.3181 | 0 | 0.35364 | 10.0509 | 10.0509
2241 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901010105 | F09-KAMANDALAGUNDI | NJY | DLMS Meter | 0.3826 | 0.24478 | 0.10393 | 0.27867 | 12.1599 | 46.4261
2242 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901010106 | F10-THIMLAPURA | NJY | DLMS Meter | 0.5576 | 0.36844 | 0.13794 | 0.41966 | 12.2058 | 32.4331
2243 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | HIREMALLANAHOLE_66 | 1310105901020305 | F11-SANGENAHALLI | NJY | DLMS Meter | 0.8644 | 0.63182 | 0.14087 | 0.72353 | 12.6758 | 38.1519
2244 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905010101 | F02-RANGENAHALLI | AGRI | DLMS Meter | 1.3725 | 1.217 | 0 | 1.3725 | 11.3292 | 11.3292
2245 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905010102 | F03-BEERANAHALLI | AGRI | DLMS Meter | 1.1031 | 0.99179 | 0 | 1.1031 | 10.0938 | 10.0938
2246 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905010103 | F04-VVPURA | AGRI | DLMS Meter | 1.2592 | 1.1333 | 0 | 1.2592 | 10.0025 | 10.0025
2247 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905020301 | F05-BYDRAHALLY | AGRI | DLMS Meter | 0 | 6e-06 | 0 | 0 | 0 | #DIV/0!
2248 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905020302 | F06-HARANKATTE | AGRI | DLMS Meter | 0.47164 | 0.42429 | 0 | 0.47164 | 10.0399 | 10.0399
2249 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905020303 | F08-MASKAL | AGRI | DLMS Meter | 0.86454 | 0.77687 | 0 | 0.86454 | 10.1404 | 10.1404
2250 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905010104 | F09-GANNAYAKANAHALLI | AGRI | DLMS Meter | 0.01326 | 0.011866 | 0 | 0.01326 | 10.5128 | 36.3322
2251 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905010105 | F10-NJYBEERANAHALLI | NJY | DLMS Meter | 0.66624 | 0.60406 | 0 | 0.66624 | 9.3332 | 46.7804
2252 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905020304 | F11-NJYHEMADALA | NJY | DLMS Meter | 0.10069 | 0.091808 | 0 | 0.10069 | 8.8214 | 30.4118
2253 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905020305 | F12-NJYMALLENU | NJY | DLMS Meter | 0.35669 | 0.3258 | 0 | 0.35669 | 8.6595 | 44.651
2254 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_220 | 1310401905010107 | F13-NANDIHALLY NJY | NJY | DLMS Meter | 0.90198 | 0.80967 | 0 | 0.90198 | 10.235 | 30.4301
2255 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_66 | #N/A | F02-NJY LAKAVANAHALLI | #N/A | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
2256 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_66 | 1310401902010101 | F03-NJYDODDAGHATTA | NJY | DLMS Meter | 0.13916 | 0.12823 | 0 | 0.13916 | 7.851 | 41.1875
2257 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_66 | 1310401902010102 | F04-ADIVALA | AGRI | DLMS Meter | 0.80902 | 0.72825 | 0 | 0.80902 | 9.9842 | 9.9842
2258 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_66 | 1310401902020101 | F05-HIRIYURBYPASS | URBAN MIXED LOAD | DLMS Meter | 2.9215 | 2.6058 | 0.10256 | 2.8189 | 7.5606 | 15.4612
2259 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_66 | 1310401902020301 | F06-PGCL+WW | WATER WORKS | DLMS Meter | 0.523 | 0.49874 | 0 | 0.523 | 4.6383 | 9.0218
2260 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_66 | 1310401902020302 | F07-LAKKAVANAHALLI | AGRI | DLMS Meter | 1.1626 | 1.0438 | 0 | 1.1626 | 10.2179 | 10.2179
2261 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_66 | 1310401902020303 | F08-HABIB | RURAL MIXED LOAD | DLMS Meter | 1.9761 | 1.7722 | 0 | 1.9761 | 10.3152 | 11.9796
2262 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_66 | 1310401902010103 | F09-HULIYURROAD | URBAN MIXED LOAD | DLMS Meter | 4.024 | 3.251 | 0.42879 | 3.5952 | 9.5717 | 19.001
2263 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_66 | 1310401902010106 | F10-HORTICULTURE COLLAGE | GOVERNMENT OFFICES | DLMS Meter | 0.75487 | 0.33212 | 0.39483 | 0.36005 | 7.7551 | 40.4372
2264 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903010101 | F01-CHANNAPATNA | AGRI | DLMS Meter | 0.65496 | 0.5891 | 0 | 0.65496 | 10.0554 | 10.0554
2265 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903010102 | F02-ADNUR | AGRI | DLMS Meter | 1.1307 | 1.0176 | 0 | 1.1307 | 10.0025 | 10.0025
2266 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903010103 | F04-ARENAHALLI | AGRI | DLMS Meter | 0.98096 | 0.86635 | 0 | 0.98096 | 11.6831 | 11.6831
2267 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903010104 | F05-APPARASANAHHALLI | AGRI | DLMS Meter | 0.81322 | 0.59025 | 0.128 | 0.68522 | 13.8601 | 13.8601
2268 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903020301 | F06-HOLALKERE | URBAN MIXED LOAD | DLMS Meter | 1.776 | 1.5008 | 0.081805 | 1.6942 | 11.4117 | 11.4117
2269 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903020101 | F07-MADDERUS | AGRI | DLMS Meter | 1.0947 | 0.98522 | 0 | 1.0947 | 10.0045 | 10.0045
2270 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903020102 | F08-BOMANKATTE | AGRI | DLMS Meter | 1.6064 | 1.4457 | 0 | 1.6064 | 10.0059 | 10.0059
2271 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903020103 | F09-GILIKENAHALLI | AGRI | DLMS Meter | 1.0086 | 0.8928 | 0 | 1.0086 | 11.4808 | 11.4808
2272 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903030503 | F12-NGHALLI | AGRI | DLMS Meter | 2.1684 | 1.9608 | 0 | 2.1684 | 9.5753 | 9.5753
2273 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903030504 | F13-GUNDERI | AGRI | DLMS Meter | 1.8599 | 1.6012 | 0 | 1.8599 | 13.9054 | 13.9054
2274 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903030505 | F14-MALENAHALLI NJY | NJY | DLMS Meter | 0.54875 | 0.25939 | 0.25511 | 0.29364 | 11.6632 | 36.6223
2275 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903030506 | F15-PUNAGURU | AGRI | DLMS Meter | 0.80785 | 0.72683 | 0 | 0.80785 | 10.0297 | 10.0297
2276 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903020302 | F16-LOKADOLALU NJY | NJY | DLMS Meter | 0.85922 | 0.39076 | 0.41147 | 0.44775 | 12.7297 | 39.0448
2277 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903010301 | F17-CHEERANAHALLI NJY | NJY | DLMS Meter | 0.8664 | 0.56948 | 0.21138 | 0.65502 | 13.0593 | 48.1476
2278 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | HOLALKERE_66 | 1310203903030507 | F18-RAMAGIRI ROAD | AGRI | DLMS Meter | 0.55792 | 0.50208 | 0 | 0.55792 | 10.0091 | 10.0091
2279 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902010104 | F01-CHIKKAVALLI | AGRI | DLMS Meter | 1.2066 | 1.0857 | 0 | 1.2066 | 10.0136 | 10.4032
2280 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902010101 | F02-HOLAVANAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.2289 | 0.55668 | 0.64 | 0.58892 | 5.4739 | 32.2791
2281 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902010102 | F03-THOGARIGATTHA | AGRI | DLMS Meter | 1.1509 | 1.0358 | 0 | 1.1509 | 10.0062 | 10.0062
2282 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902010103 | F04-HULIKUNTE | AGRI | DLMS Meter | 1.343 | 1.1975 | 0 | 1.343 | 10.8337 | 13.2487
2283 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902020301 | F05-SOMPURA | AGRI | DLMS Meter | 1.3228 | 1.1902 | 0 | 1.3228 | 10.0306 | 11.8257
2284 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902020302 | F06-KODLAHALLI | AGRI | DLMS Meter | 1.4239 | 1.2802 | 0 | 1.4239 | 10.0979 | 10.2902
2285 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902020303 | F07-B.D-PURA | AGRI | DLMS Meter | 1.9485 | 1.7533 | 0 | 1.9485 | 10.0199 | 35.8593
2286 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902020304 | F08-HV-PALYA | AGRI | DLMS Meter | 1.3447 | 1.0173 | 0.21 | 1.1347 | 10.3423 | 13.6489
2287 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902010301 | F09-SUVARNAMUKHI | NJY | DLMS Meter | 0.47326 | 0.1595 | 0.299 | 0.17426 | 8.4718 | 29.0625
2288 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902020305 | F10-B.D-PURA-NJY | NJY | DLMS Meter | 0.91632 | 0.26357 | 0.626 | 0.29032 | 9.2139 | 61.9756
2289 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902010105 | F11-GODDARAHALLY | NJY | DLMS Meter | 0.5284 | 0.35157 | 0.141 | 0.3874 | 9.2494 | 49.3549
2290 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | HOLAVINAHALLY_66 | 1320305902010106 | F12-KYAMENAHALLY | NJY | DLMS Meter | 0.457 | 0.26852 | 0.161 | 0.296 | 9.2854 | 24.7392
2291 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904020303 | F01-ARAKERE | AGRI | DLMS Meter | 1.6325 | 1.4756 | 0 | 1.6325 | 9.6141 | 9.6141
2292 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904030501 | F02-BALLESWARA | AGRI | DLMS Meter | 1.7096 | 1.5382 | 0 | 1.7096 | 10.0257 | 10.0257
2293 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904030502 | F03-HONNALI | DOMESTIC | DLMS Meter | 2.1793 | 1.9981 | 0 | 2.1793 | 8.3166 | 16.2007
2294 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904020301 | F05-MARIKOPPA | AGRI | DLMS Meter | 1.3253 | 1.1961 | 0 | 1.3253 | 9.7493 | 9.7493
2295 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904020302 | F06-HANUMASAGARA | NJY | DLMS Meter | 1.465 | 0.34529 | 1.0784 | 0.38663 | 10.692 | 33.9605
2296 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904010101 | F07-GOLLARAHALLI | DOMESTIC | DLMS Meter | 0.96924 | 0.66231 | 0.24468 | 0.72456 | 8.5913 | 31.4386
2297 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904020101 | F08-ARABAGATTE | AGRI | DLMS Meter | 1.1028 | 0.99352 | 0 | 1.1028 | 9.9073 | 9.9073
2298 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904010102 | F09-BELIMALLUR | AGRI | DLMS Meter | 1.5265 | 1.3767 | 0 | 1.5265 | 9.8151 | 9.8151
2299 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904010103 | F10-VADDARAHATTI | AGRI | DLMS Meter | 1.4199 | 1.2779 | 0 | 1.4199 | 10.0014 | 10.0014
2300 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904010104 | F11-HIREGONIGERE | NJY | DLMS Meter | 2.4914 | 0.82989 | 1.5659 | 0.92552 | 10.333 | 52.9897
2301 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALI_66 | 1310302904030503 | F13-UGD HONNALI | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
2302 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALLI_220 | 1310302905010101 | F01-KAMMARGATTE | AGRI | DLMS Meter | 1.054 | 0.9518 | 0 | 1.054 | 9.6969 | 9.6969
2303 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALLI_220 | 1310302905010102 | F02-TARAGANAHALLI | AGRI | DLMS Meter | 1.1284 | 1.0182 | 0 | 1.1284 | 9.7628 | 9.7628
2304 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALLI_220 | 1310302905010103 | F03-HARALAHALLI | AGRI | DLMS Meter | 0.96067 | 0.86489 | 0 | 0.96067 | 9.9698 | 9.9698
2305 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALLI_220 | 1310302905010104 | F04-GOVINAKOVI | NJY | DLMS Meter | 1.0845 | 0.5188 | 0.50417 | 0.58033 | 10.6031 | 36.5539
2306 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALLI_220 | 1310302905020301 | F07-GADDERAMESHWARA | AGRI | DLMS Meter | 0.43536 | 0.37435 | 0.02062 | 0.41474 | 9.7394 | 9.7394
2307 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALLI_220 | 1310302905010105 | F08-TUNGABHADRA | AGRI | DLMS Meter | 1.0204 | 0.91842 | 0 | 1.0204 | 9.996 | 9.996
2308 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALLI_220 | 1310302905020302 | F09-BASAVAPURA | AGRI | DLMS Meter | 0.90184 | 0.81215 | 0 | 0.90184 | 9.9454 | 9.9454
2309 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALLI_220 | 1310302905020303 | F10-HOLEMADAPURA | AGRI | DLMS Meter | 0.68732 | 0.61918 | 0 | 0.68732 | 9.9139 | 9.9139
2310 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | HONNALLI_220 | 1310302905010107 | F11-TAKKANAHALLI NJY | NJY | DLMS Meter | 0.8115 | 0.45037 | 0.30881 | 0.50269 | 10.4077 | 40.4106
2311 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906010101 | F01-THIMLAPURA | AGRI | DLMS Meter | 1.5021 | 1.3518 | 0 | 1.5021 | 10.0055 | 10.0055
2312 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906010102 | F02-KONEHALLI | AGRI | DLMS Meter | 1.3389 | 1.2047 | 0 | 1.3389 | 10.0238 | 10.0238
2313 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906010103 | F03-NJY-BIDRAGUDI | NJY | DLMS Meter | 0.70972 | 0.62818 | 0 | 0.70972 | 11.4888 | 28.4296
2314 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906010104 | F04-NAGATHIHALLI | AGRI | DLMS Meter | 0.86664 | 0.78018 | 0 | 0.86664 | 9.9766 | 9.9766
2315 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906020302 | F05-HULIHALLI | NJY | DLMS Meter | 0.6448 | 0.5697 | 0 | 0.6448 | 11.6469 | 41.1202
2316 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906020101 | F06-HOSAPATNA | AGRI | DLMS Meter | 0.8802 | 0.792 | 0 | 0.8802 | 10.0207 | 10.4562
2317 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906020102 | F07-NJY-HONNAVALLI | NJY | DLMS Meter | 0.31498 | 0.26806 | 0.001 | 0.31398 | 14.6255 | 37.5306
2318 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906020103 | F08-BALUVANERALU | AGRI | DLMS Meter | 0.84516 | 0.76068 | 0 | 0.84516 | 9.9957 | 9.9957
2319 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906020104 | F09-PATREHALLI | AGRI | DLMS Meter | 0.77248 | 0.62294 | 0.08 | 0.69248 | 10.0417 | 10.5499
2320 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906010105 | F10-RUDRAPURA | AGRI | DLMS Meter | 0.9054 | 0.81488 | 0 | 0.9054 | 9.9981 | 9.9981
2321 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HONNAVALLI_110 | 1320201906020301 | F11-GUDIGONDANAHALLI | NJY | DLMS Meter | 0.24169 | 0.20737 | 0.005 | 0.23669 | 12.3885 | 53.5003
2322 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HONNENAHALLI_66 | 1320104906010101 | F01-VADERAPURA IP | AGRI | DLMS Meter | 0.7718 | 0.6882 | 0 | 0.7718 | 10.8321 | 10.8321
2323 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HONNENAHALLI_66 | 1320104906010104 | F02-HONNENAHALLI IP | AGRI | DLMS Meter | 0.6904 | 0.27005 | 0.387 | 0.3034 | 10.9931 | 10.9931
2324 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HONNENAHALLI_66 | 1320104906010102 | F03-KARENAHALLI IP | AGRI | DLMS Meter | 0.8608 | 0.47282 | 0.3255 | 0.5353 | 11.671 | 22.67
2325 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | HONNENAHALLI_66 | 1320104906010103 | F04-HONASIGERE IP | AGRI | DLMS Meter | 0.9732 | 0.68908 | 0.19 | 0.7832 | 12.0169 | 12.0169
2326 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901020301 | F01-SATHNUR | AGRI | DLMS Meter | 0.71728 | 0.64547 | 0 | 0.71728 | 10.012 | 10.012
2327 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901020302 | F02-DALIMBA | AGRI | DLMS Meter | 0.82298 | 0.74062 | 0 | 0.82298 | 10.0075 | 10.0075
2328 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901010101 | F03-KANCHANAHALLY | AGRI | DLMS Meter | 0.47775 | 0.32256 | 0.11939 | 0.35836 | 9.9891 | 9.9891
2329 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901010102 | F04-KABBALU | AGRI | DLMS Meter | 1.0486 | 0.88789 | 0.062 | 0.98656 | 10.0017 | 10.0017
2330 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901020303 | F05-HARIHARA | AGRI | DLMS Meter | 0.56143 | 0.50525 | 0 | 0.56143 | 10.0066 | 10.0066
2331 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901020304 | F06-HONNIGANAHALLI | NJY | DLMS Meter | 0.10216 | 0.07434 | 0.02 | 0.08216 | 9.5186 | 20.3142
2332 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901010103 | F08-KADAHALLI | AGRI | DLMS Meter | 0.97738 | 0.81332 | 0.075 | 0.90238 | 9.8695 | 9.8695
2333 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901020305 | F10-BHOOHALLI | NJY | DLMS Meter | 0.53514 | 0.37778 | 0.118 | 0.41714 | 9.4365 | 34.7328
2334 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901020306 | F11-KAMSAGARA | NJY | DLMS Meter | 0.4064 | 0.3583 | 0.0152 | 0.3912 | 8.4109 | 31.7699
2335 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901010301 | F12-SATHANUR NJY | NJY | DLMS Meter | 0.66982 | 0.51284 | 0.102 | 0.56782 | 9.6819 | 32.3644
2336 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | HONNIGANAHALLI_66 | 1220303901020307 | F13-HALASINAMARADODDI NJY | NJY | DLMS Meter | 0.2026 | 0.19853 | 0 | 0.2026 | 2.0074 | 2.7812
2337 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903010101 | F01-THAVAREKERE | AGRI | DLMS Meter | 1.4364 | 0.90103 | 0.4351 | 1.0013 | 10.0102 | 10.0102
2338 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903010102 | F02-MULUKUNTE | AGRI | DLMS Meter | 0.91934 | 0.80427 | 0.0256 | 0.89374 | 10.0104 | 10.0104
2339 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903010103 | F03-HONNUDIKE | AGRI | DLMS Meter | 0.7842 | 0.67864 | 0.0301 | 0.7541 | 10.0065 | 10.0065
2340 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903010104 | F04-SASALU | AGRI | DLMS Meter | 0.80569 | 0.61236 | 0.1253 | 0.68039 | 9.9991 | 9.9991
2341 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903010105 | F05-HOLAKALLU | AGRI | DLMS Meter | 1.2888 | 1.1373 | 0.025 | 1.2638 | 10.0098 | 10.0098
2342 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903020301 | F06-CHOLAMBALLI | AGRI | DLMS Meter | 0.81276 | 0.70859 | 0.0252 | 0.78756 | 10.0273 | 12.397
2343 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903020302 | F07-VIRUPASANDRA | AGRI | DLMS Meter | 1.1666 | 0.9196 | 0.1435 | 1.0231 | 10.1179 | 10.1179
2344 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903020303 | F08-HONNUDIKE-NJY | NJY | DLMS Meter | 1.0879 | 0.82307 | 0.2046 | 0.88328 | 6.8172 | 43.3095
2345 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903020304 | F09-CNNL | WATER WORKS | DLMS Meter | 0.7366 | 0.007875 | 0.72794 | 0.00866 | 9.0647 | 9.0647
2346 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903020305 | F10-HOLAKALLU-NJY | NJY | DLMS Meter | 0.54154 | 0.26324 | 0.2554 | 0.28614 | 8.0024 | 49.3963
2347 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903020306 | F11-ARENAHALLI | NJY | DLMS Meter | 0.43116 | 0.33773 | 0.0684 | 0.36276 | 6.8999 | 57.1547
2348 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903020307 | F12-MAASKAL | NJY | DLMS Meter | 0.44563 | 0.39527 | 0.0196 | 0.42603 | 7.2195 | 34.0628
2349 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903010301 | F13-VAHINI PIPES | INDUSTRIAL | DLMS Meter | 2.6383 | 2.6706 | 0 | 2.6383 | -1.2243 | -1.2243
2350 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903020308 | F14-JOLUMARANAHALLI | AGRI | DLMS Meter | 0.8486 | 0.75024 | 0.0151 | 0.8335 | 9.9897 | 9.9897
2351 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HONNUDIKE_66 | 1320105903020309 | F16-PANDITHANAHALLI IP | AGRI | DLMS Meter | 1.113 | 0.58864 | 0.4591 | 0.6539 | 9.98 | 13.2004
2352 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020101 | F03-E.P.I.P | URBAN MIXED LOAD | DLMS Meter | 3.2337 | 1.968 | 1.125 | 2.1087 | 6.6709 | 13.5898
2353 | BMANZ | EAST | WHITEFIELD | E7 | HOODY_220 | 1130202903020102 | F04-E.P.I.P | URBAN MIXED LOAD | DLMS Meter | 3.3689 | 2.3875 | 0.81086 | 2.5581 | 6.6669 | 13.5318
2354 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020103 | F05-HOODY | URBAN MIXED LOAD | DLMS Meter | 3.9947 | 2.8378 | 1.0322 | 2.9626 | 4.212 | 12.4298
2355 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020104 | F06-FSEETHARAMPALYA | URBAN MIXED LOAD | DLMS Meter | 3.3072 | 3.0714 | 0.19094 | 3.1162 | 1.439 | 6.6847
2356 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020301 | F07-FD.KUNDALAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.8403 | 1.9075 | 0.82233 | 2.018 | 5.4782 | 11.9579
2357 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020302 | F08-I.T.I-AUXILLARY | INDUSTRIAL | DLMS Meter | 3.7916 | 3.2657 | 0.35561 | 3.436 | 4.9569 | 15.4338
2358 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020105 | F09-G.C-PALYA | URBAN MIXED LOAD | DLMS Meter | 3.61 | 3.5445 | 0 | 3.61 | 1.8152 | 6.3763
2359 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020303 | F10-R.H.B-COLONY | DOMESTIC | DLMS Meter | 3.4294 | 3.3202 | 0 | 3.4294 | 3.1848 | 10.8665
2360 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020304 | F11-PHEONIX-MALL | COMMERCIAL | DLMS Meter | 1.2514 | 0.51733 | 0.70543 | 0.54599 | 5.2481 | 18.4709
2361 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020402 | F13-SAP-LAB | COMMERCIAL | DLMS Meter | 0.4 | 0.36822 | 0 | 0.4 | 7.945 | #DIV/0!
2362 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020305 | F14-BIP-DEVELOPERS | COMMERCIAL | DLMS Meter | 1.0832 | 0.80442 | 0.24634 | 0.8369 | 3.8815 | 8.2446
2363 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020201 | F15-M/S.KIADB-(DODDANAKKUNDI-I/A) | URBAN MIXED LOAD | DLMS Meter | 7.2201 | 6.3403 | 0.70951 | 6.5106 | 2.6152 | 5.2276
2364 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020306 | F16-M/S.L&T-FEEDER | INDUSTRIAL | DLMS Meter | 0.75987 | 0.74699 | 0 | 0.75987 | 1.6942 | 4.2552
2365 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020403 | F18-SIPANI-FIBRES | INDUSTRIAL | DLMS Meter | 0.0034854 | 0.003331 | 0 | 0.0034854 | 4.4299 | 22.9428
2366 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020203 | F19-PURVA-PARK-RIDGE | URBAN MIXED LOAD | DLMS Meter | 3.5597 | 3.4264 | 0 | 3.5597 | 3.7449 | 6.8326
2367 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020307 | F20-M/S.VSNL-FEEDER | COMMERCIAL | DLMS Meter | 10.5718 | 10.5242 | 0 | 10.5718 | 0.44992 | 2.4178
2368 | BMANZ | EAST | WHITEFIELD | E7 | HOODY_220 | 1130202903020106 | F21-AKME-BALLET | URBAN MIXED LOAD | DLMS Meter | 4.8791 | 4.4797 | 0.05844 | 4.8207 | 7.0724 | 12.152
2369 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020308 | F22-BORUKA-TECH-PARK | COMMERCIAL | DLMS Meter | 0.40131 | 0.3905 | 0 | 0.40131 | 2.6932 | 2.6932
2370 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020309 | F23-M/S.BUSHRA-TECH-PARK. | COMMERCIAL | DLMS Meter | 1.9467 | 0.7043 | 1.1953 | 0.75138 | 6.2661 | 6.2661
2371 | BMANZ | EAST | WHITEFIELD | E12 | HOODY_220 | 1130202903020310 | F24-M/S-BELL-TOWER-HOTELS | COMMERCIAL | DLMS Meter | 0.61751 | 0.59284 | 0 | 0.61751 | 3.995 | 7.0942
2372 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HOOKUNDA_66 | 1220302903010101 | F01-AREKOPPA NJY | NJY | DLMS Meter | 0.62066 | 0.39671 | 0.18386 | 0.4368 | 9.1779 | 55.7713
2373 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HOOKUNDA_66 | 1220302903010102 | F02-HOOKUNDA NJY | NJY | DLMS Meter | 0.24124 | 0.18766 | 0.034922 | 0.20632 | 9.0414 | 40.3492
2374 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HOOKUNDA_66 | 1220302903010103 | F03-MUNESHWARA BETTA | AGRI | DLMS Meter | 0.65503 | 0.5896 | 0 | 0.65503 | 9.9893 | 9.9893
2375 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HOOKUNDA_66 | 1220302903010104 | F04-MARASANDRA | AGRI | DLMS Meter | 0.18987 | 0.1708 | 0 | 0.18987 | 10.0418 | 10.0418
2376 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HOOKUNDA_66 | 1220302903010105 | F05-DODDAKOPPA | AGRI | DLMS Meter | 0.98152 | 0.88313 | 0 | 0.98152 | 10.024 | 10.024
2377 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HOOKUNDA_66 | 1220302903020101 | F06-TERIGEDODDI | AGRI | DLMS Meter | 1.0606 | 0.95457 | 0 | 1.0606 | 9.9936 | 9.9936
2378 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HOOKUNDA_66 | 1220302903020102 | F07-KALLIGOWDANADODDI NJY | NJY | DLMS Meter | 0.2718 | 0.14449 | 0.11269 | 0.15911 | 9.1882 | 35.9201
2379 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HOOKUNDA_66 | 1220302903020103 | F08-NERALEDODDI | AGRI | DLMS Meter | 0.20692 | 0.18625 | 0 | 0.20692 | 9.9902 | 9.9902
2380 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902010101 | F02-VEDAVATI WS | WATER WORKS | DLMS Meter | 0.19024 | 0.19569 | 0 | 0.19024 | -2.8653 | 21.6044
2381 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902010110 | F03-KAPPAGERE | AGRI | DLMS Meter | 0.70106 | 0.63105 | 0 | 0.70106 | 9.9864 | 9.9864
2382 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902020301 | F06-KORATIGERE | AGRI | DLMS Meter | 0.4852 | 0.43676 | 0 | 0.4852 | 9.9827 | 9.9827
2383 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902020302 | F07-MADURE | AGRI | DLMS Meter | 1.297 | 1.1674 | 0 | 1.297 | 9.9906 | 9.9906
2384 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902020303 | F08-SIDDARAMANAGARA | DOMESTIC | DLMS Meter | 0.70566 | 0.64065 | 0 | 0.70566 | 9.2125 | 11.9944
2385 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902020304 | F10-KANGUVALLI | NJY | DLMS Meter | 0.59379 | 0.50565 | 0 | 0.59379 | 14.8431 | 42.3463
2386 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902010103 | F11-KELLODU | AGRI | DLMS Meter | 1.8926 | 1.7031 | 0 | 1.8926 | 10.0113 | 10.0113
2387 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902010104 | F12-RANGAVANAHALLI | AGRI | DLMS Meter | 0.81481 | 0.73327 | 0 | 0.81481 | 10.0072 | 10.0072
2388 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902020305 | F13-PEELAPURA | AGRI | DLMS Meter | 1.7551 | 1.5799 | 0 | 1.7551 | 9.9842 | 9.9842
2389 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902020306 | F14-DEVIGERE | AGRI | DLMS Meter | 1.6983 | 1.5285 | 0 | 1.6983 | 9.9973 | 9.9973
2390 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902010105 | F15-KOBRIPETE | DOMESTIC | DLMS Meter | 3.1587 | 2.874 | 0 | 3.1587 | 9.0131 | 9.6529
2391 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902020308 | F16-B.V.NAGARA | NJY | DLMS Meter | 1.2506 | 0.37661 | 0.82616 | 0.42444 | 11.2694 | 40.3541
2392 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902020309 | F17-MAVINAKATTE | NJY | DLMS Meter | 0.37304 | 0.33066 | 0 | 0.37304 | 11.3583 | 34.5937
2393 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | HOSADURGA_66 | 1310204902010109 | F18-ATTIGATA NJY | NJY | DLMS Meter | 0.5114 | 0.30733 | 0.1632 | 0.3482 | 11.7374 | 35.5932
2394 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902020301 | F01-SHIVPURA | AGRI | DLMS Meter | 2.4366 | 1.5821 | 0.655 | 1.7816 | 11.2005 | 11.2005
2395 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902020302 | F02-HAGALWADI | AGRI | DLMS Meter | 2.9706 | 1.8259 | 0.905 | 2.0656 | 11.6017 | 11.6017
2396 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902020303 | F03-MANCHALDORE | AGRI | DLMS Meter | 1.7191 | 1.5468 | 0 | 1.7191 | 10.0222 | 10.0222
2397 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902020304 | F04-HOVINAKATTE | AGRI | DLMS Meter | 1.4522 | 1.2425 | 0.052 | 1.4002 | 11.2666 | 11.2666
2398 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902010101 | F05-KALLANAHALLI | AGRI | DLMS Meter | 1.1643 | 1.0478 | 0 | 1.1643 | 10.0024 | 10.0024
2399 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902010102 | F06-HOSAKERE | AGRI | DLMS Meter | 0.9159 | 0.82427 | 0 | 0.9159 | 10.0038 | 10.0038
2400 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902010103 | F07-ALILUGHATTA | AGRI | DLMS Meter | 3.4352 | 2.8705 | 0.182 | 3.2532 | 11.7658 | 11.7658
2401 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902010104 | F08-BETTADAHALLI | AGRI | DLMS Meter | 1.1387 | 1.0247 | 0 | 1.1387 | 10.0106 | 10.0106
2402 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902010105 | F09-KALINGANAHALLY | NJY | DLMS Meter | 0.42598 | 0.37531 | 0 | 0.42598 | 11.8952 | 43.3225
2403 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902010106 | F10-SOMALAPURA | NJY | DLMS Meter | 0.49038 | 0.43381 | 0 | 0.49038 | 11.5362 | 25.2242
2404 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902010107 | F11-GANESHPURA | IDLE | DLMS Meter | 0.86746 | 0.3024 | 0.526 | 0.34146 | 11.44 | 11.44
2405 | CTAZ | TUMKUR | TUMKUR | NITTUR | HOSAKERE_66 | 1320107902010108 | F12-BHOGASANDRA | NJY | DLMS Meter | 0.57976 | 0.5081 | 0 | 0.57976 | 12.36 | 35.3205
2406 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906010101 | F01-JADIGENAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.18 | 2.751 | 0 | 3.18 | 13.4926 | 17.5705
2407 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906010102 | F02-MAKANAHALLI | AGRI | DLMS Meter | 1.2923 | 1.163 | 0 | 1.2923 | 10.0067 | 10.0067
2408 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906010103 | F04-GATTIGANABBE | AGRI | DLMS Meter | 0.79724 | 0.69875 | 0 | 0.79724 | 12.3541 | 12.3541
2409 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906010104 | F05-INDUSTRIAL_H | COMMERCIAL | DLMS Meter | 6.0209 | 4.3293 | 1.0077 | 5.0132 | 13.6423 | 16.7068
2410 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906010105 | F06-BPL | INDUSTRIAL | DLMS Meter | 2.676 | 1.6709 | 0.83621 | 1.8398 | 9.1775 | 13.8111
2411 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906020101 | F07-CIPLA | INDUSTRIAL | DLMS Meter | 4.5088 | 3.7436 | 0.37982 | 4.129 | 9.3326 | 12.9898
2412 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906020102 | F08-DASARAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.481 | 1.0905 | 0.22138 | 1.2597 | 13.4251 | 15.6657
2413 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906010108 | F09-BRIGADE BUENA VISTA | DOMESTIC | DLMS Meter | 0.39876 | 0.23947 | 0.14706 | 0.2517 | 4.8594 | 4.8594
2414 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906020301 | F10-IMPACT-GLASS-FACTORY | INDUSTRIAL | DLMS Meter | 1.464 | 1.1906 | 0.20829 | 1.2557 | 5.1841 | 17.274
2415 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906020302 | F11-V-R-K-P | INDUSTRIAL | DLMS Meter | 1.1107 | 0.45326 | 0.61895 | 0.49173 | 7.8242 | 10.6515
2416 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906020502 | F12-ALLAPANAHALLY | AGRI | DLMS Meter | 0.97779 | 0.86992 | 0 | 0.97779 | 11.0324 | 12.3806
2417 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906010701 | F13-MANDUR | DOMESTIC | DLMS Meter | 4.9684 | 3.3626 | 1.1429 | 3.8255 | 12.1014 | 15.42
2418 | BRAZ | BANGALORE RURAL | Hosakote | Hosakote | HOSAKOTE_66 | 1210201906010702 | F14-HOSAKOTE-NEW-TOWN | DOMESTIC | DLMS Meter | 2.7448 | 3.4993 | 0.016856 | 2.7279 | 7.9951 | 16.1063
2419 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906010703 | F16-BUDIGERE | DOMESTIC | DLMS Meter | 4.4244 | 3.7135 | 0.17976 | 4.2446 | 12.5123 | 18.8907
2420 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906010106 | F17-AGRI LAKDANAHALLI | AGRI | DLMS Meter | 2.0484 | 0.96356 | 0.97779 | 1.0706 | 9.9986 | 16.8442
2421 | BRAZ | BANGALORE RURAL | Hosakote | Hosakote | HOSAKOTE_66 | 1210201906030902 | F20-A-I-R | INDUSTRIAL | DLMS Meter | 0.99309 | 0.89165 | 0 | 0.99309 | 10.2195 | 32.5977
2422 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906030903 | F21-LAKONDANAHALLI-NJY | NJY | DLMS Meter | 2.2882 | 2.0563 | 0 | 2.2882 | 10.1341 | 18.3905
2423 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906031102 | F23-ATTUR | NJY | DLMS Meter | 2.565 | 2.3619 | 0 | 2.565 | 7.9177 | 18.4614
2424 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906020305 | F26- BHAKTHARAHALLI NJY | NJY | DLMS Meter | 1.3689 | 1.246 | 0 | 1.3689 | 8.9716 | 26.3406
2425 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905010101 | F01-DASENAHALLY | AGRI | DLMS Meter | 1.5177 | 1.1859 | 0.2 | 1.3177 | 10.0042 | 10.0042
2426 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905010102 | F02-GIRIYAMMANAPALYA | AGRI | DLMS Meter | 0.67428 | 0.60672 | 0 | 0.67428 | 10.0194 | 10.0194
2427 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905010103 | F03-CHINNENAHALLY | AGRI | DLMS Meter | 0.73078 | 0.65714 | 0 | 0.73078 | 10.0764 | 10.0764
2428 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905010104 | F04-HOSAKERE | DOMESTIC | DLMS Meter | 0.27202 | 0.24262 | 0 | 0.27202 | 10.8093 | 31.8955
2429 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905020101 | F05-NEELIHALLY | AGRI | DLMS Meter | 1.0467 | 0.94573 | 0 | 1.0467 | 9.6427 | 9.8094
2430 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905020102 | F06-BRAHMASAMUDRA | AGRI | DLMS Meter | 1.3213 | 1.1755 | 0 | 1.3213 | 11.0361 | 11.0361
2431 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905020103 | F07-JEEVAGONDANAHALLY-NJY | NJY | DLMS Meter | 0.47418 | 0.29209 | 0.146 | 0.32818 | 10.9955 | 57.0149
2432 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905020104 | F08-NERALEKERE | AGRI | DLMS Meter | 1.5858 | 1.4271 | 0 | 1.5858 | 10.0091 | 10.0091
2433 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905010106 | F09- CHEELANAHALLY NJY | NJY | DLMS Meter | 0.5265 | 0.3354 | 0.1605 | 0.366 | 8.36 | 70.0236
2434 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905020301 | F10-AVARAGALLU NJY | NJY | DLMS Meter | 0.213 | 0.16532 | 0.032 | 0.181 | 8.6646 | 71.4523
2435 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | HOSKERE_66 | 1320301905020302 | F11-KATTHIRAJANAHALLI | AGRI | DLMS Meter | 1.2257 | 1.0921 | 0 | 1.2257 | 10.8997 | 10.8997
2436 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | HOSKOTE_220 | 1210203902010101 | F01-MUTHSANDRA | AGRI | DLMS Meter | 1.0309 | 0.16637 | 0.84603 | 0.18485 | 9.9956 | 9.9956
2437 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | HOSKOTE_220 | 1210203902010102 | F02-HASIGALA | NJY | DLMS Meter | 1.2849 | 1.1289 | 0 | 1.2849 | 12.1428 | 60.3802
2438 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | HOSKOTE_220 | 1210203902010103 | F03-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 2.1788 | 2.0484 | 0 | 2.1788 | 5.9846 | 5.9846
2439 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | HOSKOTE_220 | 1210203902010104 | F04-KAMBALIPURA | AGRI | DLMS Meter | 0.84603 | 0.76135 | 0 | 0.84603 | 10.0095 | 10.2619
2440 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | HOSKOTE_220 | 1210203902010105 | F06-GODREJ-AND-TYSON | INDUSTRIAL | DLMS Meter | 2.7756 | 2.5943 | 0 | 2.7756 | 6.5302 | 7.9205
2441 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | HOSKOTE_220 | 1210203902010106 | F07-BEGUR | AGRI | DLMS Meter | 0.38106 | 0.34294 | 0 | 0.38106 | 10.0037 | 10.0037
2442 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | HOSKOTE_220 | 1210203902010107 | F08-GULLAHALLI | NJY | DLMS Meter | 1.7414 | 1.544 | 0 | 1.7414 | 11.3342 | 40.8014
2443 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | HOSKOTE_220 | 1210203902010109 | F10-SUGUNA FOODS | INDUSTRIAL | DLMS Meter | 1.8814 | 1.8804 | 0 | 1.8814 | 0.055543 | 0.055543
2444 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | HOSKOTE_220 | 1210203902010110 | F11-BANGALORE METALLURGICALS | INDUSTRIAL | DLMS Meter | 1.97 | 1.9643 | 0 | 1.97 | 0.29289 | 0.29289
2445 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | HOSUR(RAMAPURA)_66 | 1230303903010101 | F01-KUDUREBYALYA | AGRI | DLMS Meter | 0.88784 | 0.79927 | 0 | 0.88784 | 9.976 | 9.976
2446 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | HOSUR(RAMAPURA)_66 | 1230303903010102 | F02-KURUDI | AGRI | DLMS Meter | 0.85216 | 0.76684 | 0 | 0.85216 | 10.0116 | 17.0173
2447 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | HOSUR(RAMAPURA)_66 | 1230303903010103 | F03-SONAGANAHALLY | AGRI | DLMS Meter | 0.91404 | 0.82269 | 0 | 0.91404 | 9.9937 | 9.9937
2448 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | HOSUR(RAMAPURA)_66 | 1230303903010301 | F04-HOSSUR | AGRI | DLMS Meter | 1.0178 | 0.91585 | 0 | 1.0178 | 10.0202 | 10.0202
2449 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | HOSUR(RAMAPURA)_66 | 1230303903010302 | F05-BAKTHARAHALLY | AGRI | DLMS Meter | 1.0738 | 0.73701 | 0.255 | 0.81882 | 9.9912 | 15.8108
2450 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | HOSUR(RAMAPURA)_66 | 1230303903010303 | F06-BARC | INDUSTRIAL | DLMS Meter | 0.18174 | 0.17857 | 0 | 0.18174 | 1.747 | 1.9722
2451 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | HOSUR(RAMAPURA)_66 | 1230303903010104 | F07-KOTALDINNE | NJY | DLMS Meter | 1.2084 | 1.0374 | 0 | 1.2084 | 14.1495 | 49.618
2452 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | HOSUR(RAMAPURA)_66 | 1230303903010304 | F08-NJY-ANUDI | NJY | DLMS Meter | 0.87544 | 0.75267 | 0 | 0.87544 | 14.024 | 53.3735
2453 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | HOSUR(RAMAPURA)_66 | 1230303903020305 | F09-HOSA UPPARAHALLI | AGRI | DLMS Meter | 0.96304 | 0.86651 | 0 | 0.96304 | 10.0232 | 10.0232
2454 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010101 | F01-BOMMANAHALLI-IND | DOMESTIC | DLMS Meter | 4.0849 | 3.8654 | 0 | 4.0849 | 5.3736 | 7.1478
2455 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010102 | F02-BOMMANAHALLI | DOMESTIC | DLMS Meter | 5.6972 | 4.3186 | 1.1 | 4.5972 | 6.0606 | 9.0889
2456 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010103 | F03-HSR-SECTOR | DOMESTIC | DLMS Meter | 3.6496 | 3.291 | 0.16002 | 3.4895 | 5.6897 | 5.9455
2457 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010104 | F04-HSR-SECTOR | DOMESTIC | DLMS Meter | 1.6807 | 0.75225 | 0.8931 | 0.78757 | 4.4855 | 4.4855
2458 | BMASZ | SOUTH | HSR | S11 | HSRLAYOUT_220 | 1110303904010301 | F05-SOMASUNDERAPALYA | DOMESTIC | DLMS Meter | 6.1933 | 5.7164 | 0.1 | 6.0933 | 6.1856 | 10.6998
2459 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010302 | F07-FJAKKASANDRA-SECTOR | DOMESTIC | DLMS Meter | 3.5077 | 2.5756 | 0.757 | 2.7507 | 6.3653 | 9.1343
2460 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010303 | F08-KAIKONDANAHALLI | DOMESTIC | DLMS Meter | 5.1146 | 4.8504 | 0 | 5.1146 | 5.1644 | 7.1095
2461 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010105 | F09-CPWD-QUARTERS-SECTOR | DOMESTIC | DLMS Meter | 1.6528 | 1.4164 | 0.145 | 1.5078 | 6.0654 | 8.0266
2462 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010304 | F10-GOLD-HILL | INDUSTRIAL | DLMS Meter | 6.2605 | 5.939 | 0 | 6.2605 | 5.1356 | 6.7014
2463 | BMASZ | SOUTH | KORAMANGALA | S4 | HSRLAYOUT_220 | 1110303904010305 | F11-INTEL | URBAN MIXED LOAD | DLMS Meter | 3.3722 | 3.0616 | 0.047 | 3.3252 | 7.9275 | 7.9275
2464 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010106 | F12-HSR-TH-SECTOR | DOMESTIC | DLMS Meter | 1.6088 | 1.3053 | 0.22 | 1.3888 | 6.0083 | 8.3881
2465 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010306 | F13-VENKATAPURA | DOMESTIC | DLMS Meter | 2.086 | 1.8343 | 0.16 | 1.926 | 4.7591 | 4.7591
2466 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010308 | F15-BDA | DOMESTIC | DLMS Meter | 5.398 | 4.8843 | 0.26 | 5.138 | 4.9365 | 6.0225
2467 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010108 | F17-SUN-CITY | DOMESTIC | DLMS Meter | 7.8295 | 6.4375 | 0.862 | 6.9675 | 7.6063 | 8.3205
2468 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010109 | F18-AGARA | DOMESTIC | DLMS Meter | 5.9472 | 5.4902 | 0.15 | 5.7972 | 5.2958 | 7.5216
2469 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010113 | F19-HOSAPALYA | DOMESTIC | DLMS Meter | 4.5391 | 4.0259 | 0.3163 | 4.2228 | 4.6618 | 5.3993
2470 | BMASZ | SOUTH | HSR | S13 | HSRLAYOUT_220 | 1110303904030101 | F20-KCDC | URBAN MIXED LOAD | DLMS Meter | 3.3393 | 3.0592 | 0.09321 | 3.246 | 5.7545 | 7.5427
2471 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010111 | F21-KSRP | DOMESTIC | DLMS Meter | 2.8918 | 2.7181 | 0 | 2.8918 | 6.0078 | 16.126
2472 | BMASZ | SOUTH | HSR | S20 | HSRLAYOUT_220 | 1110303904010112 | F22-HSR 3RD SCTOR | DOMESTIC | DLMS Meter | 3.4805 | 1.361 | 2.0005 | 1.48 | 8.0361 | 8.0361
2473 | BMASZ | SOUTH | HSR | S11 | HSRLAYOUT_220 | 1110303904030501 | F23-PRESTIGE_FERNS | DOMESTIC | DLMS Meter | 5.2733 | 2.5216 | 2.59 | 2.6833 | 6.0263 | 11.7961
2474 | BMASZ | SOUTH | HSR | S13 | HSRLAYOUT_220 | 1110303904030502 | F24-SNN | DOMESTIC | DLMS Meter | 2.2776 | 2.178 | 0.040321 | 2.2372 | 2.6487 | 2.6487
2475 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | HULIMANGALA_66 | 1220204902010104 | F01-MARGONDANAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.3656 | 1.1057 | 0.172 | 1.1936 | 7.3613 | 7.3613
2476 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | HULIMANGALA_66 | 1220204902010103 | F02-HULIMANGALA | URBAN MIXED LOAD | DLMS Meter | 0.8426 | 0.50869 | 0.292 | 0.5506 | 7.6121 | 13.2877
2477 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | HULIMANGALA_66 | 1220204902010106 | F03-NANJAPURA | URBAN MIXED LOAD | DLMS Meter | 2.076 | 1.9237 | 0 | 2.076 | 7.3348 | 11.712
2478 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | HULIMANGALA_66 | 1220204902010107 | F04-HULLAHALLI GATE | URBAN MIXED LOAD | DLMS Meter | 1.0622 | 0.92731 | 0.067 | 0.99524 | 6.8253 | 9.3405
2479 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | HULIMANGALA_66 | 1220204902010105 | F05-THIRUPALYA | URBAN MIXED LOAD | DLMS Meter | 1.4178 | 0.77016 | 0.61 | 0.8078 | 4.6592 | 8.8935
2480 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | HULIMANGALA_66 | 1220204902020102 | F07-HULIMANGALA AGRI | AGRI | DLMS Meter | 0.19658 | 0.17707 | 0 | 0.19658 | 9.9247 | 9.9247
2481 | BMASZ | SOUTH | HSR | S13 | HULIMANGALA_66 | 1220204902020101 | F09-NEELADRI-ROAD | DOMESTIC | DLMS Meter | 3.5836 | 3.4405 | 0 | 3.5836 | 3.9917 | 3.9917
2482 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | HULIMANGALA_66 | 1220204902010101 | F10-PODU | URBAN MIXED LOAD | DLMS Meter | 1.301 | 0.92561 | 0.305 | 0.996 | 7.0673 | 20.0864
2483 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | HULIMANGALA_66 | 1220204902010102 | F11-SAI BABA TEMPLE ROAD | URBAN MIXED LOAD | DLMS Meter | 0.8166 | 0.7075 | 0.0418 | 0.7748 | 8.686 | 14.5998
2484 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905010101 | F01-TAMADIHALLI | AGRI | DLMS Meter | 0.76788 | 0.67588 | 0 | 0.76788 | 11.9804 | 11.9804
2485 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905010102 | F02-HULIYAR | URBAN MIXED LOAD | DLMS Meter | 1.4499 | 1.2583 | 0.00012 | 1.4497 | 13.2057 | 14.8487
2486 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905010103 | F03-YALANADU | AGRI | DLMS Meter | 0.7171 | 0.63582 | 0 | 0.7171 | 11.335 | 11.335
2487 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905010104 | F04-KESHAVAPURA | AGRI | DLMS Meter | 0.72306 | 0.63119 | 0 | 0.72306 | 12.7063 | 12.7063
2488 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905010105 | F05-KORGERE | AGRI | DLMS Meter | 0.82176 | 0.73935 | 0 | 0.82176 | 10.0279 | 10.0279
2489 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905020301 | F06-SOMANAHALLI | AGRI | DLMS Meter | 0.72664 | 0.65405 | 0 | 0.72664 | 9.9902 | 9.9902
2490 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905020101 | F07-KENKERE | AGRI | DLMS Meter | 0.764 | 0.68753 | 0 | 0.764 | 10.0086 | 10.0086
2491 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905020102 | F08-HOYSALAKATTE | AGRI | DLMS Meter | 0.67678 | 0.60916 | 0 | 0.67678 | 9.9907 | 9.9907
2492 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905020103 | F09-PURADAMATA NJY | NJY | DLMS Meter | 0.38098 | 0.33621 | 0 | 0.38098 | 11.7518 | 46.812
2493 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905020302 | F10-DODDABIDARE | AGRI | DLMS Meter | 0.70302 | 0.6191 | 0 | 0.70302 | 11.9372 | 11.9372
2494 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905020303 | F11-BYRAPURA-NJY | NJY | DLMS Meter | 0.55517 | 0.48616 | 0 | 0.55517 | 12.4311 | 50.6104
2495 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905010106 | F12-HOSAHALLI-NJY | NJY | DLMS Meter | 0.47398 | 0.41545 | 0 | 0.47398 | 12.349 | 48.4973
2496 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905010107 | F13-SINGAPURA-NJY | NJY | DLMS Meter | 0.43005 | 0.37095 | 0 | 0.43005 | 13.7428 | 48.1641
2497 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905010108 | F14-MOTIHALLI | AGRI | DLMS Meter | 0.7076 | 0.63706 | 0 | 0.7076 | 9.9686 | 9.9686
2498 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905020304 | F15-BARAKANAHAL | AGRI | DLMS Meter | 0.8402 | 0.75644 | 0 | 0.8402 | 9.9694 | 9.9694
2499 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905030501 | F16-NANDIHALLI | AGRI | DLMS Meter | 0.89839 | 0.80818 | 0 | 0.89839 | 10.0417 | 10.0417
2500 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905030502 | F17-OTIKERE NJY | NJY | DLMS Meter | 0.3732 | 0.32268 | 0 | 0.3732 | 13.5359 | 59.4061
2501 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905030503 | F18-SIGEBAGI | AGRI | DLMS Meter | 0.5878 | 0.52901 | 0 | 0.5878 | 10.0015 | 10.0015
2502 | CTAZ | TUMKUR | TIPTUR | CN HALLY | HULIYAR_110 | 1320203905030504 | F19-KALLAHALLI | AGRI | DLMS Meter | 1.772 | 1.5599 | 0 | 1.772 | 11.9721 | 11.9721
2503 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905010104 | F01-MAGADI ROAD | AGRI | DLMS Meter | 0.07206 | 0.064757 | 0 | 0.07206 | 10.1346 | 10.1346
2504 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905010101 | F02-YADAWANI | AGRI | DLMS Meter | 0.70954 | 0.63861 | 0 | 0.70954 | 9.9972 | 9.9972
2505 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905010102 | F03-MADAPPANAHALLI | AGRI | DLMS Meter | 0.82062 | 0.73849 | 0 | 0.82062 | 10.0078 | 10.0078
2506 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905010103 | F04-HULIYUDURGA | URBAN MIXED LOAD | DLMS Meter | 1.4623 | 1.3291 | 0 | 1.4623 | 9.1073 | 25.2572
2507 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905020301 | F05-UJINI | AGRI | DLMS Meter | 0.80544 | 0.72498 | 0 | 0.80544 | 9.9897 | 9.9897
2508 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905020302 | F06-NIDASALE | AGRI | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
2509 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905020303 | F07-BANDIHALLI | AGRI | DLMS Meter | 0.61346 | 0.55201 | 0 | 0.61346 | 10.0171 | 10.0171
2510 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905020304 | F08-KODAVATHI | AGRI | DLMS Meter | 1.0405 | 0.93616 | 0 | 1.0405 | 10.0264 | 10.0264
2511 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905020305 | F09-D-HOSALLI | AGRI | DLMS Meter | 0.76718 | 0.69049 | 0 | 0.76718 | 9.9966 | 9.9966
2512 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905020306 | F10-RAJENERA-PURA NJY | NJY | DLMS Meter | 1.5931 | 1.4475 | 0 | 1.5931 | 9.1404 | 28.0354
2513 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905020307 | F11-HALEVOOR NJY | NJY | DLMS Meter | 0.40109 | 0.36598 | 0 | 0.40109 | 8.7541 | 46.2715
2514 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | HULIYURDURGA_66 | 1320109905020308 | F12-P-H-HALLI NJY | NJY | DLMS Meter | 0.50618 | 0.45853 | 0 | 0.50618 | 9.4143 | 48.305
2515 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901010106 | F01-NERALEKERE | NJY | DLMS Meter | 0.91228 | 0.23934 | 0.65 | 0.26228 | 8.7458 | 54.5153
2516 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901010101 | F02-GANGONAHALLI | AGRI | DLMS Meter | 1.1588 | 0.98143 | 0.06 | 1.0988 | 10.6817 | 10.6817
2517 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901010102 | F03-TIPPASANDRA | AGRI | DLMS Meter | 1.4095 | 0.98272 | 0.29684 | 1.1127 | 11.6802 | 11.6802
2518 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901010103 | F04-HULLENAHALLI | AGRI | DLMS Meter | 1.3331 | 1.1649 | 0 | 1.3331 | 12.6212 | 12.6212
2519 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901020305 | F05-SANKIGATTA | AGRI | DLMS Meter | 0.99534 | 0.87371 | 0 | 0.99534 | 12.22 | 12.22
2520 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901020303 | F06-HONNAPURA | NJY | DLMS Meter | 0.26879 | 0.15001 | 0.103 | 0.16579 | 9.5187 | 57.6919
2521 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901020301 | F07-VIRUPAPURA | AGRI | DLMS Meter | 1.0138 | 0.85937 | 0.05 | 0.9638 | 10.8348 | 10.8348
2522 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901020302 | F08-SUGGANAHALLI | AGRI | DLMS Meter | 0.95162 | 0.71213 | 0.15 | 0.80162 | 11.1635 | 11.1635
2523 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901010105 | F09-HEBBALALU | NJY | DLMS Meter | 0.226 | 0.20475 | 0 | 0.226 | 9.4022 | 52.426
2524 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901010104 | F10-TAVAREKERE | NJY | DLMS Meter | 0.46 | 0.28443 | 0.145 | 0.315 | 9.7049 | 54.7041
2525 | BRAZ | RAMANAGAR | MAGADI | KUDUR | HULLENAHALLI_66 | 1210103901020101 | F11-BEECHANAHALLI | AGRI | DLMS Meter | 0.9182 | 0.80108 | 0 | 0.9182 | 12.7557 | 12.7557
2526 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HUNSANAHALLI_66 | 1220302901010101 | F01-GATTIGUNDA IP | AGRI | DLMS Meter | 0.3119 | 0.28063 | 0 | 0.3119 | 10.025 | 10.025
2527 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HUNSANAHALLI_66 | 1220302901010102 | F02-YALAVANATHA | AGRI | DLMS Meter | 0.58619 | 0.52765 | 0 | 0.58619 | 9.9869 | 9.9869
2528 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HUNSANAHALLI_66 | 1220302901010103 | F03-GOLLARADODDI NJY | NJY | DLMS Meter | 0.33934 | 0.2576 | 0.05515 | 0.28419 | 9.3571 | 30.2129
2529 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HUNSANAHALLI_66 | 1220302901010104 | F04-KABBALAIAHNADODDYDODDI NJY | NJY | DLMS Meter | 0.19254 | 0.17426 | 0.001238 | 0.1913 | 8.909 | 41.0911
2530 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HUNSANAHALLI_66 | 1220302901020301 | F05-DIMBADAHALLY | AGRI | DLMS Meter | 0.36164 | 0.32546 | 0 | 0.36164 | 10.0055 | 10.0055
2531 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HUNSANAHALLI_66 | 1220302901020302 | F06-BANNIMUKKODLU NEW | AGRI | DLMS Meter | 0.8696 | 0.78273 | 0 | 0.8696 | 9.9897 | 9.9897
2532 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HUNSANAHALLI_66 | 1220302901020303 | F07-VALASI IP | AGRI | DLMS Meter | 0.53314 | 0.4799 | 0 | 0.53314 | 9.9865 | 9.9865
2533 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HUNSANAHALLI_66 | 1220302901020304 | F08-KOLAGONDANAHALLY NJY | NJY | DLMS Meter | 0.38231 | 0.33516 | 0.011573 | 0.37074 | 9.5968 | 43.6753
2534 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | HUNSANAHALLI_66 | 1220302901010105 | F11-GANGANAHALLY | AGRI | DLMS Meter | 0.19571 | 0.17606 | 0 | 0.19571 | 10.0394 | 10.0394
2535 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904010101 | F01-GANGANAGHATTA | AGRI | DLMS Meter | 0.7644 | 0.6879 | 0 | 0.7644 | 10.008 | 10.008
2536 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904010102 | F02-HUNASEGHATTA | AGRI | DLMS Meter | 0.7232 | 0.58611 | 0.072 | 0.6512 | 9.9954 | 9.9954
2537 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904010103 | F03-SUGURU | AGRI | DLMS Meter | 0.8676 | 0.72674 | 0.06 | 0.8076 | 10.012 | 10.012
2538 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904010108 | F04-M GOLLARAHATTI | AGRI | DLMS Meter | 0.7848 | 0.70666 | 0 | 0.7848 | 9.9563 | 9.9563
2539 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904010104 | F05-KANNUGATTA | AGRI | DLMS Meter | 0.7152 | 0.64372 | 0 | 0.7152 | 9.9951 | 9.9951
2540 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904010105 | F06-WATER SUPPLY | COMMERCIAL | DLMS Meter | 0.2224 | 0.017184 | 0.2035 | 0.0189 | 9.0794 | 9.0794
2541 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904010107 | F07-MASAVANAGATTA NJY | NJY | DLMS Meter | 0.2364 | 0.14536 | 0.067 | 0.1694 | 14.1883 | 31.7146
2542 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904010106 | F08-NJY-JAYAPURA | NJY | DLMS Meter | 0.4395 | 0.36543 | 0.019 | 0.4205 | 13.0956 | 21.9693
2543 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904020301 | F09-KAMPARAHALLI | AGRI | DLMS Meter | 0.626 | 0.56331 | 0 | 0.626 | 10.0142 | 10.0142
2544 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904020302 | F10-J MALLENAHALLI | AGRI | DLMS Meter | 0.7438 | 0.60806 | 0.068 | 0.6758 | 10.0241 | 10.0241
2545 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904020303 | F11-VIRUPAKSHIPURA | AGRI | DLMS Meter | 0.7562 | 0.6805 | 0 | 0.7562 | 10.0106 | 10.0106
2546 | CTAZ | TUMKUR | TIPTUR | TIPTUR | HUNSEGHATTA_110 | 1320201904020304 | F13-SASALAHALLI | AGRI | DLMS Meter | 0.6696 | 0.60279 | 0 | 0.6696 | 9.9783 | 9.9783
2547 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | IDHALLY_66 | 1320301901010101 | F01-THONDOOTY | AGRI | DLMS Meter | 0.96302 | 0.87288 | 0 | 0.96302 | 9.3601 | 9.3601
2548 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | IDHALLY_66 | 1320301901010102 | F02-YARAGUNTE | AGRI | DLMS Meter | 1.3865 | 1.2478 | 0 | 1.3865 | 10.0041 | 11.3015
2549 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | IDHALLY_66 | 1320301901010103 | F03-PULAMACHI | AGRI | DLMS Meter | 1.0999 | 0.95986 | 0 | 1.0999 | 12.7293 | 12.7293
2550 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | IDHALLY_66 | 1320301901010106 | F04- BADAKANAHALLI | AGRI | DLMS Meter | 0.92308 | 0.83063 | 0 | 0.92308 | 10.0156 | 10.0156
2551 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | IDHALLY_66 | 1320301901020301 | F06-GARANI | AGRI | DLMS Meter | 0.99782 | 0.8978 | 0 | 0.99782 | 10.0239 | 10.0239
2552 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | IDHALLY_66 | 1320301901020302 | F07-I.D.HALLY | AGRI | DLMS Meter | 0.81456 | 0.75296 | 0 | 0.81456 | 7.5625 | 8.802
2553 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | IDHALLY_66 | 1320301901010104 | F08-SUDDEKUNTE | AGRI | DLMS Meter | 0.64908 | 0.58404 | 0 | 0.64908 | 10.0208 | 10.0208
2554 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | IDHALLY_66 | 1320301901020303 | F09-TADI------NJY | NJY | DLMS Meter | 0.64466 | 0.59163 | 0 | 0.64466 | 8.2259 | 56.172
2555 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | IDHALLY_66 | 1320301901020304 | F10-YALKUR---NJY | NJY | DLMS Meter | 0.90642 | 0.80569 | 0 | 0.90642 | 11.1129 | 77.432
2556 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | IGGALUR_66 | 1220105901010101 | F01-IGGALUR | AGRI | DLMS Meter | 1.078 | 0.96995 | 0 | 1.078 | 10.0228 | 10.0228
2557 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | IGGALUR_66 | 1220105901010102 | F03-EXPRESS(LIFT) | LIFT IRRIGATION | DLMS Meter | 0.4439 | 0.1136 | 0.326 | 0.1179 | 3.6506 | 50.6804
2558 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | IGGALUR_66 | 1220105901010103 | F04-GARKAHALLI-LIFT | LIFT IRRIGATION | DLMS Meter | 0.95396 | 0.92414 | 0 | 0.95396 | 3.1264 | 3.1264
2559 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | IGGALUR_66 | 1220105901020303 | F05-NERALURU-NJY | NJY | DLMS Meter | 1.0155 | 0.71251 | 0.231 | 0.7845 | 9.1772 | 45.9976
2560 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | IGGALUR_66 | 1220105901010104 | F07-MAREGOWDANA-DODDI | AGRI | DLMS Meter | 0.309 | 0.24008 | 0.042 | 0.267 | 10.0805 | 10.0805
2561 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | IGGALUR_66 | 1220105901020301 | F08-CB-DODDI | NJY | DLMS Meter | 0.09264 | 0.05941 | 0.0274 | 0.06524 | 8.9355 | 8.9361
2562 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | IGGALUR_66 | 1220105901020302 | F09-NIDAGODI | AGRI | DLMS Meter | 0.92994 | 0.75759 | 0.088 | 0.84194 | 10.0183 | 10.0183
2563 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | IGGALUR_66 | 1220105901030503 | F10-SARAGUR | AGRI | DLMS Meter | 1.649 | 1.1087 | 0.417 | 1.232 | 10.0114 | 10.0114
2564 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | IGGALUR_66 | 1220105901010107 | F11-NUNNUR | AGRI | DLMS Meter | 1.4767 | 1.1474 | 0.203 | 1.2737 | 9.916 | 9.916
2565 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA RURAL | IGGALUR_66 | 1220105901010501 | F14-V G DODDI | AGRI | DLMS Meter | 0.4847 | 0.43492 | 0.006 | 0.4787 | 9.1454 | 9.1454
2566 | BMANZ | NORTH | MALLESHWARA | C2 | IISC_66 | 1120202901020101 | F01-SADASHIVANAGAR | URBAN MIXED LOAD | DLMS Meter | 2.3295 | 1.9767 | 0.277 | 2.0525 | 3.6915 | 6.5732
2567 | BMANZ | NORTH | MALLESHWARA | C2 | IISC_66 | 1120202901010101 | F02-DHOBHIGHAT | URBAN MIXED LOAD | DLMS Meter | 2.1083 | 1.9108 | 0.125 | 1.9833 | 3.6548 | 7.679
2568 | BMANZ | NORTH | MALLESHWARA | C2 | IISC_66 | 1120202901010102 | F03-SSLC-BOARD | URBAN MIXED LOAD | DLMS Meter | 2.3855 | 1.9846 | 0.36 | 2.0255 | 2.0225 | 3.052
2569 | BMANZ | NORTH | MALLESHWARA | C2 | IISC_66 | 1120202901020301 | F04-MALLESHWARAM | URBAN MIXED LOAD | DLMS Meter | 4.9645 | 3.9347 | 0.91 | 4.0545 | 2.9528 | 5.0045
2570 | BMANZ | NORTH | MALLESHWARA | C6 | IISC_66 | 1120202901020102 | F06-MATHIKERE | URBAN MIXED LOAD | DLMS Meter | 2.5843 | 2.4199 | 0 | 2.5843 | 6.3629 | 14.969
2571 | BMANZ | NORTH | MALLESHWARA | C2 | IISC_66 | 1120202901020302 | F08-WATER-SUPPLY | URBAN MIXED LOAD | DLMS Meter | 4.5561 | 4.307 | 0.08 | 4.4761 | 3.7779 | 6.339
2572 | BMANZ | NORTH | MALLESHWARA | C6 | IISC_66 | 1120202901020303 | F09-YESHWANTHPUR | URBAN MIXED LOAD | DLMS Meter | 3.9758 | 3.6518 | 0 | 3.9758 | 8.1506 | 17.6605
2573 | BMANZ | NORTH | MALLESHWARA | C2 | IISC_66 | 1120202901020304 | F10-BHEL | INDUSTRIAL | DLMS Meter | 1.4427 | 1.422 | 0 | 1.4427 | 1.4339 | 1.5362
2574 | BMANZ | NORTH | MALLESHWARA | C2 | IISC_66 | 1120202901020305 | F11-BRAIN CENTRE | GOVERNMENT OFFICES | DLMS Meter | 0.60764 | 0.60272 | 0 | 0.60764 | 0.80844 | 0.80844
2575 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909010101 | F01-GUILALU | AGRI | DLMS Meter | 0.44788 | 0.39804 | 0 | 0.44788 | 11.1273 | 11.1273
2576 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909010102 | F02-TAVANDI | AGRI | DLMS Meter | 0.5578 | 0.50187 | 0 | 0.5578 | 10.0276 | 10.0276
2577 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909010103 | F03-BHARAMPURA | AGRI | DLMS Meter | 0.86874 | 0.77896 | 0 | 0.86874 | 10.3345 | 10.3345
2578 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909010104 | F04-KALLAHATTY | AGRI | DLMS Meter | 0.446 | 0.40141 | 0 | 0.446 | 9.9973 | 9.9973
2579 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909020301 | F05-PALAVVANAHALLY | AGRI | DLMS Meter | 1.1816 | 1.0598 | 0 | 1.1816 | 10.3096 | 10.3096
2580 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909020302 | F06-BURUJINAROOPPA | AGRI | DLMS Meter | 0.93783 | 0.84383 | 0 | 0.93783 | 10.0236 | 10.0236
2581 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909020501 | F07-WATERWORKS | WATER WORKS | DLMS Meter | 1.1472 | 1.0493 | 0 | 1.1472 | 8.5319 | 49.633
2582 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909020502 | F08-AIMANGALA | AGRI | DLMS Meter | 0.60996 | 0.54891 | 0 | 0.60996 | 10.0089 | 10.0089
2583 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909010105 | F09-NJYMETIKURKE | AGRI | DLMS Meter | 0.41404 | 0.37241 | 0 | 0.41404 | 10.0539 | 11.7623
2584 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909010106 | F10-MALLARASANAHATTI | AGRI | DLMS Meter | 0.90152 | 0.80191 | 0 | 0.90152 | 11.0488 | 11.0488
2585 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909010107 | F11-ECL | INDUSTRIAL | DLMS Meter | 0.48632 | 0.4767 | 0 | 0.48632 | 1.9781 | 54.5721
2586 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909020503 | F12-MARADIHALLI | AGRI | DLMS Meter | 0.65092 | 0.58551 | 0 | 0.65092 | 10.0489 | 10.0489
2587 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909020504 | F13-NONABI | AGRI | DLMS Meter | 0.41626 | 0.37456 | 0 | 0.41626 | 10.0173 | 10.0173
2588 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909020505 | F14-NJYMDKOTE | NJY | DLMS Meter | 1.0599 | 0.98053 | 0 | 1.0599 | 7.4887 | 58.4955
2589 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909030501 | F15-C.S.HALLY NJY | NJY | DLMS Meter | 0.1301 | 0.000172 | 0.1301 | 0 | 0 | #DIV/0!
2590 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909020506 | F19-NJY KC ROPPA | NJY | DLMS Meter | 0.4889 | 0.4603 | 0 | 0.4889 | 5.8507 | 48.1459
2591 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | IMANGALA_66 | 1310401909010109 | F20-KOVERAHATTI | AGRI | DLMS Meter | 0.66116 | 0.59495 | 0 | 0.66116 | 10.0144 | 10.0144
2592 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902020301 | F01-MARSANAHALLI | AGRI | DLMS Meter | 1.2233 | 1.1008 | 0 | 1.2233 | 10.0114 | 10.0114
2593 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902020302 | F02-SIDDEPALLI | AGRI | DLMS Meter | 0.78209 | 0.70383 | 0 | 0.78209 | 10.0068 | 10.0068
2594 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902020303 | F03-GOWNIPALLI | AGRI | DLMS Meter | 1.9552 | 1.0557 | 0.78209 | 1.1731 | 10.0062 | 10.0062
2595 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902010101 | F04-KENCHARLAHALLI | AGRI | DLMS Meter | 1.3386 | 0.744 | 0.512 | 0.82664 | 9.9969 | 9.9969
2596 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902010102 | F05-MITTAHALLI | AGRI | DLMS Meter | 1.568 | 1.2959 | 0.128 | 1.44 | 10.0105 | 10.0105
2597 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902010103 | F06-BATLAHALLI | AGRI | DLMS Meter | 0.29156 | 0.2623 | 0 | 0.29156 | 10.0353 | 10.0353
2598 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902020304 | F07-MADAMANGALA | AGRI | DLMS Meter | 0.79652 | 0.71689 | 0 | 0.79652 | 9.9974 | 9.9974
2599 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902010104 | F08-KODIGAL | AGRI | DLMS Meter | 0.94976 | 0.85478 | 0 | 0.94976 | 10.0007 | 10.0007
2600 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902010105 | F09-GOWDANAHALLI | AGRI | DLMS Meter | 1.2249 | 1.1025 | 0 | 1.2249 | 9.9893 | 9.9893
2601 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902020305 | F10-MADAMANGALA-(NJY) | NJY | DLMS Meter | 0.4173 | 0.35817 | 0 | 0.4173 | 14.1704 | 68.3237
2602 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902020306 | F11-RASAPALLI--(NJY) | NJY | DLMS Meter | 0.78436 | 0.6869 | 0 | 0.78436 | 12.4259 | 72.4847
2603 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902020307 | F12-K-RAGUTTAHALLI--(NJY) | NJY | DLMS Meter | 1.0741 | 0.96854 | 0 | 1.0741 | 9.8299 | 53.6417
2604 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902010106 | F13-IRRAGAMPALLI-(NJY) | NJY | DLMS Meter | 0.51132 | 0.41202 | 0.0335 | 0.47782 | 13.7717 | 74.9489
2605 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902010107 | F15-KMC NJY | NJY | DLMS Meter | 0.3781 | 0.32705 | 0 | 0.3781 | 13.5009 | 41.3671
2606 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902010108 | F16-MINDIGAL | NJY | DLMS Meter | 0.3126 | 0.27093 | 0 | 0.3126 | 13.3305 | 73.4479
2607 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902010109 | F17-B.G KOTE | AGRI | DLMS Meter | 0.9288 | 0.76362 | 0.08 | 0.8488 | 10.0348 | 10.0348
2608 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | IRAGAMPALLI_66 | 1230402902020308 | F19-K.R PURA | AGRI | DLMS Meter | 1.0373 | 0.7716 | 0.18 | 0.85728 | 9.9944 | 9.9944
2609 | BMASZ | SOUTH | JAYANAGAR | S5 | ISKCON_66 | 1110103904020202 | F02-KUVEMPUNAGAR | URBAN MIXED LOAD | DLMS Meter | 1.9015 | 1.7178 | 0.056 | 1.8455 | 6.9229 | 11.458
2610 | BMASZ | SOUTH | JAYANAGAR | S5 | ISKCON_66 | 1110103904020204 | F04-MANTRI SERENITY | DOMESTIC | DLMS Meter | 0.95105 | 0.90574 | 0 | 0.95105 | 4.764 | 7.4176
2611 | BMASZ | SOUTH | HSR | S12 | ISKCON_66 | 1110103904020205 | F05-BALAJI LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.3179 | 2.7907 | 0.125 | 3.1929 | 12.599 | 18.6984
2612 | BMASZ | SOUTH | JAYANAGAR | S6 | ISKCON_66 | 1110103904020207 | F08-GUBBALALA GATE | URBAN MIXED LOAD | DLMS Meter | 2.7309 | 2.5792 | 0 | 2.7309 | 5.5554 | 11.2223
2613 | BMASZ | SOUTH | JAYANAGAR | S5 | ISKCON_66 | 1110103904020208 | F09-ROYAL PALM | DOMESTIC | DLMS Meter | 1.6934 | 0.93236 | 0.706 | 0.98738 | 5.5727 | 6.384
2614 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902010102 | F02-J.C-INDUSTRIAL-LAYOUT | INDUSTRIAL | DLMS Meter | 2.914 | 2.4885 | 0.304 | 2.61 | 4.6556 | 4.6556
2615 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902010103 | F03-YALCHANA-HALLI | URBAN MIXED LOAD | DLMS Meter | 3.0822 | 2.8862 | 0 | 3.0822 | 6.3579 | 9.6308
2616 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902010104 | F04-ISRO-LAYOUT-PIPELINE | URBAN MIXED LOAD | DLMS Meter | 3.5677 | 3.2395 | 0.1058 | 3.4619 | 6.4238 | 8.1213
2617 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902010105 | F05-NANJAPPA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.5259 | 3.2919 | 0.021 | 3.5049 | 6.0771 | 19.3528
2618 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902010106 | F06-F-ERGO-SPACER | URBAN MIXED LOAD | DLMS Meter | 2.1266 | 1.512 | 0.5185 | 1.6081 | 5.9756 | 7.5546
2619 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902020301 | F07 KS-LAYOUT-II-STAGE | URBAN MIXED LOAD | DLMS Meter | 3.9278 | 3.2177 | 0.485 | 3.4428 | 6.5379 | 13.3424
2620 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902020302 | F08-VIKRAM-NAGAR | URBAN MIXED LOAD | DLMS Meter | 1.8755 | 1.7561 | 0 | 1.8755 | 6.3694 | 10.2307
2621 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902020303 | F09-GOWDANA-PALYA | URBAN MIXED LOAD | DLMS Meter | 2.2192 | 1.1168 | 1.02 | 1.1992 | 6.8735 | 6.8735
2622 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902020304 | F10-K.S-LAYOUT-WATERTANK | URBAN MIXED LOAD | DLMS Meter | 3.8425 | 2.5621 | 1.104 | 2.7385 | 6.4437 | 10.4004
2623 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902020305 | F11-SARAKKI-GATE | URBAN MIXED LOAD | DLMS Meter | 2.6871 | 2.2151 | 0.33 | 2.3571 | 6.0257 | 11.2327
2624 | BMASZ | SOUTH | JAYANAGAR | S5 | ISROLAYOUT_66 | 1110103902020306 | F12-VALLABHANAGAR | URBAN MIXED LOAD | DLMS Meter | 2.8024 | 2.4265 | 0.223 | 2.5794 | 5.9265 | 11.6819
2625 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901010301 | F01-RAMURTHY-NAGAR | URBAN MIXED LOAD | DLMS Meter | 4.1898 | 3.4885 | 0.43293 | 3.7569 | 7.1449 | 17.138
2626 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901020101 | F02-BANASWADI | URBAN MIXED LOAD | DLMS Meter | 5.5785 | 5.2152 | 0 | 5.5785 | 6.5122 | 12.3018
2627 | BMANZ | EAST | INDIRA NAGAR | E10 | ITI_66 | 1130204901010101 | F04-NGEF-FACTORY | URBAN MIXED LOAD | DLMS Meter | 5.2502 | 4.7667 | 0.13906 | 5.1111 | 6.7386 | 9.2202
2628 | BMANZ | EAST | INDIRA NAGAR | E10 | ITI_66 | 1130204901010102 | F05-NGEF-MUSS | URBAN MIXED LOAD | DLMS Meter | 4.2555 | 3.9273 | 0.050652 | 4.2049 | 6.6016 | 11.6997
2629 | BMANZ | EAST | WHITEFIELD | E7 | ITI_66 | 1130204901020103 | F06-F-AIR | URBAN MIXED LOAD | DLMS Meter | 5.5049 | 4.1281 | 1.0374 | 4.4675 | 7.5986 | 11.8585
2630 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901010302 | F07-F-KR-PURAM-INDL | URBAN MIXED LOAD | DLMS Meter | 5.8775 | 5.5479 | 0 | 5.8775 | 5.6087 | 13.0004
2631 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901010303 | F08-ANANDPURA | URBAN MIXED LOAD | DLMS Meter | 6.3154 | 5.7781 | 0.13101 | 6.1844 | 6.5707 | 14.6464
2632 | BMANZ | EAST | WHITEFIELD | E12 | ITI_66 | 1130204901010304 | F09-MAHADEVAPURA. | DOMESTIC | DLMS Meter | 2.6376 | 2.5663 | 0 | 2.6376 | 2.701 | 11.0712
2633 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901010305 | F10-HOYSALA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 4.1095 | 3.7328 | 0.14838 | 3.9611 | 5.7634 | 12.8719
2634 | BMANZ | EAST | WHITEFIELD | E7 | ITI_66 | 1130204901020104 | F11-DEVASANDRA | URBAN MIXED LOAD | DLMS Meter | 4.6856 | 3.702 | 0.712 | 3.9736 | 6.8368 | 14.2287
2635 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901020105 | F12-NRI-L/O | URBAN MIXED LOAD | DLMS Meter | 5.0859 | 4.6743 | 0.030826 | 5.0551 | 7.5339 | 21.2509
2636 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901010306 | F13-BWSSB | URBAN MIXED LOAD | DLMS Meter | 5.2254 | 3.8437 | 1.1788 | 4.0466 | 5.0149 | 24.5558
2637 | BMANZ | EAST | WHITEFIELD | E7 | ITI_66 | 1130204901010307 | F14-HOODY | URBAN MIXED LOAD | DLMS Meter | 5.4113 | 4.666 | 0.3406 | 5.0707 | 7.9807 | 10.2152
2638 | BMANZ | EAST | WHITEFIELD | E12 | ITI_66 | 1130204901010308 | F15-ALPINE-ECO | URBAN MIXED LOAD | DLMS Meter | 4.2147 | 4.0051 | 0.040914 | 4.1738 | 4.0415 | 12.4321
2639 | BMANZ | EAST | INDIRA NAGAR | E10 | ITI_66 | 1130204901010103 | F17-SITARI | INDUSTRIAL | DLMS Meter | 2.1832 | 2.1958 | 0 | 2.1832 | -0.57754 | -0.30408
2640 | BMANZ | EAST | INDIRA NAGAR | E10 | ITI_66 | 1130204901020301 | F18-SITARII | WATER WORKS | DLMS Meter | 0.5278 | 0.52631 | 0 | 0.5278 | 0.28205 | 0.28205
2641 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901030501 | F20-KASHIVISH VISHWANATHA LAY OUT | URBAN MIXED LOAD | DLMS Meter | 3.6273 | 3.4257 | 0.075 | 3.5523 | 3.5638 | 20.6246
2642 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901030502 | F21-VARNASI | URBAN MIXED LOAD | DLMS Meter | 5.9827 | 4.8807 | 0.79637 | 5.1864 | 5.8925 | 35.9636
2643 | BMANZ | EAST | WHITEFIELD | E7 | ITI_66 | 1130204901030503 | F22-KRISHNA THEATRE FEEDER | DOMESTIC | DLMS Meter | 5.6426 | 4.4421 | 0.8259 | 4.8167 | 7.7758 | 13.3823
2644 | BMANZ | EAST | WHITEFIELD | E7 | ITI_66 | 1130204901030505 | F23-MEDALLI KS ROAD | DOMESTIC | DLMS Meter | 0.98381 | 0.90256 | 0.005 | 0.97881 | 7.7893 | 7.7893
2645 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901010110 | F25-BATTARAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.787 | 1.3106 | 0.4 | 1.387 | 5.5115 | 5.5115
2646 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | 1130204901030504 | F26-ITI INDUSTRIAL | URBAN MIXED LOAD | DLMS Meter | 4.0525 | 3.8709 | 0 | 4.0525 | 4.4811 | 4.4811
2647 | CTAZ | DAVANAGERE | HARIHARA | HARAPANAHALLI | ITTIGI_220 | 1310303904010101 | F03-NANDIBEVOOR | AGRI | DLMS Meter | 1.316 | 1.0718 | 0.125 | 1.191 | 10.0117 | 10.0117
2648 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | J N KOTE_66 | 1310201904010101 | F01- J N KOTE | AGRI | DLMS Meter | 0.4678 | 0.42085 | 0 | 0.4678 | 10.0363 | 10.0363
2649 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | J N KOTE_66 | 1310201904010102 | F02-GOLLANAKATTE | AGRI | DLMS Meter | 0.96837 | 0.83898 | 0 | 0.96837 | 13.3618 | 13.3618
2650 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | J N KOTE_66 | 1310201904010103 | F03-PALLAVAGERE | AGRI | DLMS Meter | 0.4692 | 0.42234 | 0 | 0.4692 | 9.9872 | 9.9872
2651 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | J N KOTE_66 | 1310201904010104 | F04- J C HALLI | NJY | DLMS Meter | 0.3666 | 0.24354 | 0.102 | 0.2646 | 7.9584 | 32.3697
2652 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902010101 | F01-BELAMANGALA | AGRI | DLMS Meter | 1.0846 | 0.97538 | 0 | 1.0846 | 10.0737 | 10.0737
2653 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902010102 | F02-JADIGENAHALLI | AGRI | DLMS Meter | 1.1043 | 0.99369 | 0 | 1.1043 | 10.016 | 10.465
2654 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902010103 | F03-INDUSTRIAL-AREA | RURAL MIXED LOAD | DLMS Meter | 5.071 | 4.3012 | 0.09486 | 4.9762 | 13.5645 | 32.6996
2655 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902010104 | F04-IOC | INDUSTRIAL | DLMS Meter | 2.6021 | 2.2063 | 0.17711 | 2.425 | 9.0178 | 9.0178
2656 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902010105 | F05-DEVANAGUNDI-CROSS | AGRI | DLMS Meter | 0.83504 | 0.20446 | 0.60774 | 0.2273 | 10.0455 | 10.4406
2657 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902020306 | F07-NALLALA | AGRI | DLMS Meter | 0.60774 | 0.53907 | 0 | 0.60774 | 11.2996 | 11.2996
2658 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902020302 | F09-VISHRANTHI-TRUST | NJY | DLMS Meter | 2.6733 | 2.1556 | 0.28875 | 2.3845 | 9.6003 | 34.9036
2659 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902020303 | F10-KANEKALLU | NJY | DLMS Meter | 4.0361 | 3.5589 | 0 | 4.0361 | 11.8245 | 20.1482
2660 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902020304 | F11-HARALUR | AGRI | DLMS Meter | 0.49816 | 0.44797 | 0 | 0.49816 | 10.0753 | 10.0753
2661 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902020301 | F13-YEKAN | INDUSTRIAL | DLMS Meter | 2.929 | 2.8457 | 0 | 2.929 | 2.8419 | 3.3943
2662 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | JADIGENAHALLI_66 | 1210201902020305 | F14-ITC | INDUSTRIAL | DLMS Meter | 0 | 1.6993 | 0 | 0 | 0 | #DIV/0!
2663 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904010101 | F01-GAVIMATA | AGRI | DLMS Meter | 1.0009 | 0.87541 | 0 | 1.0009 | 12.5408 | 12.5408
2664 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904010102 | F02-THORNAGATTE | AGRI | DLMS Meter | 0.7185 | 0.62847 | 0 | 0.7185 | 12.5308 | 12.5308
2665 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904010103 | F03-JAGALURUTOWN | DOMESTIC | DLMS Meter | 2.2209 | 1.941 | 0.07675 | 2.1441 | 9.4736 | 22.3902
2666 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904010104 | F04-BILCHOD | AGRI | DLMS Meter | 1.1039 | 0.96628 | 0 | 1.1039 | 12.4674 | 12.5243
2667 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904020301 | F05-JAMMAPURA | AGRI | DLMS Meter | 1.1357 | 0.99396 | 0 | 1.1357 | 12.4823 | 12.4823
2668 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904020302 | F06-ANABUR | AGRI | DLMS Meter | 0.87588 | 0.78812 | 0 | 0.87588 | 10.0192 | 10.0192
2669 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904020303 | F07-HANUMANTHAPURA | AGRI | DLMS Meter | 0.79574 | 0.71598 | 0 | 0.79574 | 10.0227 | 10.0227
2670 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904020304 | F08-KASAVANAHALLI | AGRI | DLMS Meter | 0.79224 | 0.71283 | 0 | 0.79224 | 10.023 | 10.023
2671 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904010105 | F09-KECHENAHALLI | AGRI | DLMS Meter | 1.0284 | 0.92528 | 0 | 1.0284 | 10.0251 | 10.0251
2672 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904020305 | F10-BISTUVALLI | AGRI | DLMS Meter | 0.99608 | 0.87243 | 0 | 0.99608 | 12.4132 | 12.4132
2673 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904020501 | F11-DEVIKERENJY | NJY | DLMS Meter | 1.0479 | 0.5646 | 0.4025 | 0.6454 | 12.5196 | 49.2987
2674 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904020502 | F12-RANGAPURA | NJY | DLMS Meter | 0.72342 | 0.36071 | 0.31031 | 0.41311 | 12.685 | 55.05
2675 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904020503 | F13-RASTHEMAKUNTE | NJY | DLMS Meter | 0.40892 | 0.24407 | 0.13487 | 0.27405 | 10.9411 | 40.9655
2676 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904020504 | F14-ARISHINAGUNDI | NJY | DLMS Meter | 0.54334 | 0.25053 | 0.25738 | 0.28596 | 12.3884 | 43.9414
2677 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | JAGALUR_66 | 1310105904020505 | F15-JYOTHIPURA | NJY | DLMS Meter | 0.7768 | 0.45635 | 0.2607 | 0.5161 | 11.5771 | 44.7675
2678 | BMASZ | SOUTH | HSR | S20 | JAKKASANDRA_66 | 1110305901010101 | F01-BWSSB | URBAN MIXED LOAD | DLMS Meter | 4.6884 | 4.1983 | 0.18 | 4.5084 | 6.8782 | 10.1219
2679 | BMASZ | SOUTH | HSR | S8 | JAKKASANDRA_66 | 1110305901010103 | F02-GREENAGE APPARTMENT | DOMESTIC | DLMS Meter | 1.8412 | 1.7655 | 0 | 1.8412 | 4.1141 | 4.1141
2680 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | JALAMANGALA_66 | 1220103903010101 | F02-KANVA | AGRI | DLMS Meter | 0.27662 | 0.19901 | 0.05542 | 0.2212 | 10.0303 | 10.0303
2681 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | JALAMANGALA_66 | 1220103903010102 | F03-JALAMANGALA | AGRI | DLMS Meter | 0.30878 | 0.27792 | 0 | 0.30878 | 9.9935 | 9.9935
2682 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | JALAMANGALA_66 | 1220103903010103 | F04-AKKUR | AGRI | DLMS Meter | 0.87012 | 0.64256 | 0.1562 | 0.71392 | 9.9957 | 9.9957
2683 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | JALAMANGALA_66 | 1220103903010105 | F05-THADIKAVAGILU NJY | NJY | DLMS Meter | 0.2086 | 0.14586 | 0.0479 | 0.1607 | 9.2334 | 30.4704
2684 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | JALAMANGALA_66 | 1220103903010106 | F06-KYSAPURA NJY | NJY | DLMS Meter | 0.4192 | 0.30779 | 0.0799 | 0.3393 | 9.288 | 38.7556
2685 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | JANGAMAKOTE_66 | 1230404905010101 | F01-YANNAGUR | AGRI | DLMS Meter | 1.1521 | 1.0369 | 0 | 1.1521 | 9.9988 | 10.9133
2686 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | JANGAMAKOTE_66 | 1230404905010102 | F02-HOSAPETE | AGRI | DLMS Meter | 1.0875 | 0.97905 | 0 | 1.0875 | 9.9708 | 9.9708
2687 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | JANGAMAKOTE_66 | 1230404905010103 | F03-BYARASANDRA | AGRI | DLMS Meter | 1.3545 | 1.219 | 0 | 1.3545 | 10.0027 | 14.8531
2688 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | JANGAMAKOTE_66 | 1230404905010104 | F04-NAGAMANGALA | NJY | DLMS Meter | 1.2036 | 1.0595 | 0 | 1.2036 | 11.9719 | 79.4707
2689 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | JANGAMAKOTE_66 | 1230404905020301 | F05-NJY-JANGAMAKOTE | NJY | DLMS Meter | 2.3839 | 1.9174 | 0.18705 | 2.1968 | 12.7207 | 68.6635
2690 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | JANGAMAKOTE_66 | 1230404905020302 | F06-SUGATOOR | AGRI | DLMS Meter | 0.52379 | 0.47137 | 0 | 0.52379 | 10.0082 | 10.0082
2691 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | JANGAMAKOTE_66 | 1230404905020303 | F07-BALUVANAHALLI | AGRI | DLMS Meter | 1.3442 | 1.2096 | 0 | 1.3442 | 10.013 | 12.1956
2692 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | JANGAMAKOTE_66 | 1230404905020304 | F08-VENKATAPURA | NJY | DLMS Meter | 1.9362 | 0.70488 | 1.1224 | 0.81377 | 13.3811 | 60.1464
2693 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | JAVAGONDANAHALLI_66 | 1310401903010101 | F01-GORALADUKU | AGRI | DLMS Meter | 1.4036 | 1.2498 | 0 | 1.4036 | 10.9565 | 10.9565
2694 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | JAVAGONDANAHALLI_66 | 1310401903010102 | F02-NJYANESIDRI | NJY | DLMS Meter | 0.95486 | 0.86478 | 0 | 0.95486 | 9.4333 | 42.7041
2695 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | JAVAGONDANAHALLI_66 | 1310401903020301 | F03-JAVAGONDANAHALLI | AGRI | DLMS Meter | 2.1708 | 1.9413 | 0 | 2.1708 | 10.5714 | 10.5714
2696 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | JAVAGONDANAHALLI_66 | 1310401903010104 | F04-KTNHALLI | AGRI | DLMS Meter | 1.8587 | 1.6675 | 0 | 1.8587 | 10.2852 | 10.4315
2697 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | JAVAGONDANAHALLI_66 | 1310401903010103 | F06-OBALAPUR | AGRI | DLMS Meter | 1.3046 | 1.1645 | 0 | 1.3046 | 10.7394 | 10.7394
2698 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | JAVAGONDANAHALLI_66 | 1310401903020302 | F07-NJYPILALI | NJY | DLMS Meter | 0.32692 | 0.2971 | 0 | 0.32692 | 9.1221 | 66.8845
2699 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | JAVAGONDANAHALLI_66 | 1310401903020303 | F08-GOLDENEEDS | INDUSTRIAL | DLMS Meter | 0.99141 | 0.93019 | 0 | 0.99141 | 6.175 | 6.175
2700 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | JAVAGONDANAHALLI_66 | 1310401903010105 | F09-RANGNATHPURA | AGRI | DLMS Meter | 1.1283 | 1.0157 | 0 | 1.1283 | 9.9812 | 9.9812
2701 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | JAVAGONDANAHALLI_66 | 1310401903020304 | F10-SURAPPANAHATTY | AGRI | DLMS Meter | 1.223 | 1.0979 | 0 | 1.223 | 10.2257 | 10.2257
2702 | BMASZ | SOUTH | JAYANAGAR | S14 | JAYADEVA_66 | 1110101903010101 | F01-BTM-ND-STAGE | URBAN MIXED LOAD | DLMS Meter | 5.4667 | 4.4673 | 0.72585 | 4.7408 | 5.7691 | 8.0936
2703 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYADEVA_66 | 1110101903010102 | F02-BTS-RMU | URBAN MIXED LOAD | DLMS Meter | 3.05 | 2.2301 | 0.667 | 2.383 | 6.4163 | 8.6363
2704 | BMASZ | SOUTH | JAYANAGAR | S14 | JAYADEVA_66 | 1110101903010103 | F03-RMU-J.P.N | URBAN MIXED LOAD | DLMS Meter | 5.2112 | 4.359 | 0.47824 | 4.733 | 7.9016 | 9.2741
2705 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYADEVA_66 | 1110101903010201 | F04-TAVAREKERE | URBAN MIXED LOAD | DLMS Meter | 2.4269 | 2.0528 | 0.154 | 2.2729 | 9.6828 | 12.3596
2706 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYADEVA_66 | 1110101903020301 | F07-FSHANTHI-PARK-AXILURY | URBAN MIXED LOAD | DLMS Meter | 1.3541 | 0.91669 | 0.3403 | 1.0138 | 9.5783 | 9.782
2707 | BMASZ | SOUTH | JAYANAGAR | S14 | JAYADEVA_66 | 1110101903010204 | F09-CENTRAL-SILK-BOARD | URBAN MIXED LOAD | DLMS Meter | 5.1884 | 4.8427 | 0 | 5.1884 | 6.6622 | 8.4105
2708 | BMASZ | SOUTH | JAYANAGAR | S14 | JAYADEVA_66 | 1110101903020302 | F10-RMU-KEB-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0.84352 | 0.80322 | 0 | 0.84352 | 4.7781 | 9.4016
2709 | BMASZ | SOUTH | JAYANAGAR | S14 | JAYADEVA_66 | 1110101903020303 | F11-INDUSTRIAL-AREA-NS-PALAYA | URBAN MIXED LOAD | DLMS Meter | 4.1179 | 3.689 | 0.34514 | 3.7728 | 2.2213 | 4.3858
2710 | BMASZ | SOUTH | HSR | S19 | JAYADEVA_66 | 1110101903020401 | F12-HULIMAVU | URBAN MIXED LOAD | DLMS Meter | 4.1525 | 2.501 | 1.4607 | 2.6918 | 7.0892 | 7.0892
2711 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYADEVA_66 | 1110101903020305 | F15-MANTRY-GARDEN | URBAN MIXED LOAD | DLMS Meter | 1.0093 | 0.93862 | 0 | 1.0093 | 7.0025 | 7.0348
2712 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYADEVA_66 | 1110101903020306 | F16-JAYADEVA-HOSPITAL | HOSPITAL | DLMS Meter | 1.7349 | 1.6802 | 0 | 1.7349 | 3.1517 | 3.1517
2713 | BMASZ | SOUTH | KORAMANGALA | S16 | JAYADEVA_66 | 1110101903020307 | F17-ORACLE | URBAN MIXED LOAD | DLMS Meter | 0.36334 | 0.3455 | 0 | 0.36334 | 4.9098 | 4.9098
2714 | BMASZ | SOUTH | KORAMANGALA | S16 | JAYADEVA_66 | 1110101903020402 | F19-IBM | URBAN MIXED LOAD | DLMS Meter | 1.0201 | 0.95171 | 0 | 1.0201 | 6.7007 | 6.7007
2715 | BMASZ | SOUTH | KORAMANGALA | S16 | JAYADEVA_66 | 1110101903020404 | F21-VAKILSQUARE | URBAN MIXED LOAD | DLMS Meter | 1.4391 | 1.3521 | 0.017 | 1.4221 | 4.9234 | 13.6541
2716 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901010101 | F02-BPO | HOSPITAL | DLMS Meter | 3.2116 | 2.2799 | 0.681 | 2.5306 | 9.9056 | 10.5322
2717 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901010102 | F03-ADIGAS | URBAN MIXED LOAD | DLMS Meter | 1.9826 | 1.2986 | 0.541 | 1.4416 | 9.9187 | 10.9196
2718 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901010103 | F04-SWAGATH-RMU | URBAN MIXED LOAD | DLMS Meter | 3.5963 | 3.1019 | 0.21302 | 3.3833 | 8.3171 | 16.2982
2719 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901010104 | F05-HANUMANTHAPPA | URBAN MIXED LOAD | DLMS Meter | 3.8434 | 2.5534 | 1.0592 | 2.7842 | 8.2907 | 10.333
2720 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901010105 | F06-GEETHA-COLONY | URBAN MIXED LOAD | DLMS Meter | 1.3443 | 1.2208 | 0.022 | 1.3223 | 7.6739 | 9.1305
2721 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901010106 | F07-F-SHANTAPPA | URBAN MIXED LOAD | DLMS Meter | 1.9389 | 1.7357 | 0.057 | 1.8819 | 7.7684 | 10.3066
2722 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901020301 | F08-RAGIGUDDA | URBAN MIXED LOAD | DLMS Meter | 3.771 | 3.5619 | 0 | 3.771 | 5.5459 | 8.3309
2723 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901020302 | F09-KK-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.6875 | 2.7618 | 0.70855 | 2.9789 | 7.2875 | 9.2319
2724 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901020303 | F10-SOUTH-END-RMU | URBAN MIXED LOAD | DLMS Meter | 1.0658 | 0.96141 | 0.0205 | 1.0453 | 8.0253 | 9.459
2725 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901020305 | F12-YEDIYUR | URBAN MIXED LOAD | DLMS Meter | 1.2702 | 1.1507 | 0 | 1.2702 | 9.4086 | 11.8543
2726 | BMASZ | SOUTH | JAYANAGAR | S1 | JAYANAGAR_66 | 1110101901020306 | F14-RV-TEACHERS-COLLEGE | URBAN MIXED LOAD | DLMS Meter | 4.9689 | 3.7407 | 0.8302 | 4.1387 | 9.6166 | 10.2391
2727 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | JIDDIGERE_66 | 1320109908010201 | F01-SHETTIBIDU | AGRI | DLMS Meter | 0.64478 | 0.5737 | 0 | 0.64478 | 11.0245 | 11.0245
2728 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | JIDDIGERE_66 | 1320109908010202 | F02-BOMMADIGERE | AGRI | DLMS Meter | 0.73576 | 0.65107 | 0 | 0.73576 | 11.5104 | 11.5104
2729 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | JIDDIGERE_66 | 1320109908010203 | F03-M S PALYA | AGRI | DLMS Meter | 0.64758 | 0.58275 | 0 | 0.64758 | 10.0105 | 10.0105
2730 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | JIDDIGERE_66 | 1320109908010204 | F04-HOSURU | AGRI | DLMS Meter | 0.37228 | 0.33512 | 0 | 0.37228 | 9.9809 | 9.9809
2731 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | JIDDIGERE_66 | 1320109908010205 | F05-HULIVANA | NJY | DLMS Meter | 0.6371 | 0.54928 | 0.025345 | 0.61176 | 10.2131 | 52.322
2732 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | JIDDIGERE_66 | 1320109908020102 | F06-JIDDIGERE | AGRI | DLMS Meter | 1.2533 | 1.1132 | 0 | 1.2533 | 11.1768 | 11.1768
2733 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | JIDDIGERE_66 | 1320109908020101 | F07-DEVARAKANNASANDRA | AGRI | DLMS Meter | 0.3908 | 0.35175 | 0 | 0.3908 | 9.9933 | 9.9933
2734 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | JIDDIGERE_66 | 1320109908020103 | F09-KANTANAHALLI | AGRI | DLMS Meter | 0.2766 | 0.24902 | 0 | 0.2766 | 9.9722 | 9.9722
2735 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904010101 | F01-NAVYA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0.63328 | 0.45184 | 0.148 | 0.48528 | 6.89 | 6.89
2736 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904010106 | F02-AGILA | INDUSTRIAL | DLMS Meter | 7.208 | 7.2402 | 0 | 7.208 | -0.44728 | -0.44728
2737 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904010102 | F03-ASHIRWAAD-PIPE | INDUSTRIAL | DLMS Meter | 6.0461 | 6.0414 | 0 | 6.0461 | 0.078067 | 0.078067
2738 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904010103 | F04-RAJALAKSHMI-WIRE-COATED | INDUSTRIAL | DLMS Meter | 6.1562 | 5.8576 | 0 | 6.1562 | 4.8496 | 4.8496
2739 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904010104 | F05-BANSAL | INDUSTRIAL | DLMS Meter | 8.772 | 8.3484 | 0 | 8.772 | 4.8289 | 4.8289
2740 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904010105 | F06-KIADB | INDUSTRIAL | DLMS Meter | 3.4886 | 1.7245 | 1.7176 | 1.771 | 2.6264 | 2.6264
2741 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904020304 | F07-LAKSHMI-STEEL | INDUSTRIAL | DLMS Meter | 6.7576 | 6.3624 | 0.0982 | 6.6594 | 4.46 | 4.46
2742 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904020305 | F08-OMEX | INDUSTRIAL | DLMS Meter | 4.6797 | 3.139 | 1.38 | 3.2997 | 4.8694 | 4.8694
2743 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904020303 | F09-HCL | INDUSTRIAL | DLMS Meter | 3.6503 | 3.7095 | 0 | 3.6503 | -1.6212 | -1.6212
2744 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904020301 | F10-KIADB | INDUSTRIAL | DLMS Meter | 8.2035 | 7.7276 | 0 | 8.2035 | 5.8016 | 5.8016
2745 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904020302 | F11-SHARADHA-ENTERPRICES-IPC | INDUSTRIAL | DLMS Meter | 2.8457 | 2.7091 | 0 | 2.8457 | 4.8006 | 4.8006
2746 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904020306 | F13-DLF APARTMENT | DOMESTIC | DLMS Meter | 0.2393 | 0.22877 | 0 | 0.2393 | 4.4008 | 5.2615
2747 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI BOMMASANDRA LINK ROAD_66 | 1220204904020307 | F14-DLF | DOMESTIC | DLMS Meter | 0.40626 | 0.37539 | 0.012 | 0.39426 | 4.7864 | 4.7864
2748 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010101 | F01-JIGANI | URBAN MIXED LOAD | DLMS Meter | 5.1375 | 4.4595 | 0.31 | 4.8275 | 7.623 | 13.9548
2749 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010116 | F02-HARAPPANAHLLI | URBAN MIXED LOAD | DLMS Meter | 0.459 | 0.42617 | 0 | 0.459 | 7.1519 | 39.1433
2750 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010102 | F03-CHARBUJA | INDUSTRIAL | DLMS Meter | 1.0047 | 0.78706 | 0.163 | 0.84168 | 6.4898 | 7.7782
2751 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010103 | F04-INDALWADI | AGRI | DLMS Meter | 0.226 | 0.20342 | 0 | 0.226 | 9.992 | 9.992
2752 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010104 | F05-SLV | NJY | DLMS Meter | 1.8674 | 1.421 | 0.3346 | 1.5328 | 7.2947 | 16.5924
2753 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010105 | F06-VABHASANDRA | NJY | DLMS Meter | 0.78544 | 0.52461 | 0.215 | 0.57044 | 8.034 | 22.0404
2754 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010106 | F07-HARAGADDE | NJY | DLMS Meter | 0.89188 | 0.57569 | 0.27 | 0.62188 | 7.4272 | 20.6517
2755 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010115 | F08-AGRI | AGRI | DLMS Meter | 0.040576 | 0.036489 | 0 | 0.040576 | 10.0725 | 10.0725
2756 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905020301 | F09-STRIDE-ARCO-LAB | URBAN MIXED LOAD | DLMS Meter | 1.7602 | 1.6406 | 0 | 1.7602 | 6.7986 | 6.8908
2757 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010111 | F10-TULASI GRANITES | INDUSTRIAL | DLMS Meter | 1.7902 | 1.7904 | 0 | 1.7902 | -0.0097754 | -0.0097754
2758 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010107 | F11-IP FEEDER | AGRI | DLMS Meter | 0.15981 | 0.14388 | 0 | 0.15981 | 9.9682 | 9.9682
2759 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905030502 | F12-SITHARA | INDUSTRIAL | DLMS Meter | 3.4491 | 3.4245 | 0 | 3.4491 | 0.71381 | 0.71381
2760 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905030503 | F14-ARRON-UNIVERSAL | INDUSTRIAL | DLMS Meter | 2.0671 | 1.7006 | 0.25 | 1.8171 | 6.4125 | 6.5035
2761 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905030507 | F15-JADEMURTHY NJY | NJY | DLMS Meter | 3.1123 | 2.8011 | 0 | 3.1123 | 10.001 | 13.8396
2762 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905020302 | F18-BASANTH-BUTTON | INDUSTRIAL | DLMS Meter | 5.6042 | 5.4027 | 0 | 5.6042 | 3.5961 | 3.5961
2763 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905020306 | F19-MURUDESHWARA GRANITES | INDUSTRIAL | DLMS Meter | 3.2898 | 1.9494 | 1.2391 | 2.0508 | 4.9403 | 4.9455
2764 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905020304 | F20-KRISHNA GRANITE | INDUSTRIAL | DLMS Meter | 2.2071 | 2.1144 | 0 | 2.2071 | 4.203 | 4.203
2765 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905030504 | F21-S-B-ROAD | INDUSTRIAL | DLMS Meter | 4.4398 | 3.9171 | 0.2515 | 4.1883 | 6.4742 | 6.4742
2766 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905030509 | F22-AMBEDKAR INDUSTRIAL 1 | INDUSTRIAL | DLMS Meter | 4.5285 | 4.4139 | 0 | 4.5285 | 2.5302 | 2.5302
2767 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905020303 | F23-PEARL-POLYMER | INDUSTRIAL | DLMS Meter | 0.02252 | 0.02217 | 0 | 0.02252 | 1.5542 | 1.5542
2768 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905030505 | F25-NANDANAVANA | URBAN MIXED LOAD | DLMS Meter | 1.0706 | 0.72202 | 0.304 | 0.76662 | 5.8183 | 5.8183
2769 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010108 | F27-DNA | INDUSTRIAL | DLMS Meter | 1.4103 | 1.3657 | 0 | 1.4103 | 3.1597 | 3.1597
2770 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010113 | F28-CELEBRITY PRIME LAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.5213 | 0.000109 | 1.5212 | 0.000112 | 2.6786 | 2.6786
2771 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010109 | F29-SINGH-ISPAT | INDUSTRIAL | DLMS Meter | 0.0044 | 0.0043525 | 0 | 0.0044 | 1.0795 | 68.0109
2772 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905020305 | F61-BILL FORGE | INDUSTRIAL | DLMS Meter | 3.2716 | 3.2447 | 0 | 3.2716 | 0.82223 | 0.82223
2773 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | JIGANI_66 | 1220204905010118 | F62-TATA ADVANCE SYSTEMS | INDUSTRIAL | DLMS Meter | 2.8784 | 1.8756 | 1.0063 | 1.8721 | -0.18589 | -0.17895
2774 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | JULUPALYA_66 | 1230305905010104 | F01-SHETTYKERE | NJY | DLMS Meter | 0.25586 | 0.22432 | 0 | 0.25586 | 12.3251 | 64.3846
2775 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | JULUPALYA_66 | 1230305905010101 | F02-PEDDANAGARLU | AGRI | DLMS Meter | 0.97524 | 0.87769 | 0 | 0.97524 | 10.0031 | 10.0031
2776 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | JULUPALYA_66 | 1230305905010102 | F03-JULUPALYA | AGRI | DLMS Meter | 0.54762 | 0.49273 | 0 | 0.54762 | 10.0225 | 10.0225
2777 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | JULUPALYA_66 | 1230305905010103 | F04-CHOKKAMPALLI | AGRI | DLMS Meter | 0.41936 | 0.37725 | 0 | 0.41936 | 10.0422 | 10.0422
2778 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | JULUPALYA_66 | 1230305905020302 | F05-ACHAGANAPALLI | AGRI | DLMS Meter | 0.77998 | 0.70174 | 0 | 0.77998 | 10.0313 | 10.0313
2779 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | JULUPALYA_66 | 1230305905020303 | F06-MALLISHETTYHALLI | AGRI | DLMS Meter | 1.0243 | 0.92225 | 0 | 1.0243 | 9.9667 | 9.9667
2780 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | JULUPALYA_66 | 1230305905020304 | F08-POLANAYAKANAPALLI | NJY | DLMS Meter | 0.63442 | 0.56872 | 0 | 0.63442 | 10.3561 | 82.9093
2781 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | JULUPALYA_66 | 1230305905020305 | F09-SURAPAPALLI | NJY | DLMS Meter | 1.1999 | 0.92914 | 0.125 | 1.0749 | 13.5589 | 86.9324
2782 | BMANZ | EAST | WHITEFIELD | E4 | KACHAMARANAHALLI_66 | 1130202906010102 | F02-WHITEFIELD MAIN ROAD | DOMESTIC | DLMS Meter | 3.1402 | 2.6477 | 0.26016 | 2.88 | 8.0676 | 11.9163
2783 | BMANZ | EAST | WHITEFIELD | E4 | KACHAMARANAHALLI_66 | 1130202906010103 | F03-GUNJUR & GUNJURHOSAHALLI | DOMESTIC | DLMS Meter | 2.3056 | 1.773 | 0.36 | 1.9456 | 8.873 | 18.8539
2784 | BMANZ | EAST | WHITEFIELD | E4 | KACHAMARANAHALLI_66 | 1130202906010104 | F04-RAMAGONAHALLI | URBAN MIXED LOAD | DLMS Meter | 5.0628 | 4.7248 | 0 | 5.0628 | 6.6748 | 6.6748
2785 | BMANZ | EAST | WHITEFIELD | E4 | KACHAMARANAHALLI_66 | 1130202906020301 | F07-VARTHUR MAIN ROAD | DOMESTIC | DLMS Meter | 2.9575 | 2.7444 | 0 | 2.9575 | 7.2064 | 17.4056
2786 | BMANZ | EAST | WHITEFIELD | E4 | KACHAMARANAHALLI_66 | 1130202906020302 | F08-BALARERE ROAD | DOMESTIC | DLMS Meter | 4.8518 | 4.0883 | 0.41 | 4.4418 | 7.9581 | 21.3304
2787 | BMASZ | SOUTH | KORAMANGALA | S7 | KACHAMARANAHALLI_66 | 1130202906020303 | F09-BALAGERE | URBAN MIXED LOAD | DLMS Meter | 6.4304 | 6.1526 | 0 | 6.4304 | 4.3205 | 11.0759
2788 | BMANZ | EAST | WHITEFIELD | E4 | KACHAMARANAHALLI_66 | 1130202906020304 | F10-HAGADUR | DOMESTIC | DLMS Meter | 3.5633 | 3.4124 | 0 | 3.5633 | 4.2336 | 4.2336
2789 | BMASZ | SOUTH | HSR | S11 | KACHAMARANAHALLI_66 | 1130202906010107 | F13-MULLUR VILLAGE | URBAN MIXED LOAD | DLMS Meter | 2.8519 | 2.6515 | 0.03 | 2.8219 | 6.0382 | 10.7717
2790 | BMASZ | SOUTH | HSR | S11 | KACHAMARANAHALLI_66 | 1130202906010108 | F14-CHIKKABELLANDUR VILLAGE | URBAN MIXED LOAD | DLMS Meter | 1.2133 | 1.1329 | 0 | 1.2133 | 6.6287 | 9.9732
2791 | BMANZ | EAST | WHITEFIELD | E4 | KACHAMARANAHALLI_66 | 1130202906020307 | F15-PRESTIGE LAKE FRONT HABITAT | DOMESTIC | DLMS Meter | 4.5731 | 3.9746 | 0.45 | 4.1231 | 3.6002 | 4.9765
2792 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905010101 | F01-KODIHALLI | AGRI | DLMS Meter | 1.8085 | 0.95315 | 0.72 | 1.0885 | 12.4309 | 12.4309
2793 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905010102 | F02-K-S-HALLI | AGRI | DLMS Meter | 1.9683 | 1.2359 | 0.57 | 1.3983 | 11.6132 | 11.6132
2794 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905010103 | F03-BELAVATA | AGRI | DLMS Meter | 1.1154 | 1.0039 | 0 | 1.1154 | 9.9984 | 9.9984
2795 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905010104 | F04-HONNASHETTY-HALLI | AGRI | DLMS Meter | 1.5228 | 1.2332 | 0.15 | 1.3728 | 10.1714 | 10.1714
2796 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905020301 | F05-MALLENAHALLY | AGRI | DLMS Meter | 1.874 | 1.4792 | 0.21 | 1.664 | 11.1093 | 11.1093
2797 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905020302 | F06-GANGASANDRA | AGRI | DLMS Meter | 1.6204 | 0.84615 | 0.67 | 0.95044 | 10.9727 | 10.9727
2798 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905010106 | F07-KADABA | AGRI | DLMS Meter | 0.92022 | 0.56799 | 0.281 | 0.63922 | 11.1431 | 13.2793
2799 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905020303 | F08-BYALAHALLY | AGRI | DLMS Meter | 1.759 | 1.0229 | 0.605 | 1.154 | 11.3572 | 11.3572
2800 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905010105 | F09-BENNUR | NJY | DLMS Meter | 1.0143 | 0.69905 | 0.213 | 0.80128 | 12.7583 | 59.9533
2801 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905020304 | F10-DASARAKALLAHALLI-NJY | NJY | DLMS Meter | 0.953 | 0.84302 | 0 | 0.953 | 11.5405 | 58.4964
2802 | CTAZ | TUMKUR | TUMKUR | NITTUR | KADABA_110 | 1320107905020305 | F11-SHIVANANJAPPANAGARA | NJY | DLMS Meter | 0.24317 | 0.212 | 0 | 0.24317 | 12.8194 | 46.0894
2803 | BMASZ | SOUTH | KORAMANGALA | S17 | KADABISANAHALLI_66 | 1110203901010101 | F01-BRINDAVANTECH | INDUSTRIAL | DLMS Meter | 1.4287 | 0.20265 | 1.222 | 0.20671 | 1.9629 | 3.0401
2804 | BMASZ | SOUTH | KORAMANGALA | S17 | KADABISANAHALLI_66 | 1110203901010102 | F02-MARATHALLIBRIDGE | URBAN MIXED LOAD | DLMS Meter | 3.2809 | 3.1298 | 0 | 3.2809 | 4.6072 | 4.6072
2805 | BMASZ | SOUTH | KORAMANGALA | S7 | KADABISANAHALLI_66 | 1110203901010103 | F03-BELEGERE | URBAN MIXED LOAD | DLMS Meter | 4.2936 | 3.0968 | 0.93457 | 3.359 | 7.8082 | 27.8367
2806 | BMASZ | SOUTH | KORAMANGALA | S7 | KADABISANAHALLI_66 | 1110203901010104 | F04-MUNNEKOLA-TEMPLE | URBAN MIXED LOAD | DLMS Meter | 2.3774 | 1.8454 | 0.403 | 1.9744 | 6.535 | 12.2437
2807 | BMASZ | SOUTH | KORAMANGALA | S7 | KADABISANAHALLI_66 | 1110203901010301 | F05-AKRUTHI-APARTMENT | URBAN MIXED LOAD | DLMS Meter | 3.9575 | 3.8345 | 0 | 3.9575 | 3.1079 | 5.6007
2808 | BMASZ | SOUTH | KORAMANGALA | S17 | KADABISANAHALLI_66 | 1110203901010303 | F08-BWSSB | WATER WORKS | DLMS Meter | 5.464 | 5.1001 | 0 | 5.464 | 6.6597 | 6.6597
2809 | BMASZ | SOUTH | KORAMANGALA | S7 | KADABISANAHALLI_66 | 1110203901010304 | F09-DENTAL-COLLEGE | URBAN MIXED LOAD | DLMS Meter | 5.108 | 4.8977 | 0 | 5.108 | 4.1167 | 8.9945
2810 | BMASZ | SOUTH | KORAMANGALA | S17 | KADABISANAHALLI_66 | 1110203901010305 | F10-TULASI-THEATER-ROAD | URBAN MIXED LOAD | DLMS Meter | 4.4172 | 4.1317 | 0.029329 | 4.3879 | 5.8396 | 9.4832
2811 | BMASZ | SOUTH | KORAMANGALA | S7 | KADABISANAHALLI_66 | 1110203901010306 | F11-KMF | INDUSTRIAL | DLMS Meter | 0.23868 | 0.18244 | 0.054 | 0.18468 | 1.2129 | 6.6387
2812 | BMASZ | SOUTH | KORAMANGALA | S7 | KADABISANAHALLI_66 | 1110203901010307 | F13-PURVAREVIERA | DOMESTIC | DLMS Meter | 3.4468 | 3.1437 | 0.1 | 3.3468 | 6.0681 | 11.1935
2813 | BMASZ | SOUTH | KORAMANGALA | S17 | KADABISANAHALLI_66 | 1110203901010107 | F15-PRIMAL-PROJECT | COMMERCIAL | DLMS Meter | 2.2707 | 2.0384 | 0.060634 | 2.21 | 7.7655 | 8.9884
2814 | BMASZ | SOUTH | KORAMANGALA | S7 | KADABISANAHALLI_66 | 1110203901010108 | F16-PRIMAL PROJECT | COMMERCIAL | DLMS Meter | 2.2981 | 2.3158 | 0 | 2.2981 | -0.77201 | -0.77201
2815 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KADAJJI_66 | 1310103905010201 | F01-REDDY CAMP | AGRI | DLMS Meter | 0.37928 | 0.31226 | 0.023 | 0.35628 | 12.3549 | 12.3549
2816 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KADAJJI_66 | 1310103905010204 | F02-PUTUGANALU | AGRI | DLMS Meter | 0.72816 | 0.65514 | 0 | 0.72816 | 10.0286 | 10.0286
2817 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KADAJJI_66 | 1310103905010203 | F03-KADAJJI ALUR | AGRI | DLMS Meter | 1.0727 | 0.95391 | 0 | 1.0727 | 11.0702 | 11.0702
2818 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KADAJJI_66 | 1310103905010202 | F04-NJ SRI RAM | NJY | DLMS Meter | 1.4086 | 0.98096 | 0.28457 | 1.124 | 12.7301 | 41.1633
2819 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KADAJJI_66 | 1310103905020204 | F05-ANJANEYA | AGRI | DLMS Meter | 1.3381 | 1.1734 | 0 | 1.3381 | 12.3032 | 12.3032
2820 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KADAJJI_66 | 1310103905020201 | F06-KADAJJI | AGRI | DLMS Meter | 0.36708 | 0.32134 | 0 | 0.36708 | 12.4591 | 12.4591
2821 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KADAJJI_66 | 1310103905020202 | F07-BASAVANAL | AGRI | DLMS Meter | 1.0462 | 0.81398 | 0.125 | 0.92122 | 11.6411 | 11.6411
2822 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KADAJJI_66 | 1310103905020203 | F08-NAGARAKATTE | AGRI | DLMS Meter | 0.76622 | 0.67384 | 0 | 0.76622 | 12.057 | 12.057
2823 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906010101 | F01-DEVANAYAKANAHALLI | AGRI | DLMS Meter | 0.57712 | 0.51947 | 0 | 0.57712 | 9.9886 | 9.9886
2824 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906010102 | F02-KADEHALLI | AGRI | DLMS Meter | 1.1557 | 1.0405 | 0 | 1.1557 | 9.9701 | 9.9701
2825 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906010103 | F03-K BEVINAHALLI | AGRI | DLMS Meter | 0.71574 | 0.64398 | 0 | 0.71574 | 10.0256 | 10.0256
2826 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906010104 | F05-RACHAPURA | AGRI | DLMS Meter | 0.31718 | 0.28561 | 0 | 0.31718 | 9.9521 | 9.9521
2827 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906020101 | F07-DABEGHATTA | AGRI | DLMS Meter | 0.56092 | 0.50486 | 0 | 0.56092 | 9.9938 | 9.9938
2828 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906020102 | F08-HALADAHOSAHALLI | AGRI | DLMS Meter | 1.2019 | 1.0815 | 0 | 1.2019 | 10.0158 | 10.0158
2829 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906020302 | F09-B-PURA | AGRI | DLMS Meter | 0.57812 | 0.51988 | 0 | 0.57812 | 10.0733 | 10.0733
2830 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906020303 | F10-MAVINAKERE | AGRI | DLMS Meter | 1.2472 | 1.1223 | 0 | 1.2472 | 10.0127 | 10.0127
2831 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906020305 | F11-KARADIGERE NJY | NJY | DLMS Meter | 0.6368 | 0.47595 | 0.085 | 0.5518 | 13.7463 | 42.4756
2832 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906020304 | F12-HULIKAL NJY | NJY | DLMS Meter | 0.29096 | 0.26046 | 0 | 0.29096 | 10.4836 | 39.7324
2833 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | KADEHALLI_110 | 1320202906010105 | F13-BENAKANAKERE NJY | NJY | DLMS Meter | 0.40801 | 0.36906 | 0 | 0.40801 | 9.5466 | 41.335
2834 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905010101 | F01-NADAVATHI | URBAN MIXED LOAD | DLMS Meter | 3.0893 | 2.7401 | 0.13 | 2.9593 | 7.4066 | 9.2726
2835 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020101 | F02-KADUGODI | URBAN MIXED LOAD | DLMS Meter | 3.1168 | 2.5905 | 0.27988 | 2.8369 | 8.6835 | 18.1662
2836 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KADUGODI_66 | 1130202905010102 | F03-MUTHSANDRA | URBAN MIXED LOAD | DLMS Meter | 4.5772 | 4.1145 | 0 | 4.5772 | 10.1081 | 16.2712
2837 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KADUGODI_66 | 1130202905020102 | F04-DEVANAGUNDI | URBAN MIXED LOAD | DLMS Meter | 6.7067 | 5.8957 | 0 | 6.7067 | 12.093 | 18.5884
2838 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020103 | F05-AB&T | URBAN MIXED LOAD | DLMS Meter | 5.8474 | 4.9885 | 0.405 | 5.4424 | 8.3403 | 18.1437
2839 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905010103 | F06-F-SAI-GARDEN | URBAN MIXED LOAD | DLMS Meter | 2.2169 | 2.0432 | 0.03 | 2.1869 | 6.5694 | 16.5107
2840 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KADUGODI_66 | 1130202905020301 | F07-FMOTHER-DAIRY | URBAN MIXED LOAD | DLMS Meter | 3.0208 | 2.1228 | 0.70761 | 2.3132 | 8.2303 | 10.6703
2841 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020302 | F08-HAGADUR | URBAN MIXED LOAD | DLMS Meter | 5.782 | 5.4136 | 0 | 5.782 | 6.3718 | 14.295
2842 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020303 | F09-BPL | URBAN MIXED LOAD | DLMS Meter | 4.4667 | 4.071 | 0.1 | 4.3667 | 6.7725 | 11.675
2843 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020304 | F10-WHITEFIELD-INDL-AREA | URBAN MIXED LOAD | DLMS Meter | 3.9281 | 3.7462 | 0 | 3.9281 | 4.6312 | 6.0972
2844 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020305 | F12-WHITEFIELD-TOWN | URBAN MIXED LOAD | DLMS Meter | 6.6628 | 5.7984 | 0.52786 | 6.1349 | 5.4847 | 9.3995
2845 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020104 | F13-SAN-ENGINEERING,-ITPL-ROAD | URBAN MIXED LOAD | DLMS Meter | 0.87217 | 0.21403 | 0.64452 | 0.22764 | 5.9814 | 8.742
2846 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020306 | F14-SIGMA-TECH-PARK | URBAN MIXED LOAD | DLMS Meter | 8.2138 | 6.5381 | 1.1206 | 7.0932 | 7.8255 | 10.1958
2847 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020105 | F15-GOLDEN-BLOSSOM-APARTMENTS | URBAN MIXED LOAD | DLMS Meter | 5.5059 | 4.4031 | 0.665 | 4.8409 | 9.0436 | 18.8271
2848 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020106 | F16-VARTHUR-KODI | URBAN MIXED LOAD | DLMS Meter | 4.5221 | 3.1893 | 1.1119 | 3.4102 | 6.479 | 23.0059
2849 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905010107 | F17-BRIGADE COSMOPOLIS | DOMESTIC | DLMS Meter | 1.9412 | 0.69794 | 1.195 | 0.74617 | 6.4642 | 8.5421
2850 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905010108 | F18-VIJAYANAGARA | URBAN MIXED LOAD | DLMS Meter | 5.454 | 3.7128 | 1.5392 | 3.9148 | 5.1588 | 16.9916
2851 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905020403 | F19-URBAN FOREST | DOMESTIC | DLMS Meter | 0.95094 | 0.66291 | 0.245 | 0.70594 | 6.096 | 7.9763
2852 | BMANZ | EAST | WHITEFIELD | E4 | KADUGODI_66 | 1130202905010204 | F20-NAGONDANAHALLI | URBAN MIXED LOAD | DLMS Meter | 0.083656 | 0.078036 | 0 | 0.083656 | 6.7181 | 19.8158
2853 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | KALAMARANAHALLI_66 | 1310402904010101 | F01-GORALATTU | AGRI | DLMS Meter | 0.2631 | 0.23681 | 0 | 0.2631 | 9.9938 | 9.9938
2854 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | KALAMARANAHALLI_66 | 1310402904010102 | F02-BURUDUKUNTE | AGRI | DLMS Meter | 1.1149 | 0.83419 | 0.1877 | 0.9272 | 10.0312 | 10.0312
2855 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | KALAMARANAHALLI_66 | 1310402904010103 | F03-KALAMARANAHALLI | AGRI | DLMS Meter | 1.4839 | 0.33977 | 1.1051 | 0.37878 | 10.2975 | 10.2975
2856 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | KALAMARANAHALLI_66 | 1310402904010104 | F04-BELAGERE | AGRI | DLMS Meter | 1.3102 | 1.179 | 0 | 1.3102 | 10.0137 | 10.0137
2857 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | KALAMARANAHALLI_66 | 1310402904010105 | F05-SIDDESHWARA-NJY | NJY | DLMS Meter | 0.52106 | 0.34646 | 0.1282 | 0.39286 | 11.8103 | 60.8293
2858 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | KALAMARANAHALLI_66 | 1310402904020301 | F09-SIRADARAKAPLE | AGRI | DLMS Meter | 0.1276 | 0.11486 | 0 | 0.1276 | 9.9875 | 9.9875
2859 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903010101 | F01-TALAGUNDA | AGRI | DLMS Meter | 3.0533 | 2.6299 | 0 | 3.0533 | 13.8661 | 13.8661
2860 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903010102 | F02-BHOOPASANDRA | AGRI | DLMS Meter | 1.5885 | 1.3983 | 0 | 1.5885 | 11.9697 | 11.9697
2861 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903010103 | F03-KALLAMBELLA | AGRI | DLMS Meter | 1.5453 | 1.3908 | 0 | 1.5453 | 9.9969 | 9.9969
2862 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903010104 | F04-GOPALADEVARAHALLI | AGRI | DLMS Meter | 1.5439 | 1.4393 | 0 | 1.5439 | 6.7769 | 6.7769
2863 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903010105 | F05-MYSORE-ROAD | AGRI | DLMS Meter | 1.5243 | 1.3473 | 0 | 1.5243 | 11.6106 | 11.6106
2864 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903020301 | F06-NH4 | AGRI | DLMS Meter | 3.3996 | 2.799 | 0.2555 | 3.1441 | 10.9784 | 10.9784
2865 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903020302 | F07-DODDA-AGRAHARA | AGRI | DLMS Meter | 1.6647 | 1.4978 | 0 | 1.6647 | 10.0263 | 10.0263
2866 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903020303 | F08-HALANAHALLI | AGRI | DLMS Meter | 3.3594 | 2.8976 | 0 | 3.3594 | 13.7469 | 13.9399
2867 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903020304 | F09-VADDANAHALLI | AGRI | DLMS Meter | 1.4212 | 1.2414 | 0 | 1.4212 | 12.6545 | 12.6545
2868 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903020305 | F10-GANGANAHALLI | AGRI | DLMS Meter | 1.5254 | 1.3557 | 0 | 1.5254 | 11.1256 | 11.1256
2869 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903020306 | F11-K.G.HALLI | NJY | DLMS Meter | 0.82995 | 0.67344 | 0.073 | 0.75695 | 11.0318 | 35.4817
2870 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903020307 | F12-CHIKKANAHALLI | NJY | DLMS Meter | 0.78276 | 0.68191 | 0 | 0.78276 | 12.8839 | 45.7036
2871 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | KALLAMBELLA_66 | 1320303903020308 | F13-WATER SUPPLY | WATER WORKS | DLMS Meter | 0.64278 | 0.56249 | 0 | 0.64278 | 12.4905 | 47.0334
2872 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907010101 | F01-C.S-PURA | AGRI | DLMS Meter | 1.8362 | 0.43962 | 1.3285 | 0.50768 | 13.4052 | 19.873
2873 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907020301 | F02-PEDDANAHALLI | AGRI | DLMS Meter | 1.9147 | 1.6722 | 0 | 1.9147 | 12.6613 | 12.6613
2874 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907010102 | F03-KADABA | AGRI | DLMS Meter | 1.2128 | 1.0917 | 0 | 1.2128 | 9.9832 | 9.9832
2875 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907010103 | F04-BYADAGERE | AGRI | DLMS Meter | 1.4653 | 1.38 | 0 | 1.4653 | 5.8237 | 5.8237
2876 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907010104 | F05-KALLUR | URBAN MIXED LOAD | DLMS Meter | 2.5333 | 2.3312 | 0 | 2.5333 | 7.9777 | 8.9397
2877 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907020101 | F06-HINDIKERE | AGRI | DLMS Meter | 1.2245 | 1.081 | 0 | 1.2245 | 11.7174 | 11.7174
2878 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907020102 | F07-K.KALLAHALLI | AGRI | DLMS Meter | 2.2799 | 1.5736 | 0.48525 | 1.7947 | 12.3169 | 12.3169
2879 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907020103 | F08-ANKALAKOPPA | AGRI | DLMS Meter | 1.1217 | 0.71924 | 0.29874 | 0.823 | 12.6074 | 12.6074
2880 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907020302 | F09-MANCHIHALLI | AGRI | DLMS Meter | 1.0262 | 0.9163 | 0 | 1.0262 | 10.7074 | 10.7074
2881 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907010105 | F10-KURUBARAHALLI | AGRI | DLMS Meter | 1.5687 | 1.4522 | 0 | 1.5687 | 7.4284 | 7.4284
2882 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907010106 | F11-BENAKANGONDI | RURAL MIXED LOAD | DLMS Meter | 1.3924 | 1.2139 | 0 | 1.3924 | 12.8231 | 26.9751
2883 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907010107 | F12-BITTAGONDANAHALLI | NJY | DLMS Meter | 0.16742 | 0.15058 | 0 | 0.16742 | 10.0603 | 47.6254
2884 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907010108 | F13-MADAPATNA-NJY | NJY | DLMS Meter | 0.88639 | 0.78686 | 0 | 0.88639 | 11.2288 | 61.7317
2885 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907010109 | F14-MALLENAHALLY-NJY | NJY | DLMS Meter | 0 | 0.000852 | 0 | 0 | 0 | #DIV/0!
2886 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907020303 | F15-T.PALYA-NJY | NJY | DLMS Meter | 0.40287 | 0.27273 | 0.085 | 0.31787 | 14.2011 | 53.6157
2887 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907020308 | F16-PENDRANAHALLI | AGRI | DLMS Meter | 1.8874 | 0.63806 | 1.16 | 0.7274 | 12.2818 | 12.2818
2888 | CTAZ | TUMKUR | TUMKUR | GUBBI | KALLUR_110 | 1320106907020307 | F17-PADUGUDI NJY | NJY | DLMS Meter | 0.5124 | 0.4675 | 0 | 0.5124 | 8.7629 | 56.8486
2889 | BMASZ | SOUTH | KORAMANGALA | S17 | KALYANI TECHPARK_66 | 1110204901020101 | F09-WING A | COMMERCIAL | DLMS Meter | 1.2733 | 1.2743 | 0 | 1.2733 | -0.078238 | -0.078238
2890 | BMASZ | SOUTH | KORAMANGALA | S17 | KALYANI TECHPARK_66 | 1110204901020102 | F10-WING B | COMMERCIAL | DLMS Meter | 2.2999 | 2.2997 | 0 | 2.2999 | 0.010296 | 0.010296
2891 | BMASZ | SOUTH | KORAMANGALA | S17 | KALYANI TECHPARK_66 | 1110204901020103 | F11-WING C | COMMERCIAL | DLMS Meter | 2.6426 | 2.6562 | 0 | 2.6426 | -0.51526 | -0.51526
2892 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901010101 | F02-KUNDARASANAHALLI | AGRI | DLMS Meter | 0.86214 | 0.7759 | 0 | 0.86214 | 10.0035 | 10.0035
2893 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901010102 | F03- BATHLAHALLI | AGRI | DLMS Meter | 0.96432 | 0.86784 | 0 | 0.96432 | 10.005 | 10.005
2894 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901010103 | F04-THOPPANAHALLI | AGRI | DLMS Meter | 0.85534 | 0.77007 | 0 | 0.85534 | 9.9696 | 9.9696
2895 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901010104 | F05-BISANATHAM | AGRI | DLMS Meter | 0.94918 | 0.85428 | 0 | 0.94918 | 9.9979 | 9.9979
2896 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901020302 | F07-BHEEMAGANAHALLI | AGRI | DLMS Meter | 0.9333 | 0.84008 | 0 | 0.9333 | 9.9877 | 9.9877
2897 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901020303 | F08-MUSTRAHALLI | AGRI | DLMS Meter | 0.58234 | 0.52419 | 0 | 0.58234 | 9.9854 | 9.9854
2898 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901020304 | F09-DP HALLI | AGRI | DLMS Meter | 0.85716 | 0.7714 | 0 | 0.85716 | 10.005 | 10.005
2899 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901020305 | F10-TAMATAMAKANAHALLI | AGRI | DLMS Meter | 1.0456 | 0.94108 | 0 | 1.0456 | 9.9998 | 9.9998
2900 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901010302 | F11-NJY TALLUR | NJY | DLMS Meter | 1.139 | 1.0474 | 0 | 1.139 | 8.0481 | 69.8268
2901 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901020306 | F12-BOGLAHALLI | AGRI | DLMS Meter | 0.94686 | 0.85203 | 0 | 0.94686 | 10.0151 | 10.0151
2902 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901010106 | F13-JANAGUTTA NJY | NJY | DLMS Meter | 1.1275 | 1.0501 | 0 | 1.1275 | 6.863 | 58.9846
2903 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901010108 | F14-KADIRIPURA | AGRI | DLMS Meter | 0.74356 | 0.66898 | 0 | 0.74356 | 10.0299 | 10.4751
2904 | BRAZ | KOLAR | KGF | BANGARAPETE | KAMASAMUDRA_66 | 1230203901010107 | F15-DINNUR NJY | NJY | DLMS Meter | 0.56466 | 0.52298 | 0 | 0.56466 | 7.3813 | 67.4913
2905 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901010101 | F01-DODDAMUDAVADI | AGRI | DLMS Meter | 0.72706 | 0.64541 | 0.01 | 0.71706 | 9.9919 | 9.9919
2906 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901010102 | F02-V-R-DODDI | AGRI | DLMS Meter | 1.2972 | 1.1672 | 0 | 1.2972 | 10.0197 | 10.0197
2907 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901010103 | F04-TOWN-2 | URBAN MIXED LOAD | DLMS Meter | 2.5706 | 2.3913 | 0.04851 | 2.5221 | 5.1837 | 16.0382
2908 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901010104 | F05-SHIVANAHALLI | AGRI | DLMS Meter | 1.0954 | 0.98558 | 0 | 1.0954 | 10.0287 | 11.346
2909 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901010105 | F06-MANIYAMBAL | AGRI | DLMS Meter | 2.1098 | 1.8991 | 0 | 2.1098 | 9.9859 | 9.9859
2910 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901010106 | F07-KHB | DOMESTIC | DLMS Meter | 2.4501 | 1.7943 | 0.55377 | 1.8963 | 5.3794 | 13.3436
2911 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901010107 | F08-HUNASANAHALLI | AGRI | DLMS Meter | 1.501 | 1.3372 | 0.015 | 1.486 | 10.0134 | 10.0134
2912 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901020302 | F09-HAROHALLY | AGRI | DLMS Meter | 1.482 | 0.85237 | 0.535 | 0.947 | 9.9928 | 9.9928
2913 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901020304 | F11-DODDALAHALLY | AGRI | DLMS Meter | 0.96636 | 0.84821 | 0.024 | 0.94236 | 9.9907 | 9.9907
2914 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901020305 | F12-KODIHALLI | AGRI | DLMS Meter | 1.7418 | 1.5672 | 0 | 1.7418 | 10.0253 | 10.0253
2915 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901020301 | F13-BEKUPPE-NJY | NJY | DLMS Meter | 0.63908 | 0.36578 | 0.2489 | 0.39018 | 6.2533 | 57.707
2916 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901020306 | F14-TOWN | URBAN MIXED LOAD | DLMS Meter | 0.5188 | 0.39238 | 0.099 | 0.4198 | 6.5327 | 26.6524
2917 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901020101 | F15-CHIRANAKUPPE-NJY | NJY | DLMS Meter | 0.42854 | 0.28532 | 0.1214 | 0.30714 | 7.1046 | 45.4487
2918 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901010108 | F16-GADASAHALLI | NJY | DLMS Meter | 1.0476 | 0.64354 | 0.361 | 0.6866 | 6.272 | 45.3401
2919 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901010118 | F17-SUNDAGATTA NJY | NJY | DLMS Meter | 0.7676 | 0.40839 | 0.33 | 0.4376 | 6.675 | 57.0914
2920 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901010119 | F18-DIARY | INDUSTRIAL | DLMS Meter | 3.0199 | 2.9682 | 0 | 3.0199 | 1.713 | 1.713
2921 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901010101 | F01-OUR-NATIVE-VILLAGE | AGRI | DLMS Meter | 0.39072 | 0.35158 | 0 | 0.39072 | 10.0161 | 10.0161
2922 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901010102 | F02-KANASWADI | AGRI | DLMS Meter | 0.80064 | 0.7208 | 0 | 0.80064 | 9.9717 | 9.9717
2923 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901010103 | F03-THIMMASANDRA | AGRI | DLMS Meter | 0.85648 | 0.77128 | 0 | 0.85648 | 9.9479 | 9.9479
2924 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901010104 | F04-BSNL | URBAN MIXED LOAD | DLMS Meter | 1.5147 | 1.3433 | 0.003 | 1.5117 | 11.1425 | 16.4523
2925 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901010301 | F05-BTS-MILL | INDUSTRIAL | DLMS Meter | 2.7754 | 2.5913 | 0.0093 | 2.7661 | 6.3204 | 7.9918
2926 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901010302 | F06-MALLOHALLI | AGRI | DLMS Meter | 0.89068 | 0.80163 | 0 | 0.89068 | 9.9976 | 9.9976
2927 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901010303 | F07-KANNAMANGALA | AGRI | DLMS Meter | 0.72142 | 0.6491 | 0 | 0.72142 | 10.0253 | 10.0253
2928 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901010304 | F08-RAMDEVANAHALLI | AGRI | DLMS Meter | 0.3471 | 0.31242 | 0 | 0.3471 | 9.9924 | 9.9924
2929 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901010105 | F09-PUTTENAHALLI | NJY | DLMS Meter | 0.40618 | 0.36998 | 0 | 0.40618 | 8.9134 | 41.8408
2930 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901020101 | F10-MARASANDRA | NJY | DLMS Meter | 1.5155 | 0.21059 | 1.2819 | 0.23356 | 9.8349 | 40.5829
2931 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | KANASWADI_66 | 1210101901010108 | F11-ISTHURU | NJY | DLMS Meter | 1.1176 | 0.97325 | 0 | 1.1176 | 12.9159 | 40.6841
2932 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | KANCHIPURA_66 | 1310204906010109 | F01-KANCHIPURA | AGRI | DLMS Meter | 0.25858 | 0.23263 | 0 | 0.25858 | 10.0348 | 10.0348
2933 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | KANCHIPURA_66 | 1310204906010102 | F02-KITTADALU | AGRI | DLMS Meter | 0.6456 | 0.58092 | 0 | 0.6456 | 10.0186 | 10.0186
2934 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | KANCHIPURA_66 | 1310204906010103 | F03-KADAVIGERE | AGRI | DLMS Meter | 0.6553 | 0.58969 | 0 | 0.6553 | 10.0122 | 10.0122
2935 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | KANCHIPURA_66 | 1310204906010104 | F04-OBALAPURA | AGRI | DLMS Meter | 0.51026 | 0.4592 | 0 | 0.51026 | 10.0065 | 10.0065
2936 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | KANCHIPURA_66 | 1310204906010105 | F05-VENGALAPURA | NJY | DLMS Meter | 0.3134 | 0.27407 | 0 | 0.3134 | 12.5508 | 49.4122
2937 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | KANCHIPURA_66 | 1310204906010107 | F06-N N KATTE | NJY | DLMS Meter | 0.4564 | 0.13447 | 0.3021 | 0.1543 | 12.8548 | 24.4874
2938 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | KANCHIPURA_66 | 1310204906010108 | F07-D K KATTE | NJY | DLMS Meter | 0.2101 | 0.18639 | 0 | 0.2101 | 11.286 | 46.356
2939 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | KANCHIPURA_66 | 1310204906010106 | F08-SHIVANAGARA | NJY | DLMS Meter | 0.2236 | 0.19618 | 0 | 0.2236 | 12.2648 | 40.2988
2940 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | KANCHIPURA_66 | 1310204906020301 | F09-J.S.PURA | AGRI | DLMS Meter | 0.7894 | 0.71008 | 0 | 0.7894 | 10.0478 | 10.0478
2941 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | KANCHIPURA_66 | 1310204906010101 | F10-CBKERE | AGRI | DLMS Meter | 0.4444 | 0.39981 | 0 | 0.4444 | 10.0347 | 10.0347
2942 | BMANZ | EAST | VIDHANASOUDHA | W5 | KANTEERVA_66 | 1130103901010101 | F01-PANJAB-NATIONAL-BANK | URBAN MIXED LOAD | DLMS Meter | 1.5786 | 1.0347 | 0.4878 | 1.0908 | 5.1459 | 5.7798
2943 | BMANZ | EAST | VIDHANASOUDHA | W5 | KANTEERVA_66 | 1130103901010102 | F02-RBI | COMMERCIAL | DLMS Meter | 2.6075 | 2.0419 | 0.4998 | 2.1077 | 3.1216 | 12.0089
2944 | BMANZ | EAST | VIDHANASOUDHA | W5 | KANTEERVA_66 | 1130103901010103 | F03-SUNKALPET | URBAN MIXED LOAD | DLMS Meter | 1.9675 | 1.5622 | 0.31065 | 1.6569 | 5.7125 | 5.7125
2945 | BMANZ | EAST | VIDHANASOUDHA | W4 | KANTEERVA_66 | 1130103901020305 | F04-ADARSHA SHANGRILLA | COMMERCIAL | DLMS Meter | 1.8689 | 1.8144 | 0 | 1.8689 | 2.9152 | 2.9152
2946 | BMANZ | EAST | VIDHANASOUDHA | W4 | KANTEERVA_66 | 1130103901020306 | F05-RAJBHAVAN | GOVERNMENT OFFICES | DLMS Meter | 0.46542 | 0.44427 | 0 | 0.46542 | 4.5448 | 6.2321
2947 | BMANZ | EAST | VIDHANASOUDHA | W5 | KANTEERVA_66 | 1130103901010109 | F06-K.G.ROAD | URBAN MIXED LOAD | DLMS Meter | 2.4601 | 1.1415 | 1.2577 | 1.2024 | 5.0642 | 7.0414
2948 | BMASZ | SOUTH | JAYANAGAR | S2 | KANTEERVA_66 | 1130103901020301 | F08-RMU17ABBMP | URBAN MIXED LOAD | DLMS Meter | 1.929 | 1.215 | 0.66701 | 1.262 | 3.7193 | 9.0477
2949 | BMANZ | EAST | VIDHANASOUDHA | W5 | KANTEERVA_66 | 1130103901020302 | F09-OTC-ROAD | URBAN MIXED LOAD | DLMS Meter | 0.86681 | 0.75795 | 0.085432 | 0.78138 | 2.9989 | 3.3415
2950 | BMASZ | SOUTH | JAYANAGAR | S2 | KANTEERVA_66 | 1130103901010107 | F10-BEML | URBAN MIXED LOAD | DLMS Meter | 2.4571 | 2.209 | 0.15536 | 2.3018 | 4.0304 | 6.8197
2951 | BMASZ | SOUTH | JAYANAGAR | S2 | KANTEERVA_66 | 1130103901020303 | F11-RMU-01 SR NAGAR | URBAN MIXED LOAD | DLMS Meter | 1.8462 | 1.3865 | 0.39888 | 1.4474 | 4.2026 | 7.6955
2952 | BMASZ | SOUTH | JAYANAGAR | S2 | KANTEERVA_66 | 1130103901020304 | F12-PUREFORMA | URBAN MIXED LOAD | DLMS Meter | 3.0803 | 3.002 | 0 | 3.0803 | 2.5428 | 4.3167
2953 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KARADI_110 | 1320201910010101 | F01-KUPPURU | NJY | DLMS Meter | 0.5567 | 0.359 | 0.137 | 0.4197 | 14.4632 | 47.9732
2954 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KARADI_110 | 1320201910010103 | F02-BHADRAPURA | AGRI | DLMS Meter | 0.7328 | 0.46883 | 0.2 | 0.5328 | 12.0068 | 12.0068
2955 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KARADI_110 | 1320201910010104 | F03-BALLEKATTE | AGRI | DLMS Meter | 0.7613 | 0.63584 | 0.055 | 0.7063 | 9.9765 | 9.9765
2956 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KARADI_110 | 1320201910010102 | F04-SHETTIHALLI | AGRI | DLMS Meter | 0.5695 | 0.30982 | 0.215 | 0.3545 | 12.6037 | 12.6037
2957 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KARADI_110 | 1320201910010105 | F05-DEVARAHALLI | AGRI | DLMS Meter | 0.2612 | 0.14737 | 0.09558 | 0.16562 | 11.018 | 11.018
2958 | CTAZ | TUMKUR | TIPTUR | CN HALLY | KATHRIKEHAL_110 | 1320203902010101 | F01-THIRTHAPURA | AGRI | DLMS Meter | 1.2733 | 1.1223 | 0 | 1.2733 | 11.8576 | 11.8576
2959 | CTAZ | TUMKUR | TIPTUR | CN HALLY | KATHRIKEHAL_110 | 1320203902010102 | F02-DODDARAMPURA | AGRI | DLMS Meter | 1.4939 | 1.2809 | 0 | 1.4939 | 14.2589 | 14.2589
2960 | CTAZ | TUMKUR | TIPTUR | CN HALLY | KATHRIKEHAL_110 | 1320203902010103 | F03-BARASIDLEHALLI | AGRI | DLMS Meter | 0.9318 | 0.83858 | 0 | 0.9318 | 10.0043 | 10.0043
2961 | CTAZ | TUMKUR | TIPTUR | CN HALLY | KATHRIKEHAL_110 | 1320203902010104 | F04-SINGADAHALLI | AGRI | DLMS Meter | 0.91506 | 0.8058 | 0 | 0.91506 | 11.9401 | 11.9401
2962 | CTAZ | TUMKUR | TIPTUR | CN HALLY | KATHRIKEHAL_110 | 1320203902010105 | F05-KATHRIKEHAL | AGRI | DLMS Meter | 0.54062 | 0.43955 | 0.052 | 0.48862 | 10.0418 | 10.0418
2963 | CTAZ | TUMKUR | TIPTUR | CN HALLY | KATHRIKEHAL_110 | 1320203902010107 | F06-HOMBALAGATTA | AGRI | DLMS Meter | 0.099002 | 0.089021 | 0 | 0.099002 | 10.0816 | 10.0816
2964 | CTAZ | TUMKUR | TIPTUR | CN HALLY | KATHRIKEHAL_110 | 1320203902010106 | F07-JANEHAR NJY | NJY | DLMS Meter | 0.5927 | 0.53478 | 0 | 0.5927 | 9.7724 | 63.9282
2965 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | KATTIGE_66 | 1310302903020302 | F10-GUDDEHALLI | AGRI | DLMS Meter | 0.4774 | 0.42964 | 0 | 0.4774 | 10.0038 | 10.0038
2966 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | KATTIGE_66 | 1310302903010102 | F02-JEENAHALLI/KATTIGE | AGRI | DLMS Meter | 0.81968 | 0.7377 | 0 | 0.81968 | 10.0015 | 10.0015
2967 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | KATTIGE_66 | 1310302903010103 | F03-SORTUR | AGRI | DLMS Meter | 1.2617 | 1.1074 | 0 | 1.2617 | 12.2289 | 12.2289
2968 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | KATTIGE_66 | 1310302903010104 | F04-HATTUR AGRI | AGRI | DLMS Meter | 1.1299 | 0.98961 | 0 | 1.1299 | 12.4162 | 12.4162
2969 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | KATTIGE_66 | 1310302903010106 | F06-ARUNDI NJY | NJY | DLMS Meter | 1.199 | 1.1139 | 0 | 1.199 | 7.1014 | 11.456
2970 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | KATTIGE_66 | 1310302903010107 | F07-THIRTHARAMESHWARA NJY | NJY | DLMS Meter | 0.4163 | 0.34187 | 0.024469 | 0.39183 | 12.7504 | 31.4538
2971 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | KATTIGE_66 | 1310302903020301 | F09-BELAGUTTI | AGRI | DLMS Meter | 0.76787 | 0.7128 | 0 | 0.76787 | 7.1715 | 7.1715
2972 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KATTIGE_66 | 1310302903020303 | F11-H KADADAKATTE NJY | NJY | DLMS Meter | 0.4908 | 0.41646 | 0.019925 | 0.47088 | 11.5563 | 20.7306
2973 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KATTIGE_66 | 1310302903020304 | F12-S MALLAPURA NJY | NJY | DLMS Meter | 0.6574 | 0.18198 | 0.45622 | 0.20118 | 9.5422 | 29.6949
2974 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902010101 | F02-KUNDUR | AGRI | DLMS Meter | 0.6734 | 0.60587 | 0 | 0.6734 | 10.0282 | 10.0282
2975 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902010102 | F03-RAJATHADRIPURA | AGRI | DLMS Meter | 1.5105 | 1.3262 | 0 | 1.5105 | 12.2049 | 12.2049
2976 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902010103 | F04-K.B.CROSS | AGRI | DLMS Meter | 0.61752 | 0.55571 | 0 | 0.61752 | 10.0087 | 10.0087
2977 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902010104 | F05-DAIRY | RURAL MIXED LOAD | DLMS Meter | 0.48244 | 0.35799 | 0.0765 | 0.40594 | 11.812 | 11.812
2978 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902020301 | F06-ARALAGUPPE | AGRI | DLMS Meter | 0.56588 | 0.50935 | 0 | 0.56588 | 9.9901 | 10.258
2979 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902020302 | F08-GADABANAHALLI | AGRI | DLMS Meter | 0.81256 | 0.62327 | 0.12 | 0.69256 | 10.0052 | 10.0052
2980 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902020303 | F09-BILIGERE | AGRI | DLMS Meter | 0.8777 | 0.78992 | 0 | 0.8777 | 10.0014 | 10.0014
2981 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902020304 | F10-KARADI | AGRI | DLMS Meter | 0.93232 | 0.83885 | 0 | 0.93232 | 10.0253 | 10.0253
2982 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902020305 | F11-HALAGUNA | AGRI | DLMS Meter | 0.72626 | 0.65356 | 0 | 0.72626 | 10.0095 | 10.0095
2983 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902020306 | F12-NJY-KIBBANAHALLI | NJY | DLMS Meter | 0.79708 | 0.51793 | 0.19 | 0.60708 | 14.685 | 42.484
2984 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902020307 | F13-KUPPALU | AGRI | DLMS Meter | 0.00944 | 0.000496 | 0.00888 | 0.00056 | 11.4286 | 13.8322
2985 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902020308 | F14-NJY-BEERASANDRA | NJY | DLMS Meter | 0.65448 | 0.51603 | 0.054 | 0.60048 | 14.0632 | 20.1602
2986 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902010107 | F15-HINDISKERE NJY | NJY | DLMS Meter | 0.1434 | 0.12841 | 0 | 0.1434 | 10.4526 | 48.4299
2987 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902010109 | F16-BAREPALYA | AGRI | DLMS Meter | 0.9546 | 0.85889 | 0 | 0.9546 | 10.0257 | 10.0257
2988 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KBCROSS_220 | 1320201902010108 | F17-BYADARAHALLI | AGRI | DLMS Meter | 1.1024 | 0.89192 | 0.1 | 1.0024 | 11.0213 | 11.0213
2989 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903010102 | F03-AMARJYOTHI-LAYOUT | DOMESTIC | DLMS Meter | 0.69703 | 0.62837 | 0.045 | 0.65203 | 3.629 | 5.8607
2990 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903010103 | F04-RUNWAY | COMMERCIAL | DLMS Meter | 1.0769 | 0.96541 | 0.08 | 0.99689 | 3.1576 | 7.4294
2991 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903020101 | F06-FCHALLGATTA | DOMESTIC | DLMS Meter | 1.1995 | 0.8374 | 0.32791 | 0.87156 | 3.9197 | 3.9197
2992 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903020301 | F07-FCONTROL-TOWERS | INDUSTRIAL | DLMS Meter | 1.2 | 1.1542 | 0.02 | 1.18 | 2.1855 | 7.5526
2993 | BMASZ | SOUTH | KORAMANGALA | S17 | KC_VALLEY_66 | 1110201903020302 | F08-KEMPAPURA | DOMESTIC | DLMS Meter | 4.6111 | 3.7939 | 0.55199 | 4.0591 | 6.5331 | 6.5331
2994 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903020303 | F09-VERIFONE | COMMERCIAL | DLMS Meter | 2.4229 | 0.65617 | 1.7367 | 0.68622 | 4.3786 | 4.3786
2995 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903020304 | F10-BWSSB | COMMERCIAL | DLMS Meter | 4.5443 | 4.4068 | 0.02 | 4.5243 | 2.5986 | 4.0076
2996 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903020305 | F11-GOLF-LINK-SOFTWARE | INDUSTRIAL | DLMS Meter | 0.69221 | 0.66375 | 0.005 | 0.68721 | 3.413 | 8.8117
2997 | BMASZ | SOUTH | KORAMANGALA | S17 | KC_VALLEY_66 | 1110201903020401 | F12-BWSSB | COMMERCIAL | DLMS Meter | 3.3765 | 3.0752 | 0.11245 | 3.264 | 5.7853 | 8.4326
2998 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903010105 | F13-INTEL | COMMERCIAL | DLMS Meter | 1.0177 | 0.93073 | 0.055 | 0.96266 | 3.3164 | 3.3164
2999 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903010106 | F14-GOLDMAN-FACHAE | COMMERCIAL | DLMS Meter | 0.76707 | 0.68082 | 0.06 | 0.70707 | 3.7136 | 3.7136
3000 | BMANZ | EAST | WHITEFIELD | E4 | EPIP_66 | 1130202907010107 | F19-SHRIRAM-SAMRUDHI | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3001 | BMASZ | SOUTH | HSR | S12 | SOUTHCITY_66 | 1110304903010104 | F21-BB,-SUNCITY-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3002 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902010107 | F13-DEVAMACHOHALLI | RURAL MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3003 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | DAVANAGERE_66 | 1310101901010103 | F03-MANDIPETE | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3004 | BMASZ | SOUTH | KORAMANGALA | S17 | KC_VALLEY_66 | 1110201903010107 | F15-SIGNATURE | COMMERCIAL | DLMS Meter | 2.3232 | 2.1229 | 0.12316 | 2.2 | 3.5053 | 3.5053
3005 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903010108 | F16-CHERRY-HILL | INDUSTRIAL | DLMS Meter | 1.4679 | 0 | 1.4679 | 7.0487e-10 | 0 | #DIV/0!
3006 | BMASZ | SOUTH | KORAMANGALA | S17 | KC_VALLEY_66 | 1110201903010201 | F17-MAHESH-KHAITAN | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3007 | BMASZ | SOUTH | KORAMANGALA | S17 | KC_VALLEY_66 | 1110201903010202 | F18-PANATHUR | DOMESTIC | DLMS Meter | 3.0565 | 2.9035 | 0 | 3.0565 | 5.0049 | 8.1291
3008 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903020402 | F20-SPANDANA-APARTMENTS | DOMESTIC | DLMS Meter | 0.74392 | 0.72684 | 0 | 0.74392 | 2.296 | 4.5111
3009 | BMASZ | SOUTH | KORAMANGALA | S3 | KC_VALLEY_66 | 1110201903020403 | F21-IAM-RESEARCH-CENTER | COMMERCIAL | DLMS Meter | 1e-06 | 0 | 0 | 1e-06 | 0 | #DIV/0!
3010 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KEMBODI_66 | 1230102902010101 | F02-ABBANI | AGRI | DLMS Meter | 1.3132 | 1.1685 | 0 | 1.3132 | 11.0182 | 11.0182
3011 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KEMBODI_66 | 1230102902010102 | F03-KEMBODI | AGRI | DLMS Meter | 1.3524 | 1.2022 | 0 | 1.3524 | 11.1073 | 11.1073
3012 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KEMBODI_66 | 1230102902010103 | F04-NJY-HOLALI | NJY | DLMS Meter | 1.731 | 1.2598 | 0.3 | 1.431 | 11.9663 | 61.2315
3013 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KEMBODI_66 | 1230102902020301 | F05-LOTUSFARM | NJY | DLMS Meter | 1.835 | 0.28684 | 1.52 | 0.315 | 8.9389 | 8.9389
3014 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KEMBODI_66 | 1230102902020302 | F06-VITTAPANAHALLI | AGRI | DLMS Meter | 1.3098 | 1.1412 | 0 | 1.3098 | 12.8751 | 12.8751
3015 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KEMBODI_66 | 1230102902020303 | F07-NJY-SEESANDRA | NJY | DLMS Meter | 0.5824 | 0.51993 | 0 | 0.5824 | 10.7267 | 70.2496
3016 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KEMBODI_66 | 1230102902020304 | F08-RAMASANDRA | AGRI | DLMS Meter | 1.1874 | 1.0576 | 0 | 1.1874 | 10.932 | 10.932
3017 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | KEMPANAHALLI_66 | 1220101903010101 | F01-KEMPANAHALLI | URBAN MIXED LOAD | DLMS Meter | 0.1986 | 0.1833 | 0 | 0.1986 | 7.7034 | 22.3121
3018 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | KEMPANAHALLI_66 | 1220101903010102 | F02-KEPFHEGGADAGERE | AGRI | DLMS Meter | 0.92182 | 0.84767 | 0 | 0.92182 | 8.0439 | 8.6066
3019 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | KEMPANAHALLI_66 | 1220101903010105 | F03-URAGAHALLI | INDUSTRIAL | DLMS Meter | 0 | 7.4e-05 | 0 | 0 | 0 | #DIV/0!
3020 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | KEMPANAHALLI_66 | 1220101903010104 | F04-MAYAGANAHALLY | AGRI | DLMS Meter | 0.7577 | 0.60226 | 0.08845 | 0.66925 | 10.0104 | 10.0104
3021 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | KEMPANAHALLI_66 | 1220101903010103 | F05-INDUSTRIAL | URBAN MIXED LOAD | DLMS Meter | 0.77988 | 0.69556 | 0.02897 | 0.75091 | 7.3709 | 8.0793
3022 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | KEMPANAHALLI_66 | 1220101903010106 | F06-ABM BUILDTECH LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0.050195 | 0.047059 | 0.0009 | 0.049295 | 4.5349 | 34.7973
3023 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | KEMPANAHALLI_66 | 1220101903020302 | F07-KENCHANAKUPPE | URBAN MIXED LOAD | DLMS Meter | 2.4527 | 0.81654 | 1.5598 | 0.89289 | 8.5507 | 16.6672
3024 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | KEMPANAHALLI_66 | 1220101903020303 | F08-CHUNCHAGA NJY | NJY | DLMS Meter | 0.95556 | 0.74534 | 0.143 | 0.81256 | 8.2726 | 24.2618
3025 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | KEMPANAHALLI_66 | 1220101903020301 | F09-URAGAHALLI CRUSHER | INDUSTRIAL | DLMS Meter | 2.4526 | 2.4616 | 0 | 2.4526 | -0.36782 | 1.0554
3026 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | KEMPANAHALLI_66 | 1220101903020304 | F10-MADAPURA NJY | NJY | DLMS Meter | 1.1803 | 0.91356 | 0.18606 | 0.99425 | 8.116 | 19.4834
3027 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904010101 | F01-KEMPANAHALLI | AGRI | DLMS Meter | 1.2423 | 0.90971 | 0.23 | 1.0123 | 10.1358 | 10.1358
3028 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904010102 | F02-YEDEHALLI | AGRI | DLMS Meter | 0.74758 | 0.58277 | 0.1 | 0.64758 | 10.0082 | 10.0082
3029 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904010103 | F03-KULUMEPALYA | AGRI | DLMS Meter | 0.51162 | 0.46044 | 0 | 0.51162 | 10.0029 | 10.0029
3030 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904010104 | F04-KUNDUR | AGRI | DLMS Meter | 0.6545 | 0.58894 | 0 | 0.6545 | 10.0174 | 10.0174
3031 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904010105 | F05-SHIVAPURA NJY | NJY | DLMS Meter | 0.315 | 0.20207 | 0.082 | 0.233 | 13.2742 | 65.1542
3032 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904010106 | F06-NJY-YADEHALLI | NJY | DLMS Meter | 1.0504 | 0.95766 | 0 | 1.0504 | 8.8271 | 53.4551
3033 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904020301 | F07-SEEGEPALYA | AGRI | DLMS Meter | 0.60314 | 0.54276 | 0 | 0.60314 | 10.0103 | 10.0103
3034 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904020304 | F08 HUTHRI | AGRI | DLMS Meter | 0.66176 | 0.57742 | 0 | 0.66176 | 12.7443 | 12.7443
3035 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904020305 | F09-HALUVAGILU | AGRI | DLMS Meter | 0.12138 | 0.10913 | 0 | 0.12138 | 10.0956 | 10.0956
3036 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904020303 | F10 CHANNAPURA | AGRI | DLMS Meter | 0.7454 | 0.64508 | 0.02 | 0.7254 | 11.0726 | 11.0726
3037 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904020302 | F11-NJY RAJGERE | NJY | DLMS Meter | 0.2224 | 0.19437 | 0.006 | 0.2164 | 10.1821 | 56.0917
3038 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KEMPANAHALLI_TMK_66 | 1320110904010107 | F12-DHAANASHREE STONE CRUSHER | INDUSTRIAL | DLMS Meter | 0.084 | 0.086665 | 0 | 0.084 | -3.1726 | -3.1724
3039 | BMASZ | WEST | KENGERI | K4 | KENGERI_SATELLITE_TOWN_66 | 1140301901010101 | F01-NEW-KHB | DOMESTIC | DLMS Meter | 0.57089 | 0.50614 | 0.026 | 0.54489 | 7.1113 | 11.8146
3040 | BMASZ | WEST | KENGERI | K4 | KENGERI_SATELLITE_TOWN_66 | 1140301901010106 | F02-NEW KHB LAYOUT 2IDLE | DOMESTIC | DLMS Meter | 0.27443 | 0.18302 | 0.08417 | 0.19026 | 3.8056 | 3.8056
3041 | BMASZ | WEST | KENGERI | K1 | KENGERI_SATELLITE_TOWN_66 | 1140301901010102 | F03-NEW-KHB | DOMESTIC | DLMS Meter | 5.1128 | 3.9492 | 0.9427 | 4.1701 | 5.298 | 11.6985
3042 | BMASZ | WEST | KENGERI | K4 | KENGERI_SATELLITE_TOWN_66 | 1140301901010103 | F04-SUN-CITY | DOMESTIC | DLMS Meter | 0.95441 | 0.82876 | 0.061989 | 0.89242 | 7.1336 | 18.0725
3043 | BMASZ | WEST | KENGERI | K1 | KENGERI_SATELLITE_TOWN_66 | 1140301901010104 | F05-HUNSEMARADAPALYA | URBAN MIXED LOAD | DLMS Meter | 4.1889 | 3.6125 | 0.35698 | 3.8319 | 5.7246 | 16.5593
3044 | BMASZ | WEST | KENGERI | K4 | KENGERI_SATELLITE_TOWN_66 | 1140301901010105 | F06-FSHIRKE | DOMESTIC | DLMS Meter | 1.9367 | 0.61731 | 1.264 | 0.67273 | 8.2382 | 12.5268
3045 | BMASZ | WEST | KENGERI | K4 | KENGERI_SATELLITE_TOWN_66 | 1140301901020301 | F07-ROBIN-THEATRE | URBAN MIXED LOAD | DLMS Meter | 2.8949 | 2.694 | 0 | 2.8949 | 6.9398 | 11.5857
3046 | BMASZ | WEST | KENGERI | K4 | KENGERI_SATELLITE_TOWN_66 | 1140301901020302 | F08-HOYSALA-CIRCLE | URBAN MIXED LOAD | DLMS Meter | 2.9309 | 2.7685 | 0 | 2.9309 | 5.5381 | 11.3409
3047 | BMASZ | WEST | KENGERI | K4 | KENGERI_SATELLITE_TOWN_66 | 1140301901020303 | F09-SATELLITE-CLUB | URBAN MIXED LOAD | DLMS Meter | 1.0127 | 0.91351 | 0.056 | 0.9567 | 4.5141 | 24.5753
3048 | BMASZ | WEST | KENGERI | K1 | KENGERI_SATELLITE_TOWN_66 | 1140301901020304 | F10-KOMMAGATTA | URBAN MIXED LOAD | DLMS Meter | 1.6301 | 1.3733 | 0.17353 | 1.4566 | 5.7189 | 24.5361
3049 | BMASZ | WEST | KENGERI | K4 | KENGERI_SATELLITE_TOWN_66 | 1140301901020305 | F11-APOORVA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.4571 | 1.1711 | 0.2105 | 1.2466 | 6.0597 | 13.1523
3050 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | KEREBILACHI_66 | 1310107905010102 | F01-KEREBILACHI | NJY | DLMS Meter | 1.0109 | 0.8239 | 0.082 | 0.92894 | 11.3077 | 36.8578
3051 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | KEREBILACHI_66 | 1310107905010101 | F02-WATER WORKS | WATER WORKS | DLMS Meter | 0.41742 | 0.40235 | 0 | 0.41742 | 3.6108 | 64.7755
3052 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | KEREBILACHI_66 | 1310107905010104 | F03-HOSUR IP | AGRI | DLMS Meter | 0.68766 | 0.554 | 0.072 | 0.61566 | 10.0161 | 10.0161
3053 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | KEREBILACHI_66 | 1310107905010103 | F04-ALUR NJY | NJY | DLMS Meter | 0.28002 | 0.18023 | 0.078 | 0.20202 | 10.7855 | 36.6621
3054 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | KEREBILACHI_66 | 1310107905020103 | F05-SOMALAPURA IP | AGRI | DLMS Meter | 1.0222 | 0.91956 | 0 | 1.0222 | 10.0377 | 10.0377
3055 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | KEREBILACHI_66 | 1310107905020104 | F06-CHANNAPURA | AGRI | DLMS Meter | 1.3648 | 1.1473 | 0.09 | 1.2748 | 10.0027 | 10.0027
3056 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | KEREBILACHI_66 | 1310107905020101 | F07-SOMALAPURA NJY | NJY | DLMS Meter | 0.82252 | 0.31466 | 0.469 | 0.35352 | 10.9924 | 42.3092
3057 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | KEREBILACHI_66 | 1310107905020102 | F08-ALURU IP | AGRI | DLMS Meter | 0.86772 | 0.78055 | 0 | 0.86772 | 10.0454 | 10.0454
3058 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KEREKODI_110 | 1320201908010101 | F01-RANGAPURA | AGRI | DLMS Meter | 0.60354 | 0.52543 | 0.02 | 0.58354 | 9.9582 | 9.9582
3059 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KEREKODI_110 | 1320201908010112 | F02-SRI MATA | AGRI | DLMS Meter | 0.3268 | 0.2141 | 0.08 | 0.2468 | 13.2484 | 13.2484
3060 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KEREKODI_110 | 1320201908010110 | F03-DASIHALLI | AGRI | DLMS Meter | 0.47336 | 0.42595 | 0 | 0.47336 | 10.0158 | 10.0158
3061 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KEREKODI_110 | 1320201908010109 | F04-HOGAVANAGATTA NJY | NJY | DLMS Meter | 0.27043 | 0.22981 | 0.0055 | 0.26493 | 13.2599 | 44.7394
3062 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KEREKODI_110 | 1320201908010102 | F05-RAMACHNDRAPURA | AGRI | DLMS Meter | 1.0089 | 0.9081 | 0 | 1.0089 | 9.9931 | 9.9931
3063 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KEREKODI_110 | 1320201908010103 | F06-DASARIGHATTA | AGRI | DLMS Meter | 0.70088 | 0.63092 | 0 | 0.70088 | 9.9816 | 9.9816
3064 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KEREKODI_110 | 1320201908010111 | F08-NAGARAGATTA NJY | NJY | DLMS Meter | 0.2819 | 0.24634 | 0.01 | 0.2719 | 9.4004 | 37.3044
3065 | CTAZ | TUMKUR | TIPTUR | TIPTUR | KEREKODI_110 | 1320201908010106 | F09-NARASIKATTE | NJY | DLMS Meter | 0.3281 | 0.29052 | 0.006 | 0.3221 | 9.8041 | 38.4327
3066 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902030502 | F02-KAMASAMUDRA | AGRI | DLMS Meter | 1.2542 | 1.1288 | 0 | 1.2542 | 10.0014 | 10.7618
3067 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902020301 | F04-BEML-NAGAR | DOMESTIC | DLMS Meter | 1.8601 | 1.7098 | 0 | 1.8601 | 8.0804 | 29.721
3068 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902030504 | F05-JAYAMANGALA | AGRI | DLMS Meter | 1.39 | 1.2512 | 0 | 1.39 | 9.9815 | 9.9815
3069 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902010101 | F08-KRG-HALLI | AGRI | DLMS Meter | 0.481 | 0.43289 | 0 | 0.481 | 10.001 | 10.001
3070 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902010102 | F09-KANGANDLAHALLI | AGRI | DLMS Meter | 0.27768 | 0.24986 | 0 | 0.27768 | 10.0202 | 10.0202
3071 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902030505 | F11-BALAMANDE | AGRI | DLMS Meter | 1.1191 | 1.0075 | 0 | 1.1191 | 9.9777 | 9.9777
3072 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902020303 | F13-KESARANAHALLI | AGRI | DLMS Meter | 0.30926 | 0.27849 | 0 | 0.30926 | 9.9502 | 9.9502
3073 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902010103 | F14-ANDERSONPET-RURAL | AGRI | DLMS Meter | 1.3838 | 1.2454 | 0 | 1.3838 | 10.0013 | 10.0013
3074 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902020703 | F16-KAMMASANDRA | NJY | DLMS Meter | 1.0675 | 0.98732 | 0 | 1.0675 | 7.5114 | 64.0374
3075 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902020702 | F17-VIRUPAKSHAPURA NJY | NJY | DLMS Meter | 0.4133 | 0.37576 | 0 | 0.4133 | 9.0831 | 71.1902
3076 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902020701 | F18-DODDACHINAHALLI NJY | NJY | DLMS Meter | 0.44838 | 0.40704 | 0 | 0.44838 | 9.219 | 65.4637
3077 | BRAZ | KOLAR | KGF | KGF | ANDERSONPET_66 | 1230201901020303 | F07-ROBERTSONPET | URBAN MIXED LOAD | DLMS Meter | 3.4256 | 3.1484 | 0 | 3.4256 | 8.0923 | 8.4016
3078 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906010101 | F01-N.S.DEVARAHATTI | AGRI | DLMS Meter | 1.5569 | 1.3516 | 0 | 1.5569 | 13.1825 | 13.1825
3079 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906010102 | F02-SURIGENAHALLY | AGRI | DLMS Meter | 1.2054 | 0.93407 | 0.12585 | 1.0796 | 13.4779 | 13.683
3080 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906010103 | F03-UNGRA | AGRI | DLMS Meter | 1.3707 | 1.1761 | 0.005974 | 1.3647 | 13.8193 | 13.8193
3081 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906010501 | F04-KUNNALA | AGRI | DLMS Meter | 1.3537 | 1.2043 | 0 | 1.3537 | 11.0347 | 11.0347
3082 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906010502 | F05-KOPPA | AGRI | DLMS Meter | 2.1544 | 1.383 | 0.56954 | 1.5848 | 12.7366 | 12.7366
3083 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906010104 | F06-NAGASANDRA-NJY | NJY | DLMS Meter | 0.78233 | 0.69756 | 0 | 0.78233 | 10.8352 | 68.2287
3084 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906020301 | F07-KODIGENAHALLI | AGRI | DLMS Meter | 1.1436 | 0.61255 | 0.43746 | 0.70609 | 13.2482 | 13.2482
3085 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906020302 | F08-CHENGAVI | AGRI | DLMS Meter | 2.227 | 1.916 | 0 | 2.227 | 13.9642 | 13.9642
3086 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906020303 | F09-HOSAPALYA | AGRI | DLMS Meter | 1.1471 | 0.55988 | 0.51887 | 0.62823 | 10.8789 | 10.8789
3087 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906020304 | F10-MALLAPANAHALLI | AGRI | DLMS Meter | 1.6719 | 1.2647 | 0.25455 | 1.4174 | 10.7721 | 10.7721
3088 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | 1320106906010105 | F12-KONANAKERE-NJY | NJY | DLMS Meter | 0.88409 | 0.78252 | 0 | 0.88409 | 11.489 | 55.7878
3089 | CTAZ | TUMKUR | TUMKUR | GUBBI | KGTEMPLE_110 | #N/A | STA- | #N/A | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3090 | BMANZ | NORTH | HEBBAL | C7 | KHB_66 | 1120303902010101 | F01-BWSSB | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3091 | BMANZ | NORTH | HEBBAL | C7 | KHB_66 | 1120303902010102 | F02-PUTTENAHALLI | COMMERCIAL | DLMS Meter | 0.5432 | 0.42986 | 0.089 | 0.4542 | 5.3586 | 8.5374
3092 | BMANZ | NORTH | HEBBAL | C7 | KHB_66 | 1120303902010104 | F04-ISRO-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0.93792 | 0.87634 | 0 | 0.93792 | 6.5649 | 25.7265
3093 | BMANZ | NORTH | HEBBAL | C7 | KHB_66 | 1120303902010105 | F05-BESCOM | URBAN MIXED LOAD | DLMS Meter | 5.2904 | 4.7959 | 0.2 | 5.0904 | 5.7854 | 7.9674
3094 | BMANZ | NORTH | HEBBAL | C7 | KHB_66 | 1120303902010106 | F06-FRAJANUKUNTE | URBAN MIXED LOAD | DLMS Meter | 1.4486 | 0.29226 | 1.13 | 0.3186 | 8.2646 | 8.2646
3095 | BMANZ | NORTH | HEBBAL | C7 | KHB_66 | 1120303902020301 | F08-BYATHA | URBAN MIXED LOAD | DLMS Meter | 2.7607 | 2.2919 | 0.3976 | 2.3631 | 3.0145 | 3.0145
3096 | BMANZ | NORTH | HEBBAL | C7 | KHB_66 | 1120303902020101 | F09-SHIRKEY-MIG | INDUSTRIAL | DLMS Meter | 3.004 | 2.7293 | 0.15 | 2.854 | 4.3662 | 15.5259
3097 | BMANZ | NORTH | HEBBAL | C7 | KHB_66 | 1120303902020302 | F10-SHIRKEY-HIG | URBAN MIXED LOAD | DLMS Meter | 1.9805 | 1.9102 | 0 | 1.9805 | 3.5538 | 12.5698
3098 | BMANZ | NORTH | HEBBAL | C7 | KHB_66 | 1120303902020303 | F11-NAGARJUNA-LIG | URBAN MIXED LOAD | DLMS Meter | 3.6945 | 3.5323 | 0 | 3.6945 | 4.3908 | 12.0839
3099 | BMANZ | NORTH | JALAHALLI | C9 | KHB_66 | 1120303902020304 | F12-NAGARJUNA-MIG | COMMERCIAL | DLMS Meter | 3.6228 | 3.0566 | 0.163 | 3.4598 | 11.6533 | 19.8925
3100 | BMASZ | SOUTH | HSR | S12 | KHODAYSGLASS FACTORY_66 | 1110304902010101 | F02-AVALA-HALLI | URBAN MIXED LOAD | DLMS Meter | 2.3404 | 2.0583 | 0 | 2.3404 | 12.0542 | 22.3988
3101 | BMASZ | SOUTH | HSR | S12 | KHODAYSGLASS FACTORY_66 | 1110304902010103 | F03-ROYAL PARK | DOMESTIC | DLMS Meter | 0.7649 | 0.6759 | 0 | 0.7649 | 11.6351 | 17.4272
3102 | BMASZ | SOUTH | JAYANAGAR | S6 | KHODAYSGLASS FACTORY_66 | 1110304902020101 | F04-SHRINIDHI-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.1545 | 3.5304 | 0.40373 | 3.7508 | 5.8774 | 8.6326
3103 | BMASZ | SOUTH | JAYANAGAR | S6 | KHODAYSGLASS FACTORY_66 | 1110304902020102 | F05-KHODAY'S-GLASS-FACTORY | INDUSTRIAL | DLMS Meter | 1.0844 | 1.0423 | 0 | 1.0844 | 3.8792 | 3.8792
3104 | BMASZ | SOUTH | HSR | S12 | KHODAYSGLASS FACTORY_66 | 1110304902020103 | F06-RS CLUB HOUSE | DOMESTIC | DLMS Meter | 0.99312 | 0.87965 | 0 | 0.99312 | 11.4252 | 17.883
3105 | BMASZ | SOUTH | HSR | S12 | KHODAYSGLASS FACTORY_66 | 1110304902020104 | F07-SIR M V INDUSTRIAL AREA | URBAN MIXED LOAD | DLMS Meter | 1.1357 | 0.94998 | 0.049 | 1.0867 | 12.5817 | 12.5817
3106 | BMASZ | SOUTH | HSR | S12 | KHODAYSGLASS FACTORY_66 | 1110304902010105 | F08-SARATHI NAGAR | URBAN MIXED LOAD | DLMS Meter | 1.3744 | 1.2052 | 0 | 1.3744 | 12.3058 | 14.8472
3107 | BMASZ | SOUTH | JAYANAGAR | S6 | KHODAYSGLASS FACTORY_66 | 1110304902020301 | F09-DODDA-KALASANDRA | URBAN MIXED LOAD | DLMS Meter | 0.88944 | 0.78674 | 0.066652 | 0.82279 | 4.3811 | 13.23
3108 | BMASZ | SOUTH | HSR | S12 | KHODAYSGLASS FACTORY_66 | 1110304902020302 | F10-RAGAVANAPALYA | DOMESTIC | DLMS Meter | 0.54126 | 0.47426 | 0 | 0.54126 | 12.378 | 24.3071
3109 | BMASZ | SOUTH | HSR | S12 | KHODAYSGLASS FACTORY_66 | 1110304902020302 | F11-BANK-OFFICERS-COLONY | URBAN MIXED LOAD | DLMS Meter | 1.3644 | 1.1931 | 0 | 1.3644 | 12.5569 | 16.8791
3110 | BMASZ | SOUTH | HSR | S12 | KHODAYSGLASS FACTORY_66 | 1110304902020303 | F12-BCCH-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.1201 | 0.98113 | 0.008 | 1.1121 | 11.7801 | 23.6603
3111 | BMASZ | SOUTH | JAYANAGAR | S6 | KHODAYSGLASS FACTORY_66 | 1110304902020304 | F14-J-P-NAGAR-TH-PHASE | URBAN MIXED LOAD | DLMS Meter | 1.7056 | 1.3606 | 0.24946 | 1.4561 | 6.5575 | 6.5575
3112 | BMASZ | SOUTH | HSR | S12 | KHODAYSGLASS FACTORY_66 | 1110304902020305 | F15-SOBHA-APPARTMENT | URBAN MIXED LOAD | DLMS Meter | 1.4676 | 0.82688 | 0.515 | 0.95265 | 13.2023 | 19.1638
3113 | BMASZ | SOUTH | HSR | S12 | KHODAYSGLASS FACTORY_66 | 1110304902020307 | F16-SJS | URBAN MIXED LOAD | DLMS Meter | 0.92346 | 0.68855 | 0.155 | 0.76846 | 10.3991 | 19.0513
3114 | BMASZ | SOUTH | JAYANAGAR | S6 | KHODAYSGLASS FACTORY_66 | 1110304902020306 | F17-PRESTIGE FALCON CITY | DOMESTIC | DLMS Meter | 2.4959 | 2.3472 | 0 | 2.4959 | 5.9561 | 6.3681
3115 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KIADB HARDWARE PARK_220 | 1210205901030101 | F01-MOLEX AEROSPACE | INDUSTRIAL | DLMS Meter | 3.4495 | 3.3465 | 0 | 3.4495 | 2.9847 | 2.9847
3116 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | KIADB HARDWARE PARK_220 | 1210205901030103 | F03-BWSSB | INDUSTRIAL | DLMS Meter | 2.6177 | 2.4545 | 0 | 2.6177 | 6.2334 | 6.2334
3117 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | KIADB HARDWARE PARK_220 | 1210205901030104 | F04-MAHADEVAKODIGEHALLI | DOMESTIC | DLMS Meter | 1.1673 | 0.75804 | 0.32035 | 0.84693 | 10.4951 | 10.4951
3118 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | KIADB HARDWARE PARK_220 | 1210205901030107 | F07-CIPET | INDUSTRIAL | DLMS Meter | 1.8436 | 0.0087413 | 1.8345 | 0.0091 | 3.9423 | 3.9423
3119 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010102 | F02-BIRLA-SUPER | URBAN MIXED LOAD | DLMS Meter | 2.04 | 1.8006 | 0 | 2.04 | 11.7365 | 13.3823
3120 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010103 | F03-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 2.5393 | 2.4796 | 0 | 2.5393 | 2.3494 | 2.483
3121 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010104 | F04-ESSILOR | INDUSTRIAL | DLMS Meter | 2.3442 | 2.3668 | 0 | 2.3442 | -0.96449 | -0.96449
3122 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010105 | F05-KANASWADI | AGRI | DLMS Meter | 1.2897 | 1.161 | 0 | 1.2897 | 9.9795 | 9.9795
3123 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020301 | F06-YELLUPURA | URBAN MIXED LOAD | DLMS Meter | 1.1428 | 0.93362 | 0.068 | 1.0748 | 13.1354 | 16.4557
3124 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020302 | F07-KSSIDC | INDUSTRIAL | DLMS Meter | 4.3698 | 4.3065 | 0 | 4.3698 | 1.4495 | 2.3412
3125 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010106 | F09-BASHETTIHALLI | URBAN MIXED LOAD | DLMS Meter | 0.89976 | 0.88008 | 0 | 0.89976 | 2.1874 | 8.3244
3126 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010107 | F10-JALIGE | RURAL MIXED LOAD | DLMS Meter | 0.32864 | 0.29582 | 0 | 0.32864 | 9.9853 | 11.9133
3127 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020304 | F11-TAFE | INDUSTRIAL | DLMS Meter | 3.6717 | 3.6551 | 0 | 3.6717 | 0.45401 | 0.45605
3128 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020305 | F12-ARALU-MALLIGE | AGRI | DLMS Meter | 1.4794 | 1.3312 | 0 | 1.4794 | 10.0128 | 10.0128
3129 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010108 | F13-BUILDMET-FIBERS | INDUSTRIAL | DLMS Meter | 1.2352 | 1.1719 | 0 | 1.2352 | 5.127 | 9.9065
3130 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020306 | F14-ADVANCE CABLE | INDUSTRIAL | DLMS Meter | 4.323 | 4.2408 | 0 | 4.323 | 1.9018 | 2.5369
3131 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020307 | F15-DODDATUMKUR | NJY | DLMS Meter | 0.74256 | 4e-06 | 0.74256 | 0 | 0 | #DIV/0!
3132 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010109 | F16-TATA-STEEL | INDUSTRIAL | DLMS Meter | 0.52696 | 0.48202 | 0 | 0.52696 | 8.5274 | 8.5274
3133 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020308 | F17-APPEARL-PARK | INDUSTRIAL | DLMS Meter | 0 | 0.000376 | 0 | 0 | 0 | #DIV/0!
3134 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020309 | F18-SUPREME SOLAR | INDUSTRIAL | DLMS Meter | 0.34348 | 0.3423 | 0 | 0.34348 | 0.34354 | 0.34366
3135 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020310 | F19-APPEARL-PARK | INDUSTRIAL | DLMS Meter | 0 | 15.849 | 0 | 0 | 0 | #DIV/0!
3136 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010110 | F20-JODHANI PAPERS | INDUSTRIAL | DLMS Meter | 3.97 | 4.0091 | 0 | 3.97 | -0.98464 | -0.98464
3137 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020311 | F21-INDOUSMIM-TECH | INDUSTRIAL | DLMS Meter | 1.3958 | 1.2848 | 0.030792 | 1.365 | 5.8736 | 7.077
3138 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010111 | F22-KARENAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.5067 | 1.1726 | 0.1766 | 1.3301 | 11.8449 | 11.8449
3139 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010114 | F23-RITTAL | INDUSTRIAL | DLMS Meter | 1.3536 | 1.3671 | 0 | 1.3536 | -0.99885 | -0.99885
3140 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010115 | F24-EKASHIPURA NJY | NJY | DLMS Meter | 0.69616 | 0.60604 | 0 | 0.69616 | 12.9446 | 53.0169
3141 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907010116 | F25-DODDATUMKUR NJY | NJY | DLMS Meter | 0.56404 | 0.45918 | 0.063 | 0.50104 | 8.3555 | 26.5344
3142 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KIADB_VNP_220 | 1320103905020101 | F07-CHAMUNDI | INDUSTRIAL | DLMS Meter | 3.6884 | 3.5841 | 0 | 3.6884 | 2.8267 | 2.9686
3143 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KIADB_VNP_220 | 1320103905020102 | F08-SHARADHA | INDUSTRIAL | DLMS Meter | 6.2708 | 6.0363 | 0 | 6.2708 | 3.7399 | 4.3632
3144 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KIADB_VNP_220 | 1320103905020104 | F11-VIGNESHWARA | INDUSTRIAL | DLMS Meter | 3.108 | 1.2923 | 1.779 | 1.329 | 2.7627 | 4.9403
3145 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | KODIGEHALLI_66 | 1140303902010101 | F01-KACHOHALLI | INDUSTRIAL | DLMS Meter | 4.1034 | 3.5858 | 0.33 | 3.7734 | 4.9735 | 8.1672
3146 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | KODIGEHALLI_66 | 1140303902010102 | F02-KALPA | INDUSTRIAL | DLMS Meter | 4.7214 | 4.5629 | 0 | 4.7214 | 3.3561 | 3.3561
3147 | BMASZ | WEST | KENGERI | K4 | KODIGEHALLI_66 | 1140303902010103 | F03-BBMP | GOVERNMENT OFFICES | DLMS Meter | 1.4888 | 1.3578 | 0.03823 | 1.4506 | 6.396 | 9.6984
3148 | BMASZ | WEST | KENGERI | K4 | KODIGEHALLI_66 | 1140303902010104 | F04-KODIGEHALLI | DOMESTIC | DLMS Meter | 4.2078 | 2.768 | 1.2521 | 2.9557 | 6.3506 | 15.5203
3149 | BMASZ | WEST | KENGERI | K4 | KODIGEHALLI_66 | 1140303902020104 | F05-SEGEHALLI | INDUSTRIAL | DLMS Meter | 2.3385 | 2.1577 | 0 | 2.3385 | 7.7284 | 10.1142
3150 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | KODIGEHALLI_66 | 1140303902020101 | F06-JANAPRIYA | INDUSTRIAL | DLMS Meter | 5.7855 | 5.6225 | 0 | 5.7855 | 2.8176 | 10.6874
3151 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | KODIGEHALLI_66 | 1140303902020102 | F07- RASHI | INDUSTRIAL | DLMS Meter | 2.5547 | 2.4212 | 0 | 2.5547 | 5.2252 | 6.4108
3152 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | KODIGEHALLI_66 | 1140303902020103 | F08-KACHOHALLI INDUSTRIAL | INDUSTRIAL | DLMS Meter | 4.2157 | 3.7488 | 0.26 | 3.9557 | 5.231 | 6.144
3153 | BMASZ | WEST | KENGERI | K4 | KODIGEHALLI_66 | 1140303902020106 | F09-PADMAVATHI INDUSTRIAL AREA | INDUSTRIAL | DLMS Meter | 1.0324 | 0.9097 | 0.059621 | 0.97276 | 6.4834 | 6.4834
3154 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | KODIGEHALLI_66 | 1140303902010105 | F10-MACHOHALLI INDUSTRIAL | INDUSTRIAL | DLMS Meter | 4.3855 | 3.7283 | 0.55 | 3.8355 | 2.7932 | 3.4187
3155 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | KODIGEHALLI_66 | 1140303902010106 | F11-FOREST GATE INDUSTRIAL | INDUSTRIAL | DLMS Meter | 1.8728 | 1.6161 | 0.145 | 1.7278 | 6.4621 | 7.784
3156 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020301 | F01-KALIDEVAPURA | AGRI | DLMS Meter | 0.50456 | 0.45401 | 0 | 0.50456 | 10.018 | 10.018
3157 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020302 | F02-CHIKKAMALUR | AGRI | DLMS Meter | 0.8131 | 0.73168 | 0 | 0.8131 | 10.0132 | 10.0132
3158 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020101 | F03-KODIGENAHALLI | URBAN MIXED LOAD | DLMS Meter | 0.66712 | 0.6037 | 0 | 0.66712 | 9.5067 | 31.6051
3159 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020102 | F04-VITALAPURA | AGRI | DLMS Meter | 0.27356 | 0.24617 | 0 | 0.27356 | 10.0117 | 10.0117
3160 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020303 | F05-DASARAHALLI | AGRI | DLMS Meter | 1.1737 | 1.0561 | 0 | 1.1737 | 10.0155 | 10.0155
3161 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020304 | F06-MYDHANAHALLI | AGRI | DLMS Meter | 0.79968 | 0.71958 | 0 | 0.79968 | 10.0161 | 10.0161
3162 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020103 | F07-SINGANAHALLI | AGRI | DLMS Meter | 0.9086 | 0.81758 | 0 | 0.9086 | 10.0177 | 10.0177
3163 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020104 | F08-KODALAPURA | AGRI | DLMS Meter | 0.7904 | 0.71128 | 0 | 0.7904 | 10.0105 | 10.0359
3164 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020105 | F09-KADAGATHUR | AGRI | DLMS Meter | 0.41826 | 0.37621 | 0 | 0.41826 | 10.0543 | 10.0543
3165 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020106 | F10-THERIYUR | AGRI | DLMS Meter | 0.62528 | 0.56287 | 0 | 0.62528 | 9.9813 | 9.9813
3166 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020107 | F11-THINGALUR-NJY | NJY | DLMS Meter | 0.47062 | 0.42033 | 0 | 0.47062 | 10.685 | 51.0008
3167 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020305 | F13-ARLAPURA | NJY | DLMS Meter | 0.33234 | 0.29986 | 0 | 0.33234 | 9.774 | 46.5959
3168 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020109 | F14-VARADANAHALLI | NJY | DLMS Meter | 0.66194 | 0.58765 | 0 | 0.66194 | 11.2238 | 55.0165
3169 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901010102 | F15-LOTUS FEEDER | INDUSTRIAL | DLMS Meter | 0.26408 | 0.26013 | 0 | 0.26408 | 1.4958 | 1.4958
3170 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901010103 | F16-DODDADALAVATTA | NJY | DLMS Meter | 0.7791 | 0.69184 | 0 | 0.7791 | 11.2002 | 57.2616
3171 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901020306 | F17-KASINAYAKANAHALLI NJY | NJY | DLMS Meter | 0.7088 | 0.63999 | 0 | 0.7088 | 9.7073 | 58.7388
3172 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | KODIGENAHALLI_66 | 1320304901010101 | F18-BACHENAHALLI | AGRI | DLMS Meter | 0.259 | 0.23423 | 0 | 0.259 | 9.5637 | 9.5637
3173 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | KODIHALLI_66 | 1220302902020101 | F01-SANTHEKODIHALLI | NJY | DLMS Meter | 0.55506 | 0.46248 | 0.045256 | 0.5098 | 9.2829 | 29.5253
3174 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | KODIHALLI_66 | 1220302902020102 | F02-HUNASANAHALLI | AGRI | DLMS Meter | 0.88065 | 0.7926 | 0 | 0.88065 | 9.9985 | 9.9985
3175 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | KODIHALLI_66 | 1220302902020103 | F03-D.K.PLOT | AGRI | DLMS Meter | 1.0453 | 0.6518 | 0.32108 | 0.7242 | 9.9967 | 9.9967
3176 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | KODIHALLI_66 | 1220302902020301 | F04-HERANDAPPANAHALLI | AGRI | DLMS Meter | 0.93356 | 0.73352 | 0.11695 | 0.81661 | 10.175 | 10.175
3177 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | KODIHALLI_66 | 1220302902020302 | F05-YAKKULI NJY | NJY | DLMS Meter | 0.28815 | 0.25433 | 0.002944 | 0.2852 | 10.8249 | 39.8146
3178 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | KODIHALLI_66 | 1220302902020303 | F06-MUGGUR(ALNATHA) | AGRI | DLMS Meter | 1.032 | 0.92673 | 0 | 1.032 | 10.1974 | 10.1974
3179 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | KODIHALLI_66 | 1220302902020304 | F07-TAVAREKATTE-NJY-(HHBJ-NJY-) | NJY | DLMS Meter | 0.54916 | 0.47836 | 0.023223 | 0.52594 | 9.0463 | 41.6333
3180 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | KODIHALLI_66 | 1220302902020305 | F08-ERALPODLU-NJY(MUGGUR-NJY) | NJY | DLMS Meter | 0.3386 | 0.29293 | 0.01686 | 0.32174 | 8.9551 | 45.4413
3181 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | KODIHALLI_66 | 1220302902010105 | F09-ARAKERE NJY | NJY | DLMS Meter | 0.39956 | 0.33871 | 0.027969 | 0.37159 | 8.8484 | 50.9108
3182 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR RURAL | KODIHALLI_66 | 1220302902010106 | F10-HALASURU | AGRI | DLMS Meter | 0.6565 | 0.59091 | 0 | 0.6565 | 9.9906 | 9.9906
3183 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | KODIHALLI_BGR_66 | 1230401902010101 | F01-KURUBUR | AGRI | DLMS Meter | 0.99026 | 0.89137 | 0 | 0.99026 | 9.9863 | 9.9863
3184 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | KODIHALLI_BGR_66 | 1230401902010102 | F02-DODDAPURA-NJY | NJY | DLMS Meter | 0.69462 | 0.60912 | 0 | 0.69462 | 12.3091 | 71.5806
3185 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | KODIHALLI_BGR_66 | 1230401902010104 | F03-GAJALAHALLI | AGRI | DLMS Meter | 0.84762 | 0.76269 | 0 | 0.84762 | 10.0193 | 10.0193
3186 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | KODIHALLI_BGR_66 | 1230401902010105 | F04-PANASACHOWDANAHALLI | NJY | DLMS Meter | 1.0726 | 0.96825 | 0 | 1.0726 | 9.7317 | 68.3865
3187 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | KODIHALLI_BGR_66 | 1230401902020304 | F05-D.B.HALLI | AGRI | DLMS Meter | 0.868 | 0.78093 | 0 | 0.868 | 10.0309 | 10.0309
3188 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | KODIHALLI_BGR_66 | 1230401902020301 | F06-ANOOR | AGRI | DLMS Meter | 1.0335 | 0.93018 | 0 | 1.0335 | 9.9971 | 9.9971
3189 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | KODIHALLI_BGR_66 | 1230401902020302 | F07-K-HOSUR | AGRI | DLMS Meter | 0.64834 | 0.5836 | 0 | 0.64834 | 9.9855 | 9.9855
3190 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | KODIHALLI_BGR_66 | 1230401902020303 | F08-G-KODIHALLI | AGRI | DLMS Meter | 0.80926 | 0.72866 | 0 | 0.80926 | 9.9597 | 9.9597
3191 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | KODIHALLI_BGR_66 | 1230401902010106 | F09-KODADAVADI | NJY | DLMS Meter | 0.58228 | 0.41666 | 0.1207 | 0.46158 | 9.7321 | 69.0828
3192 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904010101 | F01-KOLALA TOWN | URBAN MIXED LOAD | DLMS Meter | 0.30808 | 0.19348 | 0.104 | 0.20408 | 5.1935 | 11.0762
3193 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904010102 | F02-MAVATUR | AGRI | DLMS Meter | 1.3107 | 1.1675 | 0 | 1.3107 | 10.9262 | 10.9262
3194 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904010103 | F03-BYRAGUNDLU | AGRI | DLMS Meter | 1.5376 | 1.3565 | 0 | 1.5376 | 11.7726 | 13.2332
3195 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904010104 | F04-CHIKKADODDAVADI | AGRI | DLMS Meter | 1.4083 | 1.2592 | 0 | 1.4083 | 10.5923 | 10.5923
3196 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904020301 | F05-SAGGERE | AGRI | DLMS Meter | 2.396 | 2.1258 | 0 | 2.396 | 11.2755 | 12.3015
3197 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904020302 | F06-PATHAGANAHALLI | AGRI | DLMS Meter | 1.6108 | 1.4251 | 0 | 1.6108 | 11.5244 | 11.5842
3198 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904020303 | F07-URIDIGERE | AGRI | DLMS Meter | 1.545 | 1.3914 | 0 | 1.545 | 9.9442 | 9.9442
3199 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904020304 | F08-KATENAHALLI | AGRI | DLMS Meter | 1.58 | 1.4096 | 0 | 1.58 | 10.7847 | 10.7847
3200 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904010105 | F09-YELACHIGERE | NJY | DLMS Meter | 0.50003 | 0.2425 | 0.235 | 0.26503 | 8.499 | 57.7635
3201 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904020305 | F10-HANUMANTHAGIRI | NJY | DLMS Meter | 0.51045 | 0.17964 | 0.318 | 0.19245 | 6.6545 | 46.2744
3202 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904020306 | F11-VAJJANAKURIKE | NJY | DLMS Meter | 0.76358 | 0.19454 | 0.55 | 0.21358 | 8.9124 | 48.9517
3203 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904020307 | F12-DODDASAGERE | NJY | DLMS Meter | 1.0621 | 0.39831 | 0.622 | 0.44013 | 9.5024 | 61.5441
3204 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KOLALA_66 | 1320305904010106 | F13-CHINNAHALLI | NJY | DLMS Meter | 0.5889 | 0.093606 | 0.485 | 0.1039 | 9.9076 | 53.6482
3205 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010101 | F01-WATERWORKS | URBAN MIXED LOAD | DLMS Meter | 1.8536 | 1.6464 | 0 | 1.8536 | 11.1809 | 16.7019
3206 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010102 | F02-KOLAR-TOWN | URBAN MIXED LOAD | DLMS Meter | 2.5525 | 2.1365 | 0.14 | 2.4125 | 11.4436 | 34.4568
3207 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010103 | F03-DODDAHASALA | AGRI | DLMS Meter | 5.1214 | 1.1189 | 3.8835 | 1.2379 | 9.6144 | 37.5881
3208 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010104 | F04-S.N.R-HOSPITAL | HOSPITAL | DLMS Meter | 0.23162 | 0.22234 | 0 | 0.23162 | 4.0048 | 52.6927
3209 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902020301 | F05-HOGRI | AGRI | DLMS Meter | 0.123 | 0.10981 | 0 | 0.123 | 10.7244 | 48.1631
3210 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902020302 | F06-DC-OFFICE | URBAN MIXED LOAD | DLMS Meter | 5.1216 | 3.3985 | 1.4191 | 3.7025 | 8.2123 | 47.1168
3211 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902020303 | F07-KOLAR-TOWN | URBAN MIXED LOAD | DLMS Meter | 3.9188 | 3.4873 | 0 | 3.9188 | 11.0129 | 33.1864
3212 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902020304 | F08-BEGLI-HOSAHALLI | AGRI | DLMS Meter | 1.0406 | 0.93644 | 0 | 1.0406 | 10.0082 | 10.8047
3213 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902020305 | F09-ARAHALLI | AGRI | DLMS Meter | 1.3981 | 1.0333 | 0.25 | 1.1481 | 9.9984 | 12.8394
3214 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010105 | F10-NARASAPURA | AGRI | DLMS Meter | 1.1837 | 0.32468 | 0.823 | 0.36074 | 9.9967 | 9.9967
3215 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010106 | F11-KOOTERI | AGRI | DLMS Meter | 0.95884 | 0.63876 | 0.249 | 0.70984 | 10.013 | 11.8357
3216 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010110 | F16-CHOKKAHALLI_NJY | NJY | DLMS Meter | 0.6789 | 0.61589 | 0 | 0.6789 | 9.2814 | 43.7979
3217 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010301 | F17-BEGLI_DIMBA_NJY | NJY | DLMS Meter | 1.0595 | 0.62322 | 0.367 | 0.69248 | 10.0016 | 60.1451
3218 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010111 | F18-NJY-DIMBA | NJY | DLMS Meter | 0.0505 | 0.046101 | 0 | 0.0505 | 8.7109 | 76.6722
3219 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010112 | F19-NJY-MADERAHALLI | NJY | DLMS Meter | 0.2618 | 0.23739 | 0 | 0.2618 | 9.325 | 31.7648
3220 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010113 | F20-VISVESWARAYA STADIUM | URBAN MIXED LOAD | DLMS Meter | 3.0668 | 2.6829 | 0.06 | 3.0068 | 10.7735 | 36.5092
3221 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902020307 | F22-GOWRIPET | URBAN MIXED LOAD | DLMS Meter | 4.2839 | 4.1374 | 0 | 4.2839 | 3.4199 | 38.0244
3222 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901010110 | F03-BRIGADE GOLDEN TRAINGALE | DOMESTIC | DLMS Meter | 2.3586 | 2.3096 | 0 | 2.3586 | 2.0779 | 2.3873
3223 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901010103 | F04-BRIGADE EXOTIKA | DOMESTIC | DLMS Meter | 0.58531 | 0.56672 | 0 | 0.58531 | 3.1768 | 4.5433
3224 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901010104 | F05-NET MAGIC | COMMERCIAL | DLMS Meter | 12.2833 | 12.2716 | 0 | 12.2833 | 0.095414 | 0.095414
3225 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901010105 | F06-KANNAMANGALA | DOMESTIC | DLMS Meter | 4.4452 | 3.8929 | 0.112 | 4.3332 | 10.1618 | 17.2966
3226 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901010106 | F07-CHEEMASANDRA | DOMESTIC | DLMS Meter | 6.8959 | 6.281 | 0 | 6.8959 | 8.9162 | 14.1262
3227 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901020301 | F08-ABC | INDUSTRIAL | DLMS Meter | 5.2267 | 2.443 | 2.4915 | 2.7352 | 10.6832 | 14.3477
3228 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901010301 | F09-SAFAL-MARKET | INDUSTRIAL | DLMS Meter | 1.4126 | 1.4091 | 0 | 1.4126 | 0.2465 | 0.24827
3229 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901010107 | F10-BGRT | COMMERCIAL | DLMS Meter | 1.8673 | 1.8632 | 0 | 1.8673 | 0.21957 | 0.21957
3230 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901010302 | F11-BHIDARAHALLI | DOMESTIC | DLMS Meter | 5.6275 | 4.4969 | 0.98393 | 4.6436 | 3.1587 | 8.9169
3231 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901010303 | F13-STRELING | DOMESTIC | DLMS Meter | 2.729 | 2.5191 | 0 | 2.729 | 7.6908 | 10.3872
3232 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901010101 | F14-SCHNIDER | COMMERCIAL | DLMS Meter | 0.000911 | 0.0009 | 0 | 0.000911 | 1.2075 | 1.2075
3233 | BRAZ | BANGALORE RURAL | HOSAKOTE | AVALAHALLI | KONADASPURA_66 | 1210201901020303 | F15-CIPLA | INDUSTRIAL | DLMS Meter | 2.7296 | 2.7259 | 0 | 2.7296 | 0.13588 | 0.13588
3234 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | KONASAGARA_66 | 1310403905010101 | F02-NETHRANAHALLY | AGRI | DLMS Meter | 0.1318 | 0.11862 | 0 | 0.1318 | 9.9985 | 9.9985
3235 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | KONASAGARA_66 | 1310403905010102 | F04-KONASAGARA | NJY | DLMS Meter | 0.1956 | 0.17085 | 0 | 0.1956 | 12.6539 | 51.7563
3236 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | KONASAGARA_66 | 1310403905010103 | F05-CHOWDIPURA | AGRI | DLMS Meter | 0.1224 | 0.10666 | 0 | 0.1224 | 12.8595 | 12.8595
3237 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | KONASAGARA_66 | 1310403905010104 | F06-UDEV | AGRI | DLMS Meter | 0.0932 | 0.083879 | 0 | 0.0932 | 10.0011 | 10.0011
3238 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902010101 | F02-P-GOLLAHALLI | AGRI | DLMS Meter | 0.3953 | 0.35593 | 0 | 0.3953 | 9.9595 | 13.6832
3239 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902010102 | F03-KURIKEMPANHALLI | AGRI | DLMS Meter | 1.053 | 0.91767 | 0 | 1.053 | 12.8537 | 12.8537
3240 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902010105 | F04-BURUDAGATTA | AGRI | DLMS Meter | 0.063224 | 0.056908 | 0 | 0.063224 | 9.9902 | 9.9902
3241 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902020301 | F05-BRAMHASANDRANJY | NJY | DLMS Meter | 0.969 | 0.85837 | 0 | 0.969 | 11.417 | 23.4502
3242 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902020302 | F06-BOMMANAHALLI | AGRI | DLMS Meter | 0.93674 | 0.83876 | 0 | 0.93674 | 10.4597 | 10.4597
3243 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902020303 | F07-KORA | AGRI | DLMS Meter | 1.021 | 0.89838 | 0 | 1.021 | 12.0113 | 13.601
3244 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902020304 | F08-KATTIGENAHALLI | AGRI | DLMS Meter | 1.1387 | 1.001 | 0 | 1.1387 | 12.0909 | 12.0909
3245 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902010104 | F09-NELAHAL | NJY | DLMS Meter | 0.57565 | 0.50862 | 0 | 0.57565 | 11.6445 | 35.4242
3246 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902030501 | F11-LAKSMHI-STEEL | INDUSTRIAL | DLMS Meter | 7.624 | 7.4487 | 0.145 | 7.479 | 0.4046 | 0.4046
3247 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902030504 | F12-IDLE | IDLE | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3248 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902030507 | F16-MUDDENAHALLI | AGRI | DLMS Meter | 1.4976 | 1.3106 | 0 | 1.4976 | 12.4862 | 12.4862
3249 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902030503 | F17-LINGANAHALLI | AGRI | DLMS Meter | 1.359 | 1.1729 | 0 | 1.359 | 13.6902 | 13.6902
3250 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | 1110202901020101 | F01-NETHRAVATHI | URBAN MIXED LOAD | DLMS Meter | 3.1993 | 2.9991 | 0 | 3.1993 | 6.2587 | 6.5849
3251 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | 1110202901020102 | F03-JYOTHINIVASA-COLLEGE | URBAN MIXED LOAD | DLMS Meter | 5.0857 | 4.7431 | 0.0618 | 5.0239 | 5.5905 | 7.6588
3252 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | 1110202901020103 | F04-GODHAVARI-STNAUX | URBAN MIXED LOAD | DLMS Meter | 0.95523 | 0.88592 | 0.025 | 0.93023 | 4.7636 | 6.2865
3253 | BMASZ | SOUTH | JAYANAGAR | S2 | KORAMANGALA_220 | 1110202901020104 | F05-KIRLOSKAR. | URBAN MIXED LOAD | DLMS Meter | 4.2251 | 4.0025 | 0.056148 | 4.1689 | 3.9927 | 5.4071
3254 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | 1110202901020105 | F06-ST-BED | URBAN MIXED LOAD | DLMS Meter | 2.7746 | 2.2684 | 0.361 | 2.4136 | 6.0172 | 7.2318
3255 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | 1110202901020301 | F07-KAPILA | URBAN MIXED LOAD | DLMS Meter | 0.78787 | 0.73723 | 0 | 0.78787 | 6.4282 | 7.9596
3256 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | 1110202901020302 | F08-JUDGESBLOCK&-THUNGABHADRA | URBAN MIXED LOAD | DLMS Meter | 0.74896 | 0.68469 | 0.018 | 0.73096 | 6.3305 | 8.5461
3257 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | 1110202901020303 | F09-PRANIDAYA-SANGHA | URBAN MIXED LOAD | DLMS Meter | 3.5448 | 2.9198 | 0.383 | 3.1618 | 7.6524 | 11.4359
3258 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | 1110202901020304 | F10-KALYANAMANTAPA | URBAN MIXED LOAD | DLMS Meter | 3.5015 | 3.2093 | 0.068 | 3.4335 | 6.5288 | 12.0601
3259 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | 1110202901020305 | F11-KORMANGALA-VILLAGE | URBAN MIXED LOAD | DLMS Meter | 5.9332 | 3.5997 | 1.732 | 4.2012 | 14.3184 | 16.9841
3260 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | 1110202901020306 | F12-RAHEJA-COMPLEX | URBAN MIXED LOAD | DLMS Meter | 5.0448 | 4.646 | 0 | 5.0448 | 7.9055 | 9.5662
3261 | BMASZ | SOUTH | JAYANAGAR | S2 | KORAMANGALA_220 | 1110202901020106 | F13-FORUM-MALL | HOSPITAL | DLMS Meter | 2.2003 | 2.1333 | 0 | 2.2003 | 3.0469 | 3.5683
3262 | BMASZ | SOUTH | KORAMANGALA | S4 | KORAMANGALA_220 | #N/A | F14- BWSSB | #N/A | DLMS Meter | 1.1172 | 1.1144 | 0 | 1.1172 | 0.25307 | 0.25307
3263 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903010101 | F01-CHIKKAPALANAHALLI | AGRI | DLMS Meter | 1.6521 | 1.3561 | 0.145 | 1.5071 | 10.0141 | 10.0141
3264 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020301 | F02-AGRAHARA | AGRI | DLMS Meter | 1.548 | 1.3932 | 0 | 1.548 | 10.0015 | 10.0015
3265 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903010102 | F03-YELERAMPURA | AGRI | DLMS Meter | 1.5864 | 1.4278 | 0 | 1.5864 | 9.9991 | 9.9991
3266 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020302 | F04-TEETHA | AGRI | DLMS Meter | 2.0088 | 1.8046 | 0 | 2.0088 | 10.166 | 12.5179
3267 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020303 | F05-KORATAGERE-TOWN | URBAN MIXED LOAD | DLMS Meter | 1.72 | 1.5929 | 0.068 | 1.652 | 3.5741 | 3.5741
3268 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020304 | F06-THUMBADI | AGRI | DLMS Meter | 2.449 | 2.2042 | 0 | 2.449 | 9.9942 | 10.1103
3269 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903010103 | F07-BUKKAPATNA | AGRI | DLMS Meter | 1.8305 | 1.6443 | 0 | 1.8305 | 10.1771 | 10.7366
3270 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903010104 | F08-SIDDARABETTA | AGRI | DLMS Meter | 2.196 | 1.9615 | 0 | 2.196 | 10.6787 | 14.8833
3271 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903010105 | F09-GORAVANAHALLI | AGRI | DLMS Meter | 1.5355 | 1.3664 | 0 | 1.5355 | 11.0125 | 11.0125
3272 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020305 | F10-KANVA | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3273 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903010501 | F11-LAKSHMI-TEMPLE | NJY | DLMS Meter | 0.559 | 0.44334 | 0.07 | 0.489 | 9.3383 | 41.3966
3274 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903010502 | F12-HEMAVATHI | NJY | DLMS Meter | 0.6434 | 0.58664 | 0 | 0.6434 | 8.8224 | 35.2078
3275 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903010503 | F13-IRAKASANDRA | NJY | DLMS Meter | 0.91298 | 0.7356 | 0.108 | 0.80498 | 8.6188 | 47.8122
3276 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020501 | F14-MALLEKAVU | NJY | DLMS Meter | 0.9179 | 0.24136 | 0.65 | 0.2679 | 9.9073 | 55.8549
3277 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020502 | F15-DODDAMMADEVI | NJY | DLMS Meter | 0.4188 | 0.19106 | 0.205 | 0.2138 | 10.6356 | 44.2266
3278 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903010504 | F16-VEERANAGAMMA | NJY | DLMS Meter | 0.9947 | 0.58405 | 0.36 | 0.6347 | 7.9803 | 46.8852
3279 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020503 | F17-EKALAVYA | NJY | DLMS Meter | 1.0549 | 0.29047 | 0.734 | 0.3209 | 9.4811 | 54.1061
3280 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020701 | F18-URDAGERE CROSS | URBAN MIXED LOAD | DLMS Meter | 0.5344 | 0.45957 | 0.05 | 0.4844 | 5.1251 | 5.1251
3281 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020703 | F19-ALALASANDRA | AGRI | DLMS Meter | 1.1908 | 1.0716 | 0 | 1.1908 | 10.0091 | 10.0091
3282 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | KORATAGERE_66 | 1320305903020702 | F20-BODABANDENAHALLI | AGRI | DLMS Meter | 1.159 | 1.0426 | 0 | 1.159 | 10.0412 | 16.378
3283 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | KOTIPURA_220 | 1220102902010101 | F01-YARABNAGAR | URBAN MIXED LOAD | DLMS Meter | 4.1092 | 0.61336 | 3.4352 | 0.67404 | 9.0021 | 16.5478
3284 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | KOTIPURA_220 | 1220102902010102 | F04-S-P-W | INDUSTRIAL | DLMS Meter | 2.1338 | 2.1505 | 0 | 2.1338 | -0.78605 | -0.66509
3285 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902020306 | F01-KANNURU | NJY | DLMS Meter | 1.0174 | 0.4808 | 0.4825 | 0.5349 | 10.1143 | 54.391
3286 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902011501 | F02-BISKUR | NJY | DLMS Meter | 0.557 | 0.26894 | 0.2595 | 0.2975 | 9.5997 | 48.0203
3287 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902020302 | F03-KAGIMADU | AGRI | DLMS Meter | 0.8866 | 0.79797 | 0 | 0.8866 | 9.997 | 9.997
3288 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902020303 | F04-SRIGIRIPURA | AGRI | DLMS Meter | 0.9132 | 0.76029 | 0.05 | 0.8632 | 11.922 | 11.922
3289 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902010107 | F05-VEERASAGARA | NJY | DLMS Meter | 0.4394 | 0.2542 | 0.158 | 0.2814 | 9.6677 | 39.3485
3290 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902010103 | F07-MARURU | AGRI | DLMS Meter | 0.9718 | 0.85122 | 0 | 0.9718 | 12.4081 | 12.4081
3291 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | #N/A | F08-KUDUR | #N/A | DLMS Meter | 2.1301 | 1.8909 | 0 | 2.1301 | 11.2328 | 19.2808
3292 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902010102 | F09-HULLICAL | AGRI | DLMS Meter | 1.0146 | 0.88567 | 0 | 1.0146 | 12.7074 | 12.7074
3293 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902010104 | F10-TIPPASANDRA | AGRI | DLMS Meter | 0.7586 | 0.5303 | 0.16 | 0.5986 | 11.4096 | 11.4096
3294 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902020305 | F11-NARASANDRA | AGRI | DLMS Meter | 1.5472 | 1.3607 | 0 | 1.5472 | 12.0522 | 12.0522
3295 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902020307 | F12-ARSINAKUNTE | NJY | DLMS Meter | 0.4256 | 0.30239 | 0.09 | 0.3356 | 9.8966 | 38.1235
3296 | BRAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | 1210103902011502 | F14- HOOJENAHALLI | NJY | DLMS Meter | 0.5467 | 0.35114 | 0.157 | 0.3897 | 9.8938 | 36.3838
3297 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903010101 | F01-KOLKUNTE | AGRI | DLMS Meter | 0.53538 | 0.48175 | 0 | 0.53538 | 10.017 | 10.017
3298 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903010102 | F02-GIRIYAPURA | AGRI | DLMS Meter | 0.69256 | 0.62352 | 0 | 0.69256 | 9.9692 | 9.9692
3299 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903010103 | F03-KAIDALA | AGRI | DLMS Meter | 0.89118 | 0.80235 | 0 | 0.89118 | 9.9677 | 9.9677
3300 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903010104 | F04-HADADIKKD | AGRI | DLMS Meter | 0.78934 | 0.71072 | 0 | 0.78934 | 9.9601 | 9.9601
3301 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903020301 | F05-NJKALBANDE | NJY | DLMS Meter | 0.5388 | 0.44744 | 0.024 | 0.5148 | 13.0853 | 53.852
3302 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903020302 | F06-KUKKAWADA | AGRI | DLMS Meter | 0.61724 | 0.41301 | 0.158 | 0.45924 | 10.0677 | 10.0677
3303 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903020303 | F08-LOKIKERE | AGRI | DLMS Meter | 0.84104 | 0.75729 | 0 | 0.84104 | 9.958 | 9.958
3304 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903030501 | F09-KANAGONDANAHALLI | AGRI | DLMS Meter | 0.86286 | 0.7765 | 0 | 0.86286 | 10.0092 | 10.0092
3305 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903030502 | F11-NAGARASANAHALLI | AGRI | DLMS Meter | 0.69772 | 0.62769 | 0 | 0.69772 | 10.0374 | 10.0374
3306 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903030503 | F12-HOOVINAMADU NJY | NJY | DLMS Meter | 0.62285 | 0.47164 | 0.083 | 0.53985 | 12.6359 | 48.0233
3307 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903020304 | F14-BALLUR NJY | NJY | DLMS Meter | 0.55614 | 0.4826 | 0.0169 | 0.53924 | 10.5043 | 47.1074
3308 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903020306 | F15-NJ KALKERE | NJY | DLMS Meter | 0.5661 | 0.4518 | 0.0466 | 0.5195 | 13.0327 | 51.3072
3309 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902010101 | F02-KENGERI-TOWN | URBAN MIXED LOAD | DLMS Meter | 4.6022 | 3.8474 | 0.61453 | 3.9877 | 3.5179 | 9.3182
3310 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902010102 | F03-WONDER | URBAN MIXED LOAD | DLMS Meter | 5.5058 | 5.2771 | 0 | 5.5058 | 4.1542 | 11.5234
3311 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902020301 | F04-RAMOHALLI | URBAN MIXED LOAD | DLMS Meter | 3.5154 | 1.9958 | 1.3706 | 2.1448 | 6.9476 | 18.9963
3312 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902020302 | F05-GONIPURA | URBAN MIXED LOAD | DLMS Meter | 2.415 | 1.3021 | 1.0674 | 1.3476 | 3.375 | 33.424
3313 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902010103 | F06-BYROHALLI | INDUSTRIAL | DLMS Meter | 3.5045 | 3.3673 | 0 | 3.5045 | 3.9164 | 5.3963
3314 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902020303 | F07-FDEVIKIRAN | INDUSTRIAL | DLMS Meter | 3.1663 | 2.9006 | 0.15124 | 3.015 | 3.7964 | 8.6242
3315 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902020304 | F08-DECCAN-HERALD | INDUSTRIAL | DLMS Meter | 0.43994 | 0.4252 | 0.006207 | 0.43373 | 1.967 | 1.967
3316 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902020305 | F09-BGS-INTERNATIONAL | URBAN MIXED LOAD | DLMS Meter | 3.1134 | 2.7395 | 0.25562 | 2.8577 | 4.1381 | 8.8796
3317 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902010104 | F10-KAMBIPURA-/-KENGERI | URBAN MIXED LOAD | DLMS Meter | 6.364 | 5.7208 | 0.46524 | 5.8988 | 3.0166 | 7.2784
3318 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902010105 | F11-KIADB-ST-PHASE | INDUSTRIAL | DLMS Meter | 5.8361 | 5.6898 | 0.010124 | 5.826 | 2.3372 | 11.2521
3319 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902020306 | F12-KIADB-ND-PHASE | INDUSTRIAL | DLMS Meter | 5.0672 | 4.5699 | 0.30361 | 4.7635 | 4.0662 | 5.0073
3320 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902010106 | F13-GERUPALYA | INDUSTRIAL | DLMS Meter | 5.1636 | 4.9028 | 0.075133 | 5.0885 | 3.6496 | 5.2743
3321 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902020307 | F14-ISRO | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3322 | BMASZ | WEST | KENGERI | K1 | KUMBALOGODU_66 | 1140301902010108 | F15-BRIGADE PANORAMA | DOMESTIC | DLMS Meter | 1.8136 | 0.90211 | 0.78374 | 1.0298 | 12.4023 | 12.4023
3323 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | KUMBARANAHALLI_66 | 3210203902020101 | F01-SAI TEMPLE | NJY | DLMS Meter | 3.641 | 3.2438 | 0 | 3.641 | 10.9089 | 13.8959
3324 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | KUMBARANAHALLI_66 | 3210203902020102 | F02-SABALA | INDUSTRIAL | DLMS Meter | 6.3455 | 5.898 | 0 | 6.3455 | 7.053 | 7.9434
3325 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | KUMBARANAHALLI_66 | 3210203902020103 | F03-SOPPAHALLI IP | AGRI | DLMS Meter | 0.1414 | 0.12736 | 0 | 0.1414 | 9.9327 | 11.375
3326 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | KUMBARANAHALLI_66 | 3210203902020104 | F04-SHAKTHI PRECESSION | INDUSTRIAL | DLMS Meter | 2.972 | 1.3209 | 1.51 | 1.462 | 9.6502 | 17.8074
3327 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | KUMBARANAHALLI_66 | 3210203902020105 | F05-RAJAPURA | DOMESTIC | DLMS Meter | 0.4044 | 0.045212 | 0.356 | 0.0484 | 6.5868 | 6.5868
3328 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | KUMBARANAHALLI_66 | 3210203902010103 | F06-KUMBARANAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.7876 | 3.521 | 0 | 3.7876 | 7.0381 | 7.4918
3329 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | KUMBARANAHALLI_66 | 3210203902010101 | F07-ANUGRAHA LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.2566 | 2.15 | 0 | 2.2566 | 4.7218 | 5.6914
3330 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | KUMBARANAHALLI_66 | 3210203902010102 | F08-LINGAPURA | URBAN MIXED LOAD | DLMS Meter | 0.774 | 0.36527 | 0.38276 | 0.39124 | 6.6391 | 13.1047
3331 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902010101 | F02-BEERASANDRA | AGRI | DLMS Meter | 1.0294 | 0.64985 | 0.30653 | 0.72285 | 10.0985 | 10.3114
3332 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902010102 | F03-KUNDANNA | AGRI | DLMS Meter | 0.65238 | 0.58715 | 0 | 0.65238 | 9.9983 | 10.9608
3333 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902010103 | F04-DODDACHIMANAHALLI | NJY | DLMS Meter | 2.6652 | 2.0624 | 0.38353 | 2.2816 | 9.6087 | 33.2488
3334 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902010104 | F05-RAMANATHAPURA | AGRI | DLMS Meter | 1.154 | 1.0385 | 0 | 1.154 | 10.0087 | 10.3999
3335 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902010105 | F06-CHAPPARADAKALLU NJY | NJY | DLMS Meter | 2.0885 | 1.9612 | 0 | 2.0885 | 6.0997 | 43.3473
3336 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902020301 | F07-IVC ROAD | URBAN MIXED LOAD | DLMS Meter | 2.7818 | 0.77158 | 1.9135 | 0.86829 | 11.1371 | 23.2678
3337 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902020302 | F08-SINGRAHALLI | AGRI | DLMS Meter | 0.20653 | 0.18125 | 0 | 0.20653 | 12.2382 | 12.2382
3338 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902020303 | F09-THINDLU | AGRI | DLMS Meter | 0.54815 | 0.49975 | 0 | 0.54815 | 8.8299 | 10.7804
3339 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902020101 | F10-UGANAVADI | URBAN MIXED LOAD | DLMS Meter | 5.3882 | 4.8378 | 0 | 5.3882 | 10.2151 | 10.2151
3340 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902020305 | F11-DC OFFICE | GOVERNMENT OFFICES | DLMS Meter | 0.05874 | 0.058545 | 0 | 0.05874 | 0.33197 | 0.33197
3341 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | KUNDANA_66 | 1210202902020304 | F12-PANDITHAPURA | NJY | DLMS Meter | 1.0054 | 0.9102 | 0 | 1.0054 | 9.4661 | 42.3554
3342 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907010104 | F01-HANUMANAHALLI IP | AGRI | DLMS Meter | 0.8877 | 0.79951 | 0 | 0.8877 | 9.9342 | 9.9342
3343 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907010103 | F02-THIMLAPURA NJY | NJY | DLMS Meter | 0.66018 | 0.49493 | 0.10154 | 0.55864 | 11.4035 | 34.3667
3344 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907010102 | F03-NERALAGUNDI IP | AGRI | DLMS Meter | 0.74394 | 0.67032 | 0 | 0.74394 | 9.8958 | 9.8958
3345 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907010101 | F04-SINGATAGERE IP | AGRI | DLMS Meter | 0.72204 | 0.62745 | 0 | 0.72204 | 13.1007 | 13.1007
3346 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907010105 | F05-ANJANEYA INDUSTRIAL | INDUSTRIAL | DLMS Meter | 0.63004 | 0.58361 | 0 | 0.63004 | 7.369 | 7.6735
3347 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907010106 | F06-KUNDUR IP | AGRI | DLMS Meter | 0.39259 | 0.35332 | 0 | 0.39259 | 10.0038 | 10.0038
3348 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907010107 | F07-KULAMBI NJY | NJY | DLMS Meter | 1.4222 | 1.1316 | 0.15821 | 1.264 | 10.4748 | 32.6285
3349 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907020304 | F08-BANNIKODU IP | AGRI | DLMS Meter | 0.2438 | 0.21962 | 0 | 0.2438 | 9.9163 | 9.9163
3350 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907020302 | F09-NELAHONNE IP | AGRI | DLMS Meter | 0.39393 | 0.35451 | 0 | 0.39393 | 10.0061 | 10.0061
3351 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907020301 | F10-MUKTHENAHALLI IP | AGRI | DLMS Meter | 0.82901 | 0.74636 | 0 | 0.82901 | 9.9698 | 9.9698
3352 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | KUNDUR_66 | 1310302907020303 | F11-YAKKANAHALLI IP | AGRI | DLMS Meter | 0.6616 | 0.59278 | 0 | 0.6616 | 10.4019 | 10.4019
3353 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902010101 | F01-BORALINGANAPALYA | AGRI | DLMS Meter | 1.0076 | 0.90673 | 0 | 1.0076 | 10.0147 | 10.0147
3354 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902010102 | F02-KENKERE | AGRI | DLMS Meter | 1.037 | 0.69935 | 0.255 | 0.782 | 10.5692 | 10.5692
3355 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902010103 | F03-KUNIGAL AGRAHARA | URBAN MIXED LOAD | DLMS Meter | 1.8814 | 1.4226 | 0.3265 | 1.5549 | 8.5102 | 26.0597
3356 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902010104 | F04-RAYAPPAMARGA | URBAN MIXED LOAD | DLMS Meter | 2.6088 | 2.5704 | 0 | 2.6088 | 1.472 | 15.5348
3357 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902010108 | F05-WATER SUPPLY TMC | WATER WORKS | DLMS Meter | 0.05288 | 0.048382 | 0 | 0.05288 | 8.5061 | 8.5061
3358 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902010105 | F06-KALASIPALYA | AGRI | DLMS Meter | 1.029 | 0.92606 | 0 | 1.029 | 10.0071 | 10.0071
3359 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902020301 | F07-JANAGERE | AGRI | DLMS Meter | 1.077 | 0.96945 | 0 | 1.077 | 9.983 | 9.983
3360 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902020302 | F08-BHAKTHARAHALLI | AGRI | DLMS Meter | 1.682 | 1.5159 | 0 | 1.682 | 9.8735 | 9.8735
3361 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902020303 | F09-HERURU | AGRI | DLMS Meter | 1.1133 | 1.0019 | 0 | 1.1133 | 10.0075 | 10.0075
3362 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902020304 | F10-MADDUR-ROAD | URBAN MIXED LOAD | DLMS Meter | 1.1661 | 1.0924 | 0 | 1.1661 | 6.3195 | 15.901
3363 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902020305 | F11-BIDANAGERE | URBAN MIXED LOAD | DLMS Meter | 0.82146 | 0.73172 | 0 | 0.82146 | 10.9249 | 32.1804
3364 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | KUNIGAL_66 | 1320110902010109 | F13-BILIDEVALAYA NJY | AGRI | DLMS Meter | 0.5764 | 0.38937 | 0.14756 | 0.42884 | 9.2033 | 29.3513
3365 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KUNUR_66 | 1220301905010103 | F01-THERINADODDI | AGRI | DLMS Meter | 1.15 | 0.96113 | 0.082 | 1.068 | 10.0064 | 10.0064
3366 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KUNUR_66 | 1220301905010101 | F03-HULIBALE-NJY | NJY | DLMS Meter | 0.7452 | 0.55564 | 0.145 | 0.6002 | 7.4247 | 57.6942
3367 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KUNUR_66 | 1220301905010102 | F04-KR DODDI | AGRI | DLMS Meter | 0.6458 | 0.3931 | 0.209 | 0.4368 | 10.0053 | 10.0053
3368 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | KURUBARAHALLI_66 | 1310301903010101 | F01-TUMBIGERI | AGRI | DLMS Meter | 0.5822 | 0.52408 | 0 | 0.5822 | 9.9827 | 9.9827
3369 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | KURUBARAHALLI_66 | 1310301903010102 | F02-VATAGANAHALLI | AGRI | DLMS Meter | 0.6754 | 0.49533 | 0.125 | 0.5504 | 10.0053 | 10.2678
3370 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | KURUBARAHALLI_66 | 1310301903010103 | F04-SHANTINAGARA | AGRI | DLMS Meter | 0.8974 | 0.80781 | 0 | 0.8974 | 9.9827 | 9.9827
3371 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | KURUBARAHALLI_66 | 1310301903020301 | F05-CHIKKABIDARI | AGRI | DLMS Meter | 0.7844 | 0.70591 | 0 | 0.7844 | 10.006 | 10.006
3372 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | KURUBARAHALLI_66 | 1310301903020302 | F06-NEW-SARATHI | AGRI | DLMS Meter | 0.7863 | 0.70766 | 0 | 0.7863 | 10.0014 | 10.0014
3373 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | KURUBARAHALLI_66 | 1310301903020303 | F07-KONDAJJI | AGRI | DLMS Meter | 1.2289 | 1.106 | 0 | 1.2289 | 9.9999 | 9.9999
3374 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | KURUBARAHALLI_66 | 1310301903020304 | F08-KENCHANAHALLI | AGRI | DLMS Meter | 1.0394 | 0.80039 | 0.15 | 0.8894 | 10.0079 | 10.0079
3375 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | KURUBARAHALLI_66 | 1310301903010104 | F09-KONDAJJI-WATER-WORKS | NJY | DLMS Meter | 0.561 | 0.46508 | 0.052 | 0.509 | 8.6287 | 29.7434
3376 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | KURUBARAHALLI_66 | 1310301903020305 | F10-KALPATARU NJY | NJY | DLMS Meter | 0.5196 | 0.3189 | 0.169 | 0.3506 | 9.0418 | 45.5976
3377 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | KURUBARAHALLI_66 | 1310301903010106 | F11-DUGGAVATHI | NJY | DLMS Meter | 0.3375 | 0.21747 | 0.099 | 0.2385 | 8.8164 | 44.9765
3378 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | KUTAGALLU_66 | 1220103901010101 | F01-KUTAGALLU | AGRI | DLMS Meter | 0.25095 | 0.22599 | 0 | 0.25095 | 9.945 | 9.945
3379 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | KUTAGALLU_66 | 1220103901010105 | F02-DANAYAKANAPURA NJY | NJY | DLMS Meter | 1.1342 | 1.0426 | 0.0072 | 1.127 | 7.4886 | 23.3234
3380 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | KUTAGALLU_66 | 1220103901010102 | F03-SHANUBHOGANAHALLI | AGRI | DLMS Meter | 0.67698 | 0.60922 | 0 | 0.67698 | 10.0093 | 10.0093
3381 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | KUTAGALLU_66 | 1220103901010103 | F04-YEREHALLI | AGRI | DLMS Meter | 0.55698 | 0.4921 | 0.01015 | 0.54683 | 10.0079 | 10.0079
3382 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | KUTAGALLU_66 | 1220103901010104 | F05-KUNAMUDANAHALLI NJY | NJY | DLMS Meter | 0.1386 | 0.10935 | 0.0185 | 0.1201 | 8.9484 | 41.806
3383 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | KUTAGALLU_66 | 1220103901010106 | F06-KOOTAGAL YEREHALLI NJY | NJY | DLMS Meter | 0.4544 | 0.36478 | 0.0534 | 0.401 | 9.0327 | 45.6872
3384 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904020101 | F01-INDUSTRIAL-AREA | INDUSTRIAL | DLMS Meter | 0.1054 | 0.10165 | 0 | 0.1054 | 3.56 | 4.1878
3385 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904010101 | F02-KAMANDAHALLI | AGRI | DLMS Meter | 0.9224 | 0.83013 | 0 | 0.9224 | 10.0028 | 10.0028
3386 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904010102 | F03-URITI-AGRAHARA | AGRI | DLMS Meter | 1.4488 | 1.3039 | 0 | 1.4488 | 10.0012 | 11.5495
3387 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904010103 | F04-MADDERI | AGRI | DLMS Meter | 1.3148 | 1.178 | 0 | 1.3148 | 10.4071 | 10.4071
3388 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904020305 | F05-MADIVALA | AGRI | DLMS Meter | 1.509 | 1.3404 | 0 | 1.509 | 11.1757 | 11.1757
3389 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904020301 | F06-CHALDIGANAHALLI | AGRI | DLMS Meter | 1.0178 | 0.91234 | 0 | 1.0178 | 10.3616 | 10.3616
3390 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904020302 | F07-THIPPENAHALLI | AGRI | DLMS Meter | 0.986 | 0.87946 | 0 | 0.986 | 10.8056 | 10.8056
3391 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904020303 | F08-KYALANUR-EXPRESS | NJY | DLMS Meter | 1.059 | 0.60393 | 0.39 | 0.669 | 9.7262 | 36.9726
3392 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904010104 | F09-NJY-A.R.AGRAHARA | NJY | DLMS Meter | 1.0536 | 0.9436 | 0 | 1.0536 | 10.4404 | 75.8058
3393 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904020304 | F10-NJY-KADAHALLI | NJY | DLMS Meter | 0.6966 | 0.62554 | 0 | 0.6966 | 10.2004 | 70.3809
3394 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | KYALANUR_66 | 1230102904010105 | F11-CHOLAGATTA | NJY | DLMS Meter | 0.5176 | 0.46126 | 0 | 0.5176 | 10.885 | 81.1122
3395 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905020305 | F01-KANGANDLAHALLI | AGRI | DLMS Meter | 0.39458 | 0.35498 | 0 | 0.39458 | 10.036 | 10.036
3396 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905020302 | F02-K.R.G.-HALLI | AGRI | DLMS Meter | 0.9493 | 0.85422 | 0 | 0.9493 | 10.0157 | 10.0157
3397 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905010101 | F03-GANGAPURA | AGRI | DLMS Meter | 0.96354 | 0.8672 | 0 | 0.96354 | 9.9991 | 9.9991
3398 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905010102 | F04-J.K.PURA-NJ | NJY | DLMS Meter | 1.8887 | 1.6492 | 0.0022 | 1.8865 | 12.5794 | 57.6089
3399 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905020303 | F05-JAKKARASAKUPPA(R-) | AGRI | DLMS Meter | 1.065 | 0.95848 | 0 | 1.065 | 10.0036 | 10.0036
3400 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905020101 | F06-MADIVALA | AGRI | DLMS Meter | 0.3769 | 0.33936 | 0 | 0.3769 | 9.9594 | 9.9594
3401 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905010103 | F07-MALLAPALLI(-R) | AGRI | DLMS Meter | 0.9156 | 0.82407 | 0 | 0.9156 | 9.9973 | 9.9973
3402 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905010104 | F08-MAHADEVPURA | AGRI | DLMS Meter | 0.25722 | 0.23145 | 0 | 0.25722 | 10.0171 | 10.0171
3403 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905020304 | F09-KAVARAGANAHALLI | AGRI | DLMS Meter | 0.55544 | 0.47535 | 0 | 0.55544 | 14.4199 | 14.4199
3404 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905010501 | F10-KYASAMBALLY NJY | NJY | DLMS Meter | 0.57158 | 0.49945 | 0 | 0.57158 | 12.6201 | 67.1068
3405 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905010502 | F11-BENNAVARA | AGRI | DLMS Meter | 0.8936 | 0.80411 | 0 | 0.8936 | 10.0145 | 10.0145
3406 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905010503 | F12-GENNERHALLI | AGRI | DLMS Meter | 0.72126 | 0.64917 | 0 | 0.72126 | 9.9943 | 9.9943
3407 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905010504 | F13-NJY KALLIKUPPA | NJY | DLMS Meter | 1.0586 | 0.69878 | 0.274 | 0.78462 | 10.9399 | 30.8323
3408 | BRAZ | KOLAR | KGF | BETHAMANGLA | KYASAMBALLI_66 | 1230203905010505 | F14-ALLIKALLU | AGRI | DLMS Meter | 0.50332 | 0.45295 | 0 | 0.50332 | 10.0075 | 10.0075
3409 | BRAZ | KOLAR | KGF | MALUR | LAKKUR_66 | 1230204901010101 | F01-PURA | AGRI | DLMS Meter | 1.3797 | 1.2417 | 0 | 1.3797 | 10.0025 | 10.0386
3410 | BRAZ | KOLAR | KGF | MALUR | LAKKUR_66 | 1230204901010102 | F02-CHIKKA-TIRUPATHI | AGRI | DLMS Meter | 1.1534 | 1.0383 | 0 | 1.1534 | 9.9803 | 9.9803
3411 | BRAZ | KOLAR | KGF | MALUR | LAKKUR_66 | 1230204901010103 | F03-LAKKUR | AGRI | DLMS Meter | 1.1966 | 1.077 | 0 | 1.1966 | 9.9964 | 10.1185
3412 | BRAZ | KOLAR | KGF | MALUR | LAKKUR_66 | 1230204901020301 | F04-CHENNIGARAYAPURA | NJY | DLMS Meter | 4.5507 | 4.0802 | 0 | 4.5507 | 10.3377 | 71.4447
3413 | BRAZ | KOLAR | KGF | MALUR | LAKKUR_66 | 1230204901020302 | F05-SAMPANGERE | NJY | DLMS Meter | 3.637 | 2.9152 | 0.37337 | 3.2636 | 10.6744 | 64.4377
3414 | BRAZ | KOLAR | KGF | MALUR | LAKKUR_66 | 1230204901010104 | F06-HOSAKOTE | AGRI | DLMS Meter | 1.2392 | 1.1151 | 0 | 1.2392 | 10.0197 | 10.0531
3415 | BRAZ | KOLAR | KGF | MALUR | LAKKUR_66 | 1230204901020303 | F07-KODIHALLI | AGRI | DLMS Meter | 1.3451 | 1.2104 | 0 | 1.3451 | 10.0161 | 10.3516
3416 | BRAZ | KOLAR | KGF | MALUR | LAKKUR_66 | 1230204901020304 | F09-FIRE-LUXOR | DOMESTIC | DLMS Meter | 1.1282 | 0.99317 | 0.0369 | 1.0913 | 8.9957 | 41.2414
3417 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906010101 | F01-PATHUR | AGRI | DLMS Meter | 1.1888 | 1.0699 | 0 | 1.1888 | 10.0013 | 10.0013
3418 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906010102 | F02-KASHETTIPALLI | AGRI | DLMS Meter | 0.96477 | 0.86802 | 0 | 0.96477 | 10.0283 | 10.0283
3419 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906010103 | F03-PULUGURUKOTE | AGRI | DLMS Meter | 1.7661 | 1.5897 | 0 | 1.7661 | 9.9909 | 9.9909
3420 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906010104 | F04-JONNAPALLI NJY | NJY | DLMS Meter | 0.70869 | 0.6494 | 0 | 0.70869 | 8.3657 | 80.579
3421 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906010301 | F05-RAYALAPADU | AGRI | DLMS Meter | 1.0126 | 0.91125 | 0 | 1.0126 | 10.0072 | 10.0072
3422 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906010302 | F06-SUNNAKAL | AGRI | DLMS Meter | 0.7442 | 0.66967 | 0 | 0.7442 | 10.0152 | 10.0152
3423 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906010303 | F07-LAKSHMIPURA-LOVCAL | AGRI | DLMS Meter | 1.0379 | 0.93403 | 0 | 1.0379 | 10.0058 | 10.0058
3424 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906010304 | F08-SONNAPALLI | AGRI | DLMS Meter | 0.21912 | 0.12294 | 0.0825 | 0.13662 | 10.0102 | 10.0102
3425 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906010305 | F09-NELAVANKI NJY | NJY | DLMS Meter | 1.0052 | 0.9148 | 0 | 1.0052 | 8.9932 | 71.9759
3426 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906010105 | F10- BANDARLAHALLI | AGRI | DLMS Meter | 0.6824 | 0.61416 | 0 | 0.6824 | 10.0003 | 10.0003
3427 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | LAKSHMIPURA_66 | 1230103906020302 | F11-THUPALLI NJY | NJY | DLMS Meter | 0.54002 | 0.49151 | 0 | 0.54002 | 8.9824 | 79.956
3428 | BMANZ | EAST | INDIRA NAGAR | E6 | LEELAVENTURE_66 | 1130203901010101 | F01-NGEF-P&T | DOMESTIC | DLMS Meter | 3.8588 | 3.0485 | 0.68148 | 3.1773 | 4.0532 | 5.1084
3429 | BMASZ | SOUTH | KORAMANGALA | S3 | LEELAVENTURE_66 | 1130203901020301 | F04-MANIPAL-HOSPITAL | COMMERCIAL | DLMS Meter | 4.7502 | 3.903 | 0.73017 | 4.02 | 2.9103 | 7.6556
3430 | BMANZ | EAST | INDIRA NAGAR | E6 | LEELAVENTURE_66 | 1130203901020103 | F05-LEELA-PALACE | COMMERCIAL | DLMS Meter | 2.881 | 2.4798 | 0.27854 | 2.6024 | 4.7116 | 4.7116
3431 | BMANZ | EAST | INDIRA NAGAR | E6 | LEELAVENTURE_66 | 1130203901020302 | F07-FLEELA-PALACE | COMMERCIAL | DLMS Meter | 0.40093 | 0.39893 | 0 | 0.40093 | 0.49884 | 0.49884
3432 | BMANZ | EAST | INDIRA NAGAR | E6 | LEELAVENTURE_66 | 1130203901020304 | F10-J-B-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.27 | 2.128 | 0.039269 | 2.2308 | 4.6087 | 6.5701
3433 | BMASZ | SOUTH | KORAMANGALA | S3 | LEELAVENTURE_66 | 1130203901020305 | F11-INTEL-TECH | INDUSTRIAL | DLMS Meter | 4.175 | 4.0335 | 0 | 4.175 | 3.3882 | 19.4791
3434 | BMANZ | EAST | INDIRA NAGAR | E6 | LEELAVENTURE_66 | 1130203901020106 | F12-DOMLUR-SERVICE-ROAD | URBAN MIXED LOAD | DLMS Meter | 2.2504 | 2.1304 | 0 | 2.2504 | 5.3315 | 6.763
3435 | BMANZ | EAST | INDIRA NAGAR | E6 | LEELAVENTURE_66 | 1130203901010102 | F14-ISRO | URBAN MIXED LOAD | DLMS Meter | 0.6579 | 0.65933 | 0 | 0.6579 | -0.21629 | -0.21629
3436 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902010101 | F01-ITTAGI | AGRI | DLMS Meter | 1.8516 | 1.6612 | 0 | 1.8516 | 10.2829 | 10.2829
3437 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902010102 | F02-ASTAPANAHALLI | AGRI | DLMS Meter | 1.6321 | 1.4649 | 0 | 1.6321 | 10.2448 | 10.2448
3438 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902010103 | F03-HIREMALALLI | AGRI | DLMS Meter | 1.8291 | 1.6427 | 0 | 1.8291 | 10.1856 | 10.1856
3439 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902010104 | F04-WATERWORKS | WATER WORKS | DLMS Meter | 0.9726 | 0.21809 | 0.73825 | 0.23435 | 6.939 | 67.3029
3440 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902020101 | F05-KAGATHUR | AGRI | DLMS Meter | 0.4058 | 0.31767 | 0.052 | 0.3538 | 10.2117 | 10.2117
3441 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902020301 | F06-GALIHALLI | AGRI | DLMS Meter | 1.7205 | 1.5095 | 0.042 | 1.6785 | 10.0701 | 10.0701
3442 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902020302 | F07-NALLUR | NJY | DLMS Meter | 1.4466 | 1.0852 | 0.2643 | 1.1823 | 8.2157 | 32.3021
3443 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902020303 | F08-HALESHPURA | AGRI | DLMS Meter | 2.378 | 2.0435 | 0.106 | 2.272 | 10.0565 | 10.0565
3444 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902010105 | F09-ASTAPANAHALLINJY | NJY | DLMS Meter | 1.419 | 0.28876 | 1.0965 | 0.3225 | 10.4614 | 56.9872
3445 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902010106 | F10-GKHALLINJY | NJY | DLMS Meter | 1.4308 | 0.47823 | 0.905 | 0.5258 | 9.0474 | 52.2654
3446 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902010301 | F11-SULEKERE-WATER-SUPPLY | WATER WORKS | DLMS Meter | 1.0676 | 1.01 | 0 | 1.0676 | 5.3934 | 71.1027
3447 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | LINGADAHALLI_66 | 1310106902010107 | F12-BULASAGARA NJY | NJY | DLMS Meter | 0.1551 | 0.14229 | 0 | 0.1551 | 8.2592 | 57.9283
3448 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | LINGADAHALLI_TMK2_66 | 1320306905010101 | F01-RANGASAMUDRA | AGRI | DLMS Meter | 0.92802 | 0.83515 | 0 | 0.92802 | 10.0079 | 10.0079
3449 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | LINGADAHALLI_TMK2_66 | 1320306905010105 | F02- S R PALYA | AGRI | DLMS Meter | 1.3353 | 1.2051 | 0 | 1.3353 | 9.7553 | 9.7553
3450 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | LINGADAHALLI_TMK2_66 | 1320306905010102 | F03-SASALAKUNTE | AGRI | DLMS Meter | 0.89208 | 0.80284 | 0 | 0.89208 | 10.0035 | 10.0035
3451 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | LINGADAHALLI_TMK2_66 | 1320306905010103 | F04-MALLAMMANAHALLI | AGRI | DLMS Meter | 1.3704 | 1.2392 | 0 | 1.3704 | 9.5747 | 9.5747
3452 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | LINGADAHALLI_TMK2_66 | 1320306905020301 | F05-NIDGAL | AGRI | DLMS Meter | 1.5055 | 1.3611 | 0 | 1.5055 | 9.5935 | 9.5935
3453 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | LINGADAHALLI_TMK2_66 | 1320306905020302 | F07-MUDDAGANAHALLY | AGRI | DLMS Meter | 1.2913 | 1.162 | 0 | 1.2913 | 10.0088 | 10.0088
3454 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | LINGADAHALLI_TMK2_66 | 1320306905020303 | F08-LINGADAHALLI | AGRI | DLMS Meter | 0.35984 | 0.32372 | 0 | 0.35984 | 10.0378 | 13.1366
3455 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | LINGADAHALLI_TMK2_66 | 1320306905010106 | F09-NJY-R-GOVARDHANGIRI | NJY | DLMS Meter | 0.25148 | 0.22657 | 0 | 0.25148 | 9.9042 | 73.6344
3456 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | LINGADAHALLI_TMK2_66 | 1320306905010107 | F10-NJY-NIDAGALLU | NJY | DLMS Meter | 0.7518 | 0.66917 | 0 | 0.7518 | 10.9904 | 74.738
3457 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | LINGADAHALLI_TMK2_66 | 1320306905020304 | F11-NJY-KENCHAMMANAHALLI | NJY | DLMS Meter | 0.81129 | 0.73067 | 0 | 0.81129 | 9.9373 | 65.5072
3458 | BMANZ | NORTH | HEBBAL | C5 | LRBANDE_66 | 1120302901010301 | F01-KB-SANDRA | URBAN MIXED LOAD | DLMS Meter | 1.8006 | 1.4925 | 0.08 | 1.7206 | 13.2539 | 17.4363
3459 | BMANZ | NORTH | HEBBAL | C5 | LRBANDE_66 | 1120302901010302 | F02-CAUVERY-NAGAR | URBAN MIXED LOAD | DLMS Meter | 1.8123 | 1.2292 | 0.47 | 1.3423 | 8.4237 | 15.9064
3460 | BMANZ | EAST | SHIVAJINAGAR | E9 | LRBANDE_66 | 1120302901010303 | F04-BEL | COMMERCIAL | DLMS Meter | 5.1175 | 1.51 | 3.4738 | 1.6437 | 8.134 | 8.134
3461 | BMANZ | NORTH | HEBBAL | C5 | LRBANDE_66 | 1120302901010102 | F05-AMBEDKAR-COLLEGE | URBAN MIXED LOAD | DLMS Meter | 5.6425 | 4.611 | 0.25682 | 5.3857 | 14.3849 | 24.0573
3462 | BMANZ | NORTH | HEBBAL | C5 | LRBANDE_66 | 1120302901010103 | F06-FD-J-HALLI | URBAN MIXED LOAD | DLMS Meter | 6.1101 | 5.2558 | 0.00486 | 6.1053 | 13.9131 | 24.1393
3463 | BMANZ | EAST | SHIVAJINAGAR | E1 | LRBANDE_66 | 1120302901010104 | F07 A-K-ASHRAM | URBAN MIXED LOAD | DLMS Meter | 3.9211 | 3.4984 | 0.045322 | 3.8757 | 9.7368 | 18.9897
3464 | BMANZ | NORTH | HEBBAL | C5 | LRBANDE_66 | 1120302901010304 | F08-GANESHA-BLOCK | URBAN MIXED LOAD | DLMS Meter | 3.4358 | 3.0585 | 0 | 3.4358 | 10.9819 | 20.5326
3465 | BMANZ | NORTH | HEBBAL | C5 | LRBANDE_66 | 1120302901010105 | F09-PERIYAR-NAGAR | URBAN MIXED LOAD | DLMS Meter | 5.4439 | 4.6227 | 0.04 | 5.4039 | 14.4555 | 26.5318
3466 | BMANZ | EAST | SHIVAJINAGAR | E9 | LRBANDE_66 | 1120302901010305 | F10-VHBCSLAYOUT | URBAN MIXED LOAD | DLMS Meter | 7.9037 | 7.31 | 0 | 7.9037 | 7.5108 | 11.3306
3467 | BMANZ | EAST | SHIVAJINAGAR | E9 | LRBANDE_66 | 1120302901010306 | F11-CHANAKYALAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.8937 | 4.5359 | 0.24412 | 4.6496 | 2.4439 | 2.4439
3468 | BMANZ | NORTH | HEBBAL | C5 | LRBANDE_66 | 1120302901010307 | F12-V-NAGENAHALLI | URBAN MIXED LOAD | DLMS Meter | 5.7908 | 3.058 | 2.4891 | 3.3017 | 7.3813 | 19.1598
3469 | BMANZ | NORTH | HEBBAL | C5 | LRBANDE_66 | 1120302901010308 | F14-MODI-ROAD | URBAN MIXED LOAD | DLMS Meter | 5.7265 | 4.8604 | 0.0196 | 5.7069 | 14.833 | 36.2093
3470 | BMANZ | NORTH | HEBBAL | C5 | LRBANDE_66 | 1120302901020401 | F15-BMRCL | RAILWAYS OR METRO | DLMS Meter | 2.0732 | 2.0636 | 0 | 2.0732 | 0.46256 | 0.46256
3471 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | MADADAKERE_66 | 1310204908010101 | F01-SEERANAKATTE | AGRI | DLMS Meter | 0.72346 | 0.65086 | 0 | 0.72346 | 10.0346 | 10.0346
3472 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | MADADAKERE_66 | 1310204908010104 | F02-RANGAPPA TEMPLE | NJY | DLMS Meter | 0.3146 | 0.25668 | 0.024059 | 0.29054 | 11.6534 | 40.6569
3473 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | MADADAKERE_66 | 1310204908010102 | F03-S K HALLI | AGRI | DLMS Meter | 0.9094 | 0.81869 | 0 | 0.9094 | 9.9747 | 9.9747
3474 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | MADADAKERE_66 | 1310204908010103 | F04-KENKERE | AGRI | DLMS Meter | 0.8392 | 0.75514 | 0 | 0.8392 | 10.0164 | 10.0164
3475 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | MADADAKERE_66 | 1310204908020102 | F06-NAKIKERE | AGRI | DLMS Meter | 1.555 | 1.3994 | 0 | 1.555 | 10.0048 | 10.0048
3476 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | MADADAKERE_66 | 1310204908020103 | F07-POOJARAHATTI | AGRI | DLMS Meter | 0.4868 | 0.43793 | 0 | 0.4868 | 10.0386 | 10.0386
3477 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | MADADAKERE_66 | 1310204908020101 | F08-MADADAKERE NJY | NJY | DLMS Meter | 0.55 | 0.35886 | 0.14415 | 0.40585 | 11.5772 | 39.9837
3478 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | MADANAYAKANAHALLI_66 | 1310201902010106 | F00-NJY INAHALLI | NJY | DLMS Meter | 0.94 | 0.73333 | 0.14002 | 0.79998 | 8.3312 | 26.7139
3479 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | MADANAYAKANAHALLI_66 | 1310201902010101 | F01-MDKHALLI | AGRI | DLMS Meter | 0.74003 | 0.65123 | 0 | 0.74003 | 12.0008 | 12.0008
3480 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | MADANAYAKANAHALLI_66 | 1310201902010102 | F02-CGHALLI | AGRI | DLMS Meter | 0.85925 | 0.75179 | 0 | 0.85925 | 12.5063 | 12.5063
3481 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | MADANAYAKANAHALLI_66 | 1310201902010104 | F03-NJY YALAVERTHI | NJY | DLMS Meter | 0.77594 | 0.52291 | 0.20194 | 0.574 | 8.9012 | 43.3368
3482 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | MADANAYAKANAHALLI_66 | 1310201902010103 | F04-MUDDAPURA | AGRI | DLMS Meter | 0.98954 | 0.86345 | 0 | 0.98954 | 12.7416 | 12.7416
3483 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | MADANAYAKANAHALLI_66 | 1310201902010105 | F06-HOSAGOLARAHATTI | AGRI | DLMS Meter | 0.91796 | 0.82591 | 0 | 0.91796 | 10.0273 | 10.0273
3484 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | MADANAYAKANAHALLI_66 | 1310201902020301 | F07-RAYANAHALLI | AGRI | DLMS Meter | 1.0085 | 0.89628 | 0 | 1.0085 | 11.131 | 11.131
3485 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | MADANAYAKANAHALLI_66 | 1310201902020302 | F08-SURENAHALLI | AGRI | DLMS Meter | 1.254 | 1.1251 | 0 | 1.254 | 10.2832 | 10.2832
3486 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_220 | 1320301904020101 | F01-GONDIHALLI IDLE | IDLE | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3487 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_220 | 1320301904020102 | F02-RANGANAHALLY-NJY | NJY | DLMS Meter | 0.27692 | 0.2525 | 0 | 0.27692 | 8.8166 | 60.0616
3488 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_220 | 1320301904020103 | F03-SHETTYHALLY | AGRI | DLMS Meter | 0.78482 | 0.71674 | 0 | 0.78482 | 8.6741 | 8.6741
3489 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_220 | 1320301904020301 | F04-BALENAHALLI | AGRI | DLMS Meter | 0.90776 | 0.81691 | 0 | 0.90776 | 10.0079 | 10.0079
3490 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_220 | 1320301904010301 | F07-INDUSTRIAL | DOMESTIC | DLMS Meter | 1.043 | 0.68965 | 0.266 | 0.77704 | 11.2464 | 14.4835
3491 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_220 | 1320301904010101 | F08-BANDREHALLY | AGRI | DLMS Meter | 1.3071 | 1.1764 | 0 | 1.3071 | 9.9993 | 9.9993
3492 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_220 | 1320301904010102 | F09-SHOMBONAHALLY | AGRI | DLMS Meter | 0.6133 | 0.55999 | 0 | 0.6133 | 8.6928 | 8.6928
3493 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_220 | 1320301904010103 | F10-AMARAVATHI | AGRI | DLMS Meter | 1.3815 | 1.2416 | 0 | 1.3815 | 10.1267 | 14.5018
3494 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_220 | 1320301904020302 | F12-GANJALAGUNTE NJY | NJY | DLMS Meter | 0.57634 | 0.52223 | 0 | 0.57634 | 9.3892 | 58.8872
3495 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907010101 | F01-ARENAHALLY | AGRI | DLMS Meter | 1.012 | 0.89507 | 0 | 1.012 | 11.5547 | 11.5547
3496 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907010102 | F02-MADHUGIRI-TOWN | DOMESTIC | DLMS Meter | 3.3962 | 2.7649 | 0.285 | 3.1112 | 11.1324 | 12.9681
3497 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907010103 | F03-CHINAKAVAJRA NJY | NJY | DLMS Meter | 0.2574 | 0.23114 | 0 | 0.2574 | 10.2016 | 59.4631
3498 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907010104 | F04-BHOOTHANAHALLY | AGRI | DLMS Meter | 1.3626 | 1.2024 | 0 | 1.3626 | 11.7591 | 12.1213
3499 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907010105 | F05-CHINAKAVAJRA | AGRI | DLMS Meter | 0.94538 | 0.83813 | 0 | 0.94538 | 11.345 | 11.345
3500 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907020301 | F06-D.V.HALLY | AGRI | DLMS Meter | 1.192 | 1.0704 | 0 | 1.192 | 10.2008 | 10.2008
3501 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907020302 | F08-KAMBATHANAHALLY | AGRI | DLMS Meter | 0.18766 | 0.16884 | 0 | 0.18766 | 10.0314 | 10.0314
3502 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907020303 | F09-SIDDAPURA | AGRI | DLMS Meter | 1.2292 | 1.0823 | 0 | 1.2292 | 11.9491 | 11.9491
3503 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907020304 | F10-DABBEGHATTA | AGRI | DLMS Meter | 1.8474 | 1.6626 | 0 | 1.8474 | 10.0024 | 10.8659
3504 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907010107 | F11-JADEGONDANAHALLY NJY | NJY | DLMS Meter | 0.3602 | 0.30102 | 0.03 | 0.3302 | 8.8365 | 43.0397
3505 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MADHUGIRI_66 | 1320301907010108 | F12-THIMMALAPURA NJY | NJY | DLMS Meter | 0.7279 | 0.6273 | 0.04 | 0.6879 | 8.8094 | 52.1771
3506 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902010101 | F02-MAGADI-TOWN | URBAN MIXED LOAD | DLMS Meter | 2.4907 | 1.7878 | 0.48 | 2.0107 | 11.0822 | 12.8187
3507 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902010102 | F03-KALARI | AGRI | DLMS Meter | 1.0508 | 0.94582 | 0 | 1.0508 | 9.9939 | 9.9939
3508 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902010103 | F04-GUDEMARANAHALLI | AGRI | DLMS Meter | 0.49263 | 0.44325 | 0 | 0.49263 | 10.0248 | 10.0248
3509 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902020301 | F05-CHAKRABALVI | AGRI | DLMS Meter | 1.3981 | 1.2586 | 0 | 1.3981 | 9.9738 | 9.9738
3510 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902020302 | F06-KENCHANAHALLI | AGRI | DLMS Meter | 0.83314 | 0.74963 | 0 | 0.83314 | 10.0239 | 10.0239
3511 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902010107 | F07-SIDAGANAHALLI | AGRI | DLMS Meter | 0.7678 | 0.61898 | 0.08 | 0.6878 | 10.0057 | 10.0057
3512 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902010104 | F08-TAGIKUPPE | URBAN MIXED LOAD | DLMS Meter | 0.5096 | 0.35938 | 0.1 | 0.4096 | 12.2611 | 17.803
3513 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902020303 | F09-SAVANADURGA | AGRI | DLMS Meter | 0.67139 | 0.60425 | 0 | 0.67139 | 10.0007 | 10.0007
3514 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902010105 | F10-VENGALAPPANAHALLI CRUSHERS | INDUSTRIAL | DLMS Meter | 0.96074 | 0.88077 | 0.008 | 0.95274 | 7.5542 | 14.9128
3515 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902020304 | F11-NETHENAHALLI | RURAL MIXED LOAD | DLMS Meter | 0.60078 | 0.42213 | 0.13 | 0.47078 | 10.3341 | 22.7973
3516 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902020305 | F12-KALYAGATE | URBAN MIXED LOAD | DLMS Meter | 2.8601 | 2.4523 | 0.15 | 2.7101 | 9.5117 | 9.748
3517 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902020306 | F13-MADABAL | URBAN MIXED LOAD | DLMS Meter | 1.0801 | 0.70718 | 0.298 | 0.78209 | 9.5786 | 12.9694
3518 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902010109 | F14-BELAGUMBA NJY | NJY | DLMS Meter | 0.6105 | 0.28511 | 0.293 | 0.3175 | 10.201 | 34.3059
3519 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902010108 | F15 - JODAGATTE NJY | NJY | DLMS Meter | 0.3847 | 0.19166 | 0.173 | 0.2117 | 9.4674 | 20.6371
3520 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MAGADI_66 | 1210102902010110 | F16-CHANDURAYANAHALLI | NJY | DLMS Meter | 0.44072 | 0.30828 | 0.1 | 0.34072 | 9.5224 | 43.4208
3521 | BMASZ | WEST | RAJAJINAGAR | N3 | MAHALAKSHMILAYOUT_66 | 1120103901010101 | F01-THIMMAIAH-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.4295 | 3.1503 | 0 | 3.4295 | 8.1411 | 11.9357
3522 | BMASZ | WEST | RAJAJINAGAR | N3 | MAHALAKSHMILAYOUT_66 | 1120103901010102 | F02-BASAWESHWARA-NAGARA | URBAN MIXED LOAD | DLMS Meter | 4.1636 | 3.9014 | 0 | 4.1636 | 6.2977 | 12.216
3523 | BMASZ | WEST | RAJAJINAGAR | N3 | MAHALAKSHMILAYOUT_66 | 1120103901010103 | F03-SHANKARMATT | URBAN MIXED LOAD | DLMS Meter | 3.407 | 3.1952 | 0 | 3.407 | 6.2162 | 13.8995
3524 | BMANZ | NORTH | PEENYA | N7 | MAHALAKSHMILAYOUT_66 | 1120103901010104 | F04-NAGAPURA-PARK | URBAN MIXED LOAD | DLMS Meter | 2.6634 | 2.4984 | 0 | 2.6634 | 6.195 | 11.9417
3525 | BMANZ | NORTH | PEENYA | N7 | MAHALAKSHMILAYOUT_66 | 1120103901010105 | F05-HAMSA-SAGAR | URBAN MIXED LOAD | DLMS Meter | 2.998 | 2.6871 | 0.040064 | 2.9579 | 9.1543 | 19.202
3526 | BMASZ | WEST | RAJAJINAGAR | N1 | MAHALAKSHMILAYOUT_66 | 1120103901010106 | F06-FKETHAMARANAHALLY | URBAN MIXED LOAD | DLMS Meter | 2.4134 | 0.71323 | 1.6845 | 0.72892 | 2.1535 | 4.1287
3527 | BMASZ | WEST | RAJAJINAGAR | N3 | MAHALAKSHMILAYOUT_66 | 1120103901020301 | F07-F-GUDDAGANAPATHI | URBAN MIXED LOAD | DLMS Meter | 1.2532 | 1.1941 | 0 | 1.2532 | 4.715 | 10.7879
3528 | BMANZ | NORTH | PEENYA | N7 | MAHALAKSHMILAYOUT_66 | 1120103901020302 | F08-BOVI-PALYA | URBAN MIXED LOAD | DLMS Meter | 3.4314 | 3.0432 | 0.16917 | 3.2622 | 6.7152 | 15.368
3529 | BMANZ | NORTH | PEENYA | N7 | MAHALAKSHMILAYOUT_66 | 1120103901020303 | F09-G.D-NAIDU-HALL | URBAN MIXED LOAD | DLMS Meter | 2.5143 | 2.3059 | 0 | 2.5143 | 8.2889 | 13.9047
3530 | BMANZ | NORTH | PEENYA | N7 | MAHALAKSHMILAYOUT_66 | 1120103901020304 | F10-WADPACK | INDUSTRIAL | DLMS Meter | 3.2453 | 2.7271 | 0.25181 | 2.9935 | 8.9016 | 12.2978
3531 | BMANZ | NORTH | PEENYA | N7 | MAHALAKSHMILAYOUT_66 | 1120103901020305 | F12-ESTEEM-CLASSIC | URBAN MIXED LOAD | DLMS Meter | 1.163 | 0.67772 | 0.44548 | 0.71756 | 5.5527 | 6.4318
3532 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905010101 | F01-KOKKANUR | AGRI | DLMS Meter | 1.0456 | 0.94083 | 0 | 1.0456 | 10.0197 | 10.0197
3533 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905010102 | F02-MALEBENNUR | NJY | DLMS Meter | 3.2756 | 2.8079 | 0.1835 | 3.0921 | 9.1926 | 14.0842
3534 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905010103 | F03-HALIVANA | AGRI | DLMS Meter | 1.4682 | 1.3218 | 0 | 1.4682 | 9.9742 | 9.9742
3535 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905010104 | F04-GOVINAHAL | AGRI | DLMS Meter | 1.0922 | 0.98278 | 0 | 1.0922 | 10.0187 | 10.0187
3536 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905020301 | F05-NANDITAVARE | AGRI | DLMS Meter | 1.31 | 1.1793 | 0 | 1.31 | 9.9739 | 9.9739
3537 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905020101 | F06-BUDIHAL | AGRI | DLMS Meter | 0.72145 | 0.64935 | 0 | 0.72145 | 9.9942 | 9.9942
3538 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905020302 | F07-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 0.2574 | 0.2355 | 0 | 0.2574 | 8.5076 | 9.7463
3539 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905020303 | F08-JIGALI | AGRI | DLMS Meter | 0.8572 | 0.77097 | 0 | 0.8572 | 10.06 | 10.06
3540 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905020304 | F09-SRI-RANGANATHA--NJY | NJY | DLMS Meter | 0.37786 | 0.34785 | 0 | 0.37786 | 7.9429 | 41.274
3541 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905020305 | F10-GUDADAHALLI-NJY | NJY | DLMS Meter | 0.5123 | 0.46139 | 0 | 0.5123 | 9.9377 | 49.9177
3542 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905020306 | F11-KUNIBELEKERI-NJY | NJY | DLMS Meter | 0.5898 | 0.5354 | 0 | 0.5898 | 9.224 | 43.1848
3543 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | MALEBENNUR_66 | 1310301905020307 | F12-HINDASAGATTA NJY | NJY | DLMS Meter | 0.68135 | 0.60923 | 0.0135 | 0.66785 | 8.7776 | 47.4659
3544 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | MALLADIHALLI_ 66 | 1310203908010103 | F01-SHIVAPURA | AGRI | DLMS Meter | 1.5273 | 0.80574 | 0.63202 | 0.89524 | 9.998 | 9.998
3545 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | MALLADIHALLI_ 66 | 1310203908010104 | F02-RAMAGHATTA | AGRI | DLMS Meter | 0.63202 | 0.59721 | 0 | 0.63202 | 5.507 | 5.507
3546 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | MALLADIHALLI_ 66 | 1310203908010101 | F03-KENGUNTE | NJY | DLMS Meter | 0.6745 | 0.5137 | 0.097198 | 0.5773 | 11.0176 | 34.8502
3547 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | MALLADIHALLI_ 66 | 1310203908010102 | F04-DUMMI | AGRI | DLMS Meter | 1.0799 | 0.9427 | 0 | 1.0799 | 12.7017 | 12.7017
3548 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | MALLADIHALLI_ 66 | 1310203908020103 | F06-KUNAGALI NJY | NJY | DLMS Meter | 0.74001 | 0.28058 | 0.42069 | 0.31932 | 12.1327 | 58.0354
3549 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | MALLADIHALLI_ 66 | 1310203908020101 | F07-HULEMALALI | AGRI | DLMS Meter | 1.5459 | 1.3272 | 0 | 1.5459 | 14.1502 | 14.1502
3550 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | MALLADIHALLI_ 66 | 1310203908020102 | F08-AGRAHARA | AGRI | DLMS Meter | 1.457 | 1.0511 | 0.2346 | 1.2224 | 14.0157 | 14.0157
3551 | BRAZ | KOLAR | KGF | MULABAGILU | MALLANAYAKANAHALLI_66 | 1230202908010201 | F01-MITTAHALLI | AGRI | DLMS Meter | 1.0614 | 0.95501 | 0 | 1.0614 | 10.0243 | 10.0243
3552 | BRAZ | KOLAR | KGF | MULABAGILU | MALLANAYAKANAHALLI_66 | 1230202908010202 | F02-VAJRANAGENAHALLI | AGRI | DLMS Meter | 1.0036 | 0.54148 | 0.4019 | 0.60174 | 10.0146 | 10.0146
3553 | BRAZ | KOLAR | KGF | MULABAGILU | MALLANAYAKANAHALLI_66 | 1230202908010203 | F03-PUTTENAHALLI | AGRI | DLMS Meter | 0.73313 | 0.65961 | 0 | 0.73313 | 10.028 | 10.028
3554 | BRAZ | KOLAR | KGF | MULABAGILU | MALLANAYAKANAHALLI_66 | 1230202908010204 | F04-BELAGANAHALLI | AGRI | DLMS Meter | 0.90728 | 0.62652 | 0.211 | 0.69628 | 10.0195 | 10.0195
3555 | BRAZ | KOLAR | KGF | MULABAGILU | MALLANAYAKANAHALLI_66 | 1230202908010205 | F08-CHUKKANAHALLI | NJY | DLMS Meter | 0.29436 | 0.26537 | 0 | 0.29436 | 9.8471 | 72.6132
3556 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | MALLAPPANAHALLY_66 | 1310401911020101 | F01-SALLABOMMANAHALLY | AGRI | DLMS Meter | 1.0838 | 0.96818 | 0 | 1.0838 | 10.6676 | 10.6676
3557 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | MALLAPPANAHALLY_66 | 1310401911020102 | F03-HARTHIKOTE | AGRI | DLMS Meter | 0.5222 | 0.46444 | 0 | 0.5222 | 11.0618 | 11.1542
3558 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | MALLAPPANAHALLY_66 | 1310401911010101 | F05-MALLAPPANAHALLY | NJY | DLMS Meter | 0.7034 | 0.63267 | 0 | 0.7034 | 10.0558 | 43.763
3559 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | MALLAPPANAHALLY_66 | 1310401911010102 | F06-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 0.098373 | 0.092883 | 0 | 0.098373 | 5.5808 | 6.9851
3560 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | MALLAPPANAHALLY_66 | 1310401911010103 | F07-G.B.HALLY | NJY | DLMS Meter | 0.7086 | 0.67335 | 0 | 0.7086 | 4.9749 | 53.5516
3561 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | MALLAPPANAHALLY_66 | 1310401911010104 | F08-BHOTAPPANAGUDI | AGRI | DLMS Meter | 0.5456 | 0.49094 | 0 | 0.5456 | 10.0189 | 10.0189
3562 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902010301 | F01-S.G.PALYA | AGRI | DLMS Meter | 0.84766 | 0.7712 | 0 | 0.84766 | 9.0201 | 9.0201
3563 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902020101 | F02-HABBATANAHALLI | AGRI | DLMS Meter | 0.98468 | 0.85567 | 0 | 0.98468 | 13.1016 | 13.1016
3564 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902020102 | F03-MALLASANDRA TOWN | RURAL MIXED LOAD | DLMS Meter | 1.501 | 1.2842 | 0.038 | 1.463 | 12.2206 | 22.3251
3565 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902020103 | F04-PUTTANAPALYA | AGRI | DLMS Meter | 0.9672 | 0.85842 | 0 | 0.9672 | 11.2471 | 11.2471
3566 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902010302 | F05-KAGGERE | AGRI | DLMS Meter | 1.9056 | 1.6736 | 0 | 1.9056 | 12.177 | 12.177
3567 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902010306 | F06-GOLLAHALLI-NJY | NJY | DLMS Meter | 0.57626 | 0.5196 | 0 | 0.57626 | 9.8322 | 57.5811
3568 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902010303 | F07-DODDANARVANGALA | AGRI | DLMS Meter | 0.95088 | 0.85555 | 0 | 0.95088 | 10.0259 | 10.0259
3569 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902010304 | F08-CHOWKENAHALLI | AGRI | DLMS Meter | 1.1719 | 1.0161 | 0 | 1.1719 | 13.2937 | 13.3985
3570 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902010305 | F09-KMF | INDUSTRIAL | DLMS Meter | 1.7493 | 1.7799 | 0 | 1.7493 | -1.7475 | -1.7475
3571 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902010101 | F11-JOGIRANAHATTY | AGRI | DLMS Meter | 0.95294 | 0.85771 | 0 | 0.95294 | 9.9934 | 9.9934
3572 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902010307 | F12-MUDIGERE | AGRI | DLMS Meter | 0.83246 | 0.73717 | 0 | 0.83246 | 11.4472 | 12.1137
3573 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902010103 | F13-GOWDIHALLI | AGRI | DLMS Meter | 1.1834 | 1.0279 | 0 | 1.1834 | 13.1377 | 13.1377
3574 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | MALLASANDRA_BNG_66 | 1230102906010101 | F01-MUDUVADI | AGRI | DLMS Meter | 1.7942 | 1.5893 | 0 | 1.7942 | 11.4184 | 13.2119
3575 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | MALLASANDRA_BNG_66 | 1230102906010102 | F02-NJY-BELLAMBURI | NJY | DLMS Meter | 1.9206 | 1.7228 | 0 | 1.9206 | 10.301 | 66.9268
3576 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | MALLASANDRA_BNG_66 | 1230102906010103 | F04-ARINAGENAHALLI | AGRI | DLMS Meter | 0.5766 | 0.51667 | 0 | 0.5766 | 10.3928 | 10.3928
3577 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | MALLASANDRA_BNG_66 | 1230102906020301 | F05-VEERAPURA | AGRI | DLMS Meter | 0.5919 | 0.53275 | 0 | 0.5919 | 9.9924 | 22.1802
3578 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | MALLASANDRA_BNG_66 | 1230102906020302 | F06-NJY-YADAHALLI | NJY | DLMS Meter | 0.7001 | 0.62003 | 0 | 0.7001 | 11.4365 | 65.3299
3579 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | MALLASANDRA_BNG_66 | 1230102906020303 | F07-NUKKANAHALLI | AGRI | DLMS Meter | 1.5246 | 1.361 | 0 | 1.5246 | 10.7336 | 10.7336
3580 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | MALLASANDRA_BNG_66 | 1230102906020304 | F08-ANNEHALLI | AGRI | DLMS Meter | 1.5346 | 1.3628 | 0 | 1.5346 | 11.196 | 11.196
3581 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904010101 | F01-LAKKUR | AGRI | DLMS Meter | 1.0073 | 0.90679 | 0 | 1.0073 | 9.9778 | 9.9778
3582 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904010102 | F02-ARALERI | AGRI | DLMS Meter | 1.7594 | 1.5824 | 0 | 1.7594 | 10.0586 | 10.1944
3583 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904010103 | F03-KUDIYANUR | AGRI | DLMS Meter | 1.9634 | 1.7665 | 0 | 1.9634 | 10.0299 | 10.0299
3584 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904020301 | F04-MALUR-RURAL | AGRI | DLMS Meter | 0.9089 | 0.81794 | 0 | 0.9089 | 10.0077 | 10.0077
3585 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904020302 | F05-SHIVARAPATNA | AGRI | DLMS Meter | 0.4485 | 0.39977 | 0 | 0.4485 | 10.8659 | 33.519
3586 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904020303 | F06-MALUR-TOWN | DOMESTIC | DLMS Meter | 1.3774 | 1.2347 | 0.02 | 1.3574 | 9.0389 | 29.8871
3587 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904020304 | F07-CHIKKAKUNTHUR | AGRI | DLMS Meter | 1.6105 | 1.4496 | 0 | 1.6105 | 9.9924 | 9.9924
3588 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904030501 | F08-INDUSTRIAL-AREA | DOMESTIC | DLMS Meter | 1.0068 | 0.85108 | 0.065 | 0.94184 | 9.6361 | 26.5831
3589 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904030502 | F10-KUMBARPET | DOMESTIC | DLMS Meter | 4.1384 | 3.6837 | 0.1 | 4.0384 | 8.7835 | 44.5977
3590 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904030503 | F11-WATERSUPPLY | DOMESTIC | DLMS Meter | 0.47564 | 0.42543 | 0.01 | 0.46564 | 8.6354 | 50.1416
3591 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904030504 | F12-CHANNAKAL | NJY | DLMS Meter | 3.3449 | 3.0228 | 0 | 3.3449 | 9.631 | 66.7274
3592 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904010104 | F13-ABBENAHALLI | AGRI | DLMS Meter | 1.0625 | 0.97471 | 0 | 1.0625 | 8.2628 | 15.6723
3593 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904010201 | F15-CHOKKANDAHALLI | NJY | DLMS Meter | 1.278 | 1.1834 | 0 | 1.278 | 7.403 | 53.3439
3594 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904010202 | F16-DODDASHIVARA | NJY | DLMS Meter | 1.116 | 1.0084 | 0 | 1.116 | 9.6424 | 47.6676
3595 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904010203 | F17-INDUSTRIAL EXPRESS | INDUSTRIAL | DLMS Meter | 3.8488 | 2.4738 | 1.16 | 2.6888 | 7.9965 | 7.9965
3596 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904020305 | F18-PURVA | DOMESTIC | DLMS Meter | 1.1702 | 1.0695 | 0 | 1.1702 | 8.6077 | 35.0169
3597 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904010110 | F19-HUNGENAHALLI | AGRI | DLMS Meter | 1.2202 | 1.0977 | 0 | 1.2202 | 10.0402 | 11.7805
3598 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904010109 | F20-HAROHALLI | DOMESTIC | DLMS Meter | 1.6233 | 1.475 | 0 | 1.6233 | 9.1379 | 34.4935
3599 | BRAZ | KOLAR | KGF | MALUR | MALUR_66 | 1230204904020306 | F21-MARIKAMBA | DOMESTIC | DLMS Meter | 3.902 | 3.6573 | 0 | 3.902 | 6.2715 | 48.9812
3600 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903010101 | F01-AEGON BATTERY | INDUSTRIAL | DLMS Meter | 1.788 | 1.8112 | 0 | 1.788 | -1.2968 | 0.6866
3601 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903010102 | F02-KURANDAHALLI | AGRI | DLMS Meter | 0.87446 | 0.78673 | 0 | 0.87446 | 10.0324 | 10.0324
3602 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903010103 | F03-LAXMI-ROSHAN | INDUSTRIAL | DLMS Meter | 2.7325 | 2.6553 | 0 | 2.7325 | 2.8229 | 3.2651
3603 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903010104 | F04-S-PRAKASH | INDUSTRIAL | DLMS Meter | 2.8972 | 1.2289 | 1.595 | 1.3022 | 5.6286 | 5.8576
3604 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903020301 | F05-S.L-CEREMIC | INDUSTRIAL | DLMS Meter | 3.4261 | 3.2609 | 0 | 3.4261 | 4.8215 | 5.1046
3605 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903020302 | F06-BENSAR | INDUSTRIAL | DLMS Meter | 2.7401 | 2.6724 | 0 | 2.7401 | 2.4715 | 2.4715
3606 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903020303 | F07-SRS STEEL | INDUSTRIAL | DLMS Meter | 5.8306 | 5.7181 | 0 | 5.8306 | 1.9281 | 2.3373
3607 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903020304 | F08-FOURTH-PHASE-KIDAB | INDUSTRIAL | DLMS Meter | 8.4745 | 1.0399 | 7.38 | 1.0945 | 4.991 | 10.7003
3608 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903010105 | F09-NOSAGERE | NJY | DLMS Meter | 2.4967 | 2.2544 | 0 | 2.4967 | 9.7064 | 27.1683
3609 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903010201 | F10-FLIPKART | INDUSTRIAL | DLMS Meter | 2.8461 | 2.5961 | 0 | 2.8461 | 8.7829 | 10.2376
3610 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903010202 | F11-APPOLO TRICOAT | INDUSTRIAL | DLMS Meter | 1.0936 | 1.0313 | 0 | 1.0936 | 5.6978 | 5.6978
3611 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903010203 | F12-CITY GRANITE | INDUSTRIAL | DLMS Meter | 3.0129 | 1.648 | 1.258 | 1.7549 | 6.0905 | 6.3131
3612 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903010204 | F13-BHAGYA LAKSHMI | INDUSTRIAL | DLMS Meter | 4.8605 | 4.7966 | 0 | 4.8605 | 1.3154 | 1.3154
3613 | BRAZ | KOLAR | KGF | MALUR | MALUR_IND_AREA_66 | 1230204903010205 | F15-IFB | INDUSTRIAL | DLMS Meter | 2.7298 | 2.6995 | 0 | 2.7298 | 1.11 | 1.11
3614 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904010106 | F01-DANDIGANAHALLY | AGRI | DLMS Meter | 0.7275 | 0.65462 | 0 | 0.7275 | 10.0183 | 10.0183
3615 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904010101 | F02-ADDEKOPPA | AGRI | DLMS Meter | 0.86542 | 0.70692 | 0.08 | 0.78542 | 9.9948 | 9.9948
3616 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904010102 | F03-JARABANDAHALLY | AGRI | DLMS Meter | 1.1611 | 1.0452 | 0 | 1.1611 | 9.9829 | 9.9829
3617 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904010103 | F04-POSHETTYHALLY | AGRI | DLMS Meter | 1.1145 | 1.0029 | 0 | 1.1145 | 10.0176 | 10.0176
3618 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904010104 | F06-KANAGANAKOPPA | AGRI | DLMS Meter | 1.0421 | 0.93774 | 0 | 1.0421 | 10.0165 | 10.0165
3619 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904020301 | F07-BISILAHALLY | AGRI | DLMS Meter | 1.746 | 1.5713 | 0 | 1.746 | 10.003 | 10.003
3620 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904020302 | F08-NJY-MANCHENAHALLY | NJY | DLMS Meter | 1.454 | 1.2526 | 0 | 1.454 | 13.851 | 49.905
3621 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904020303 | F09-MINAKANAGURKI | AGRI | DLMS Meter | 0.97626 | 0.75706 | 0.135 | 0.84126 | 10.0094 | 11.4343
3622 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904020304 | F10-NJY-MARIMAKALAHALLI | NJY | DLMS Meter | 1.363 | 1.2012 | 0 | 1.363 | 11.8741 | 58.4047
3623 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904020305 | F11-SIR-M.VISHWESHWARAIAH | WATER WORKS | DLMS Meter | 0.78288 | 0.71471 | 0 | 0.78288 | 8.7081 | 8.7081
3624 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904020307 | F12-SRINIVASA SAGARA | NJY | DLMS Meter | 0.62229 | 0.45364 | 0.125 | 0.49729 | 8.7773 | 37.6065
3625 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904020308 | F13-KAMAREDDY HALLY | AGRI | DLMS Meter | 0.5086 | 0.42622 | 0.035 | 0.4736 | 10.0042 | 10.0042
3626 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | MANCHENAHALLI_66 | 1230303904010301 | F14-KLEN PAKS | INDUSTRIAL | DLMS Meter | 2.7132 | 2.7219 | 0 | 2.7132 | -0.3201 | -0.31813
3627 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | MANDIKAL_66 | 1230302902010201 | F03-AVULABETTA | AGRI | DLMS Meter | 0.8967 | 0.80693 | 0 | 0.8967 | 10.0115 | 10.0115
3628 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | MANDIKAL_66 | 1230302902010202 | F04-ADDAGAL | AGRI | DLMS Meter | 0.8822 | 0.79403 | 0 | 0.8822 | 9.9941 | 10.2858
3629 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | MANDIKAL_66 | 1230302902010203 | F05-NAVILUGURKI | NJY | DLMS Meter | 2.2049 | 1.9489 | 0 | 2.2049 | 11.6116 | 27.6342
3630 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | MANDIKAL_66 | 1230302902010204 | F06-PATHURU NJY | NJY | DLMS Meter | 0.3351 | 0.30505 | 0 | 0.3351 | 8.9665 | 72.0752
3631 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | MANDIKAL_66 | 1230302902010205 | F07-KAMMAGUTTAHALLI | AGRI | DLMS Meter | 1.2017 | 1.0573 | 0.027111 | 1.1746 | 9.9891 | 9.9891
3632 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | MANGALWADA_66 | 1320306903010101 | F01-KKHALLY | AGRI | DLMS Meter | 1.7609 | 1.5942 | 0 | 1.7609 | 9.4634 | 10.7382
3633 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | MANGALWADA_66 | 1320306903010102 | F02-ARASIKERE | AGRI | DLMS Meter | 1.779 | 1.6013 | 0 | 1.779 | 9.9889 | 9.9889
3634 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | MANGALWADA_66 | 1320306903010103 | F04-MANGALAWADA | AGRI | DLMS Meter | 1.4559 | 1.3097 | 0 | 1.4559 | 10.039 | 10.039
3635 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | MANGALWADA_66 | 1320306903020301 | F05-MARUR | AGRI | DLMS Meter | 2.2602 | 2.0342 | 0 | 2.2602 | 9.9966 | 10.381
3636 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | MANGALWADA_66 | 1320306903010105 | F06-HANUMASAGARA | AGRI | DLMS Meter | 1.4141 | 1.2772 | 0 | 1.4141 | 9.684 | 11.715
3637 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | MANGALWADA_66 | 1320306903020302 | F07-KILARLAHALLY | AGRI | DLMS Meter | 1.3054 | 1.1844 | 0 | 1.3054 | 9.2667 | 10.819
3638 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | MANGALWADA_66 | 1320306903020303 | F08-KANNAMEDI | AGRI | DLMS Meter | 1.5062 | 1.364 | 0 | 1.5062 | 9.4432 | 10.4178
3639 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | MANGALWADA_66 | 1320306903020304 | F09-NJY C K PURA | NJY | DLMS Meter | 1.0808 | 0.96049 | 0 | 1.0808 | 11.1312 | 75.741
3640 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | MANGALWADA_66 | 1320306903020101 | F10-NJY ARASIKERE | NJY | DLMS Meter | 0.2746 | 0.24826 | 0 | 0.2746 | 9.591 | 60.4396
3641 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | MANGALWADA_66 | 1320306903010106 | F11-NJY-UDDAGATTE | NJY | DLMS Meter | 0.537 | 0.48688 | 0 | 0.537 | 9.3329 | 66.509
3642 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905010101 | F30-L1 BLOCK | COMMERCIAL | DLMS Meter | 0.98904 | 0.989 | 0 | 0.98904 | 0 | 0.0065165
3643 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905010103 | F31-H2 BLOCK | COMMERCIAL | DLMS Meter | 1.234 | 1.1679 | 0 | 1.234 | 5.3543 | 5.3806
3644 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905010102 | F32-G6 BLOCK | COMMERCIAL | DLMS Meter | 0.33347 | 0.3333 | 0 | 0.33347 | 0.050035 | 0.050035
3645 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905010104 | F35-FRONT PARCEL | COMMERCIAL | DLMS Meter | 0.35774 | 0 | 0.35774 | 0 | 0 | #DIV/0!
3646 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905020102 | F37-L2 BLOCK | COMMERCIAL | DLMS Meter | 0.7694 | 0.7701 | 0 | 0.7694 | -0.091609 | -0.091609
3647 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905020103 | F38-G4 BLOCK | COMMERCIAL | DLMS Meter | 0.3524 | 0.35205 | 0 | 0.3524 | 0.098523 | 0.098523
3648 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905020104 | F40-L6 BLOCK | COMMERCIAL | DLMS Meter | 4.5521 | 4.537 | 0 | 4.5521 | 0.33116 | 0.33116
3649 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905020105 | F41-B BLOCK | COMMERCIAL | DLMS Meter | 0.92668 | 0.9124 | 0.0072872 | 0.9194 | 0.7609 | 0.7609
3650 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905020106 | F42-F3 BLOCK | COMMERCIAL | DLMS Meter | 1.2921 | 0.78363 | 0.5082 | 0.78389 | 0.033656 | 0.033656
3651 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905030101 | F43-L3 BLOCK | COMMERCIAL | DLMS Meter | 1.9067 | 1.9066 | 0 | 1.9067 | 0 | 0.001206
3652 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905030104 | F44-N1 BLOCK | COMMERCIAL | DLMS Meter | 0.98907 | 0.9818 | 0 | 0.98907 | 0.73499 | 0.73499
3653 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905030102 | F45-MARUTHI LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.46 | 3.0875 | 0.11755 | 3.3425 | 7.6279 | 14.6321
3654 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905030103 | F46-RACHENAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.3728 | 3.1301 | 0.050965 | 3.3218 | 5.7713 | 23.2317
3655 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905030105 | F48-D4 BLOCK | COMMERCIAL | DLMS Meter | 2.4596 | 1.918 | 0.51687 | 1.9427 | 1.2729 | 1.2729
3656 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905040102 | F50-E1 BLOCK | COMMERCIAL | DLMS Meter | 0.48953 | 0.48702 | 0 | 0.48953 | 0.51339 | 0.51339
3657 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905040101 | F51-G3 BLOCK | COMMERCIAL | DLMS Meter | 0.87575 | 0.87495 | 0 | 0.87575 | 0.091731 | 0.091731
3658 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905040104 | F52-G1 BLOCK | COMMERCIAL | DLMS Meter | 1.9583 | 1.301 | 0.65751 | 1.3008 | -0.012659 | -0.012659
3659 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905040103 | F53-L6 BLOCK | COMMERCIAL | DLMS Meter | 5.7057 | 5.6555 | 3.1243e-05 | 5.7057 | 0.88002 | 0.88002
3660 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905040105 | F54-P3 P4 P5 BLOCK | COMMERCIAL | DLMS Meter | 2.6716 | 2.6666 | 0 | 2.6716 | 0.18539 | 0.18539
3661 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECH_PARK_220 | 1130305905040106 | F55-C2 BLOCK | COMMERCIAL | DLMS Meter | 1.6985 | 1.6954 | 0 | 1.6985 | 0.18106 | 0.18106
3662 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901020101 | F01-FIDELITY | COMMERCIAL | DLMS Meter | 0.19342 | 0 | 0.19342 | 0 | 0 | #DIV/0!
3663 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901020102 | F02-PHILIPS | INDUSTRIAL | DLMS Meter | 4.2602 | 4.1686 | 0 | 4.2602 | 2.1509 | 2.1509
3664 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901020103 | F03-INCUBATOR | COMMERCIAL | DLMS Meter | 0.054607 | 0.0544 | 0.00042205 | 0.054185 | -0.39658 | -0.39658
3665 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901020104 | F04-IBMDBLK | COMMERCIAL | DLMS Meter | 0.82917 | 0 | 0.82917 | 0 | 0 | #DIV/0!
3666 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901020105 | F05-IBM--D-&-D-BLK | COMMERCIAL | DLMS Meter | 1.1341 | 1.127 | 0 | 1.1341 | 0.62245 | 0.62245
3667 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901010103 | F07-STAND BYIDLE | IDLE | DLMS Meter | 4.6994 | 3.835 | 0.61521 | 4.0842 | 6.1016 | 9.9345
3668 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901010301 | F08-IBMDBLK | COMMERCIAL | DLMS Meter | 1.1313 | 1.1282 | 0.0013908 | 1.1299 | 0.14766 | 0.14766
3669 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901010302 | F09-F-BLK | COMMERCIAL | DLMS Meter | 1.2739 | 1.2735 | 0 | 1.2739 | 0.033792 | 0.033792
3670 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901010303 | F10-L-SEIMENS | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3671 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901010304 | F11-MANYATA-MTP-RESIDENCE | URBAN MIXED LOAD | DLMS Meter | 2.7943 | 2.3094 | 0.33949 | 2.4548 | 5.9225 | 12.3658
3672 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901010305 | F12-BTS-LUCENT | COMMERCIAL | DLMS Meter | 5.4368 | 5.1989 | 0 | 5.4368 | 4.3763 | 4.3763
3673 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901010306 | F13-ANZH-BLK | COMMERCIAL | DLMS Meter | 3.1566 | 2.9476 | 0.02288 | 3.1337 | 5.9408 | 13.7401
3674 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901010307 | F14-CBLOCK | COMMERCIAL | DLMS Meter | 1.0687 | 0.72765 | 0.33398 | 0.73477 | 0.96834 | 0.96834
3675 | BMANZ | NORTH | HEBBAL | C4 | MANYATHA_TECHPARK_66 | 1130305901020301 | F15-GODREJ | COMMERCIAL | DLMS Meter | 3.486 | 2.733 | 0.48 | 3.006 | 9.0822 | 15.1998
3676 | BMANZ | NORTH | HEBBAL | C8 | MANYATHA_TECHPARK_66 | 1130305901020108 | F16-,JNC | INDUSTRIAL | DLMS Meter | 2.2921 | 2.1117 | 0 | 2.2921 | 7.8731 | 12.0787
3677 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901020107 | F17-LNOKIA | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3678 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901020109 | F18-G-BLK | COMMERCIAL | DLMS Meter | 0.28386 | 0 | 0.28386 | 0 | 0 | #DIV/0!
3679 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901020310 | F19-MFAR | URBAN MIXED LOAD | DLMS Meter | 4.351 | 4.2994 | 0 | 4.351 | 1.1854 | 1.1854
3680 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901020311 | F20-MADHUVANGRUHANIRMAN | URBAN MIXED LOAD | DLMS Meter | 1.1662 | 1.1584 | 0 | 1.1662 | 0.66933 | 0.73276
3681 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901030501 | F21-H2BLOCK | COMMERCIAL | DLMS Meter | 3.0847 | 0.001746 | 3.0828 | 0.001911 | 8.6365 | 8.6365
3682 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901030502 | F22-N1BLOCK | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3683 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901030503 | F23-F3BLOCK | COMMERCIAL | DLMS Meter | 0.16557 | 0 | 0.16557 | 0 | 0 | #DIV/0!
3684 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901030504 | F24-G2BLOCK | COMMERCIAL | DLMS Meter | 2.187 | 2.1869 | 0 | 2.187 | 0 | 0.00015116
3685 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901030505 | F25-ANZ H BLOCK | COMMERCIAL | DLMS Meter | 2.3647 | 2.3666 | 0 | 2.3647 | -0.083007 | -0.075752
3686 | BMANZ | EAST | SHIVAJINAGAR | E9 | MANYATHA_TECHPARK_66 | 1130305901030506 | F26-BTS LUCENT | COMMERCIAL | DLMS Meter | 5.7122 | 5.71 | 0 | 5.7122 | 0.038405 | 0.038405
3687 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903020101 | F01-THATTEKERE--F | AGRI | DLMS Meter | 1.1158 | 1.0043 | 0 | 1.1158 | 9.9933 | 9.9933
3688 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903010102 | F02-MARALAWADI-F | URBAN MIXED LOAD | DLMS Meter | 0.60852 | 0.51407 | 0.04 | 0.56852 | 9.5777 | 31.9972
3689 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903010103 | F03-THERUBEEDI-F | AGRI | DLMS Meter | 1.0638 | 0.95774 | 0 | 1.0638 | 9.9697 | 9.9697
3690 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903010101 | F04-SIDIDEVARAHALLI | AGRI | DLMS Meter | 0.56508 | 0.50872 | 0 | 0.56508 | 9.974 | 9.974
3691 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903010301 | F05-YALACHAVADI-NJY--F | NJY | DLMS Meter | 0.43846 | 0.27827 | 0.1303 | 0.30816 | 9.7009 | 60.7273
3692 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903010302 | F06-GANDHI-FARM | AGRI | DLMS Meter | 0.92188 | 0.78472 | 0.05 | 0.87188 | 9.9967 | 9.9967
3693 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903010303 | F07-MARIGOWDANA-DODDI | AGRI | DLMS Meter | 1.0004 | 0.87753 | 0.025 | 0.97536 | 10.03 | 10.03
3694 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903020301 | F08-THOKASANDRA-F | AGRI | DLMS Meter | 1.4531 | 1.0971 | 0.234 | 1.2191 | 10.0064 | 10.0064
3695 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903010304 | F09-BANAVASI-NJY--F | NJY | DLMS Meter | 0.67076 | 0.48866 | 0.1298 | 0.54096 | 9.6684 | 55.7038
3696 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903020306 | F10-AGARA NJY | NJY | DLMS Meter | 0.48578 | 0.34863 | 0.101 | 0.38478 | 9.3943 | 59.6247
3697 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903020307 | F11-SADENAHALLI NJY | NJY | DLMS Meter | 0.3756 | 0.27398 | 0.0725 | 0.3031 | 9.6087 | 49.0074
3698 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903020308 | F12-DUNNASANDRA NJY | NJY | DLMS Meter | 0.4917 | 0.26728 | 0.2031 | 0.2886 | 7.3883 | 44.2189
3699 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903010104 | F14-KALLANAKUPPE | AGRI | DLMS Meter | 0.97906 | 0.88115 | 0 | 0.97906 | 10.0003 | 10.0003
3700 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | MARALAWADI_66 | 1220304903010105 | F15-ANEHOSAHALLI | AGRI | DLMS Meter | 0.2649 | 0.23824 | 0 | 0.2649 | 10.0634 | 10.0634
3701 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905010101 | F01-TORALAKKI | AGRI | DLMS Meter | 1.3741 | 1.2364 | 0 | 1.3741 | 10.0197 | 10.0197
3702 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905010102 | F02-THURANASI | AGRI | DLMS Meter | 1.6801 | 1.3769 | 0.15 | 1.5301 | 10.0149 | 10.0284
3703 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905010103 | F03-D-N-DODDI | AGRI | DLMS Meter | 3.8991 | 1.6371 | 2.08 | 1.8191 | 10.0016 | 10.0016
3704 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905010104 | F04-DINAHALLI | AGRI | DLMS Meter | 1.4368 | 1.2929 | 0 | 1.4368 | 10.0113 | 34.2201
3705 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905020301 | F05-KESARAGERE | AGRI | DLMS Meter | 2.0145 | 1.6957 | 0.13 | 1.8845 | 10.0192 | 10.9008
3706 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905020302 | F06-CHIKKAIGGALUR | AGRI | DLMS Meter | 1.4102 | 1.2693 | 0 | 1.4102 | 9.994 | 9.994
3707 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905020303 | F07-RAJENAHALLI | AGRI | DLMS Meter | 2.3647 | 1.9479 | 0.2 | 2.1647 | 10.0159 | 10.17
3708 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905020304 | F08-MASTI-VENKATESH-IYENGAR | NJY | DLMS Meter | 3.6556 | 1.4433 | 2.05 | 1.6056 | 10.1069 | 88.9573
3709 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905020305 | F09-ANIKARA-HALLI | NJY | DLMS Meter | 2.4693 | 2.2614 | 0 | 2.4693 | 8.4196 | 90.6018
3710 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905020306 | F10-ASANDAHALLI | NJY | DLMS Meter | 1.9593 | 1.7827 | 0 | 1.9593 | 9.0098 | 92.4779
3711 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905020307 | F11-DODDAKALA-HALLI | NJY | DLMS Meter | 2.939 | 2.6601 | 0 | 2.939 | 9.4914 | 88.7833
3712 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905010105 | F12-BANTEHALLI | AGRI | DLMS Meter | 1.888 | 1.4922 | 0.23 | 1.658 | 10.0003 | 10.0003
3713 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905010201 | F13-MASTHI TOWN | DOMESTIC | DLMS Meter | 1.75 | 1.5669 | 0 | 1.75 | 10.4653 | 50.5575
3714 | BRAZ | KOLAR | KGF | MALUR | MASTI_66 | 1230204905010202 | F14-ALAHALLI | AGRI | DLMS Meter | 0.59326 | 0.53383 | 0 | 0.59326 | 10.0172 | 10.0172
3715 | BMANZ | NORTH | MALLESHWARA | C6 | MATHIKERE_66 | 1120204901010101 | F02-LG-HALLI | URBAN MIXED LOAD | DLMS Meter | 2.0204 | 1.8838 | 0 | 2.0204 | 6.7642 | 19.1532
3716 | BMANZ | NORTH | MALLESHWARA | C6 | MATHIKERE_66 | 1120204901010104 | F05-PAMPA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.5912 | 3.0849 | 0.187 | 3.4042 | 9.3787 | 19.7726
3717 | BMANZ | NORTH | MALLESHWARA | C6 | MATHIKERE_66 | 1120204901020302 | F06-FYESHWANTPUR-ST-MAIN | URBAN MIXED LOAD | DLMS Meter | 3.09 | 2.9248 | 0 | 3.09 | 5.3451 | 16.1518
3718 | BMANZ | NORTH | MALLESHWARA | C6 | MATHIKERE_66 | 1120204901020101 | F07-FSBM-COLONY | URBAN MIXED LOAD | DLMS Meter | 3.6849 | 3.3783 | 0 | 3.6849 | 8.3202 | 15.8423
3719 | BMANZ | NORTH | JALAHALLI | C3 | MATHIKERE_66 | 1120204901020301 | F08-BANDAPPA-GARDEN | DOMESTIC | DLMS Meter | 2.5042 | 2.313 | 0.035 | 2.4692 | 6.3275 | 13.0527
3720 | BMANZ | NORTH | MALLESHWARA | C6 | MATHIKERE_66 | 1120204901020303 | F09-V-R-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.6081 | 2.3185 | 0.0668 | 2.5413 | 8.764 | 18.11
3721 | BMANZ | NORTH | JALAHALLI | C3 | MATHIKERE_66 | 1120204901020304 | F10-SUNDAR-NAGAR | URBAN MIXED LOAD | DLMS Meter | 1.3437 | 1.2703 | 0.035 | 1.3087 | 2.9298 | 5.4382
3722 | BMANZ | NORTH | JALAHALLI | C3 | MATHIKERE_66 | 1120204901020102 | F11-SRIRAMASADAN | DOMESTIC | DLMS Meter | 0.57472 | 0.54758 | 0 | 0.57472 | 4.723 | 4.723
3723 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MATHIKERE_YELIGEHALLI_66 | 1210102905010203 | F02-Y G GUDDA WSL | WATER WORKS | DLMS Meter | 0.2519 | 0.018474 | 0.2312 | 0.0207 | 10.7536 | 80.3502
3724 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MATHIKERE_YELIGEHALLI_66 | 1210102905010202 | F03-GEJJAGARAGUPPE NJY | NJY | DLMS Meter | 0.6624 | 0.52839 | 0.077 | 0.5854 | 9.7379 | 32.276
3725 | BRAZ | RAMANAGAR | MAGADI | MAGADI | MATHIKERE_YELIGEHALLI_66 | 1210102905010201 | F04-YELIGEHALLY | AGRI | DLMS Meter | 0.7591 | 0.68301 | 0 | 0.7591 | 10.024 | 10.024
3726 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | MATHOD_66 | 1310204904010101 | F01-G.NKERE | AGRI | DLMS Meter | 0.86244 | 0.77631 | 0 | 0.86244 | 9.9871 | 9.9871
3727 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | MATHOD_66 | 1310204904010102 | F02-BUKKASAGARA | AGRI | DLMS Meter | 1.4266 | 1.2834 | 0 | 1.4266 | 10.039 | 10.039
3728 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | MATHOD_66 | 1310204904020301 | F05-MATHODU | AGRI | DLMS Meter | 1.0228 | 0.92014 | 0 | 1.0228 | 10.0332 | 10.0332
3729 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | MATHOD_66 | 1310204904020302 | F07-NAGATHIHALLI | AGRI | DLMS Meter | 0.78118 | 0.70299 | 0 | 0.78118 | 10.0096 | 10.0096
3730 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | MATHOD_66 | 1310204904010108 | F08-MENASINODU | AGRI | DLMS Meter | 1.5492 | 1.3937 | 0 | 1.5492 | 10.0401 | 10.0401
3731 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | MATHOD_66 | 1310204904020303 | F09-MTDNJY | NJY | DLMS Meter | 0.59874 | 0.51474 | 0.000942 | 0.5978 | 13.8936 | 41.1573
3732 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | MATHOD_66 | 1310204904010103 | F10-D.T.VATTI | NJY | DLMS Meter | 0.48722 | 0.42666 | 0 | 0.48722 | 12.4299 | 49.46
3733 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | MATHOD_66 | 1310204904010109 | F11-VAJRA NJY | NJY | DLMS Meter | 0.4312 | 0.37105 | 0 | 0.4312 | 13.9493 | 51.5815
3734 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | MAVINAKATTE_66 | 1310106906010101 | F01-MAVINKATTENJY | NJY | DLMS Meter | 0.96082 | 0.48213 | 0.428 | 0.53282 | 9.5137 | 49.0902
3735 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | MAVINAKATTE_66 | 1310106906010102 | F02-DONDRAGATTA | AGRI | DLMS Meter | 1.3467 | 1.0662 | 0.159 | 1.1877 | 10.2333 | 10.2333
3736 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | MAVINAKATTE_66 | 1310106906010103 | F03-HOSUR | AGRI | DLMS Meter | 1.8655 | 1.6825 | 0 | 1.8655 | 9.811 | 9.811
3737 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | MAVINAKATTE_66 | 1310106906010104 | F04-MADENAHALLI | AGRI | DLMS Meter | 0.768 | 0.54736 | 0.15942 | 0.60858 | 10.0588 | 10.0588
3738 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | MAVINAKATTE_66 | 1310106906020301 | F05-HANCHINASIDDAPURA | AGRI | DLMS Meter | 0.87082 | 0.051115 | 0.81367 | 0.05715 | 10.5599 | 10.5599
3739 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | MAVINAKATTE_66 | 1310106906020302 | F06-GURURAJPURANJY | NJY | DLMS Meter | 0.21012 | 0.10944 | 0.09 | 0.12012 | 8.8928 | 64.3753
3740 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | MAVINAKATTE_66 | 1310106906020303 | F07-BRT | AGRI | DLMS Meter | 1.4878 | 1.0303 | 0.342 | 1.1458 | 10.0832 | 10.0832
3741 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | MAVINAKATTE_66 | 1310106906020304 | F08-MAVINAKATTE | AGRI | DLMS Meter | 1.2271 | 1.0132 | 0.098 | 1.1291 | 10.2709 | 10.2709
3742 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | MAVINAKATTE_66 | #N/A | F09-MRUJARA_IPP | #N/A | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3743 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | MAVINAKATTE_66 | 1310106906010106 | F10-BASAVAPURA WATER SUPPLY | WATER WORKS | DLMS Meter | 0.073521 | 0.065648 | 0.005 | 0.068521 | 4.1933 | 97.9519
3744 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904010101 | F01-B DURGA | AGRI | DLMS Meter | 1.1635 | 1.0467 | 0 | 1.1635 | 10.0346 | 10.0346
3745 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904010102 | F02-DINDADAHALLI | AGRI | DLMS Meter | 1.0857 | 0.97736 | 0 | 1.0857 | 9.977 | 9.977
3746 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904010103 | F03-NARAGANAHALLI | AGRI | DLMS Meter | 1.2189 | 1.097 | 0 | 1.2189 | 10.0026 | 10.0026
3747 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904010104 | F04-MAYAKONDA NJY | NJY | DLMS Meter | 0.58548 | 0.38025 | 0.165 | 0.42048 | 9.5675 | 23.4325
3748 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904010107 | F05-BULLAPURA | AGRI | DLMS Meter | 0.86026 | 0.77434 | 0 | 0.86026 | 9.9881 | 9.9881
3749 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904020301 | F06-KODAGANUR | AGRI | DLMS Meter | 0.76178 | 0.68537 | 0 | 0.76178 | 10.0299 | 10.0299
3750 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904020302 | F07-BADAMYK | AGRI | DLMS Meter | 1.6607 | 1.4942 | 0 | 1.6607 | 10.0241 | 10.0241
3751 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904020303 | F08-NALKUNDA | AGRI | DLMS Meter | 2.1269 | 1.8765 | 0 | 2.1269 | 11.7716 | 11.7716
3752 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904010106 | F09-H BASAVAPURA | AGRI | DLMS Meter | 0.95077 | 0.85574 | 0 | 0.95077 | 9.9948 | 9.9948
3753 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904010105 | F10-WATERWORKS | WATER WORKS | DLMS Meter | 1.2335 | 0.5807 | 0.565 | 0.66846 | 13.1288 | 47.7462
3754 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904010109 | F11-BOMMENAHALLI NJY | NJY | DLMS Meter | 1.1064 | 0.52531 | 0.505 | 0.60143 | 12.6573 | 22.5164
3755 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904010108 | F12-BAVIHAL NJY | NJY | DLMS Meter | 0.1545 | 0.13977 | 0 | 0.1545 | 9.5333 | 29.7161
3756 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MAYAKONDA_66 | 1310104904020304 | F13-ANABERU | AGRI | DLMS Meter | 0.2506 | 0.22555 | 0 | 0.2506 | 9.9956 | 9.9956
3757 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010101 | F01-BYTHARAHOSAHALLI | AGRI | DLMS Meter | 0.98538 | 0.88666 | 0 | 0.98538 | 10.0187 | 10.0187
3758 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010102 | F02-MAYASANDRA | AGRI | DLMS Meter | 0.71554 | 0.64389 | 0 | 0.71554 | 10.0134 | 10.0134
3759 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010103 | F03-MUTUGADAHALLI | AGRI | DLMS Meter | 0.40016 | 0.35998 | 0 | 0.40016 | 10.0415 | 10.0415
3760 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010104 | F04-HEDDANAKATTE | AGRI | DLMS Meter | 0.8376 | 0.75387 | 0 | 0.8376 | 9.9968 | 9.9968
3761 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010105 | F05-VADAVANGHATTA | AGRI | DLMS Meter | 0.78526 | 0.70644 | 0 | 0.78526 | 10.0377 | 10.0377
3762 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901020301 | F06-BOMMENAHALLI | AGRI | DLMS Meter | 1.0981 | 0.9882 | 0 | 1.0981 | 10.0048 | 10.0048
3763 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901020302 | F07-MALLIGERE | AGRI | DLMS Meter | 0.6262 | 0.56365 | 0 | 0.6262 | 9.9885 | 9.9885
3764 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901020303 | F08-ANADAGU | AGRI | DLMS Meter | 0.5525 | 0.49726 | 0 | 0.5525 | 9.9989 | 9.9989
3765 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901020304 | F09-MANICHANDUR | AGRI | DLMS Meter | 1.5225 | 1.3701 | 0 | 1.5225 | 10.0062 | 10.0062
3766 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901020305 | F10-ITTIGEHALLI NJY | NJY | DLMS Meter | 1.0199 | 0.49175 | 0.47 | 0.54986 | 10.5673 | 53.1262
3767 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901020306 | F11-YARADAHALLI | AGRI | DLMS Meter | 1.8969 | 1.7146 | 0 | 1.8969 | 9.6095 | 9.6095
3768 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010501 | F13-TUMBEPURA | AGRI | DLMS Meter | 1.7783 | 1.6001 | 0 | 1.7783 | 10.0219 | 10.0219
3769 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010502 | F14-SEEGEHALLI | AGRI | DLMS Meter | 1.6302 | 1.4668 | 0 | 1.6302 | 10.0218 | 10.0218
3770 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010503 | F15-MALLENAHALLI | AGRI | DLMS Meter | 1.2357 | 1.1118 | 0 | 1.2357 | 10.0281 | 10.0281
3771 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901020502 | F16-NANDHI | AGRI | DLMS Meter | 1.2644 | 0.79566 | 0.38 | 0.88438 | 10.0314 | 10.0314
3772 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010106 | F17-CHIKKAPURA NJY | NJY | DLMS Meter | 0.4038 | 0.35998 | 0 | 0.4038 | 10.8522 | 40.2637
3773 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901020501 | F18-THUBINAKATTE NJY | NJY | DLMS Meter | 0.4706 | 0.37096 | 0.038 | 0.4326 | 14.2492 | 45.7849
3774 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010301 | F19 -JADEYA NJY | NJY | DLMS Meter | 0.3542 | 0.28991 | 0.025 | 0.3292 | 11.9352 | 58.6899
3775 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010302 | F20-CHIKKASHETTIKERE NJY | NJY | DLMS Meter | 0.6852 | 0.6193 | 0 | 0.6852 | 9.6175 | 41.2928
3776 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | MAYASANDRA_110 | 1320202901010107 | F21-KANAKURU | AGRI | DLMS Meter | 0.32 | 0.28796 | 0 | 0.32 | 10.0131 | 10.0131
3777 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MEDIGESHI_66 | 1320301903010101 | F01-CHANDRABAVI | AGRI | DLMS Meter | 1.6084 | 1.4476 | 0 | 1.6084 | 9.9987 | 10.3583
3778 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MEDIGESHI_66 | 1320301903010102 | F02-REDDYHALLY | AGRI | DLMS Meter | 1.6595 | 1.5445 | 0 | 1.6595 | 6.931 | 6.931
3779 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MEDIGESHI_66 | 1320301903010103 | F03-MIDAGESHI | DOMESTIC | DLMS Meter | 0.85902 | 0.13033 | 0.716 | 0.14302 | 8.8708 | 15.066
3780 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MEDIGESHI_66 | 1320301903010104 | F04-MALLANAYAKANAHALLY | AGRI | DLMS Meter | 1.1368 | 1.0231 | 0 | 1.1368 | 10.0022 | 10.0022
3781 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MEDIGESHI_66 | 1320301903010105 | F05-HANUMANTHAPURA-NJY | NJY | DLMS Meter | 1.092 | 0.99855 | 0 | 1.092 | 8.5589 | 48.1711
3782 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | MEDIGESHI_66 | 1320301903010106 | F06-LAKSHMIPURA--NJY | NJY | DLMS Meter | 0.41434 | 0.36966 | 0 | 0.41434 | 10.7846 | 61.4685
3783 | BMANZ | NORTH | PEENYA | N5 | MEILAYOUT_66 | 1120102903010101 | F01 AGBG-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.9652 | 1.8368 | 0 | 1.9652 | 6.5351 | 19.9132
3784 | BMANZ | NORTH | PEENYA | N5 | MEILAYOUT_66 | 1120102903010102 | F02-MALLASANDRA PIPELINE | URBAN MIXED LOAD | DLMS Meter | 3.2358 | 2.7905 | 0.186 | 3.0498 | 8.5033 | 28.7974
3785 | BMANZ | NORTH | PEENYA | N5 | MEILAYOUT_66 | 1120102903010103 | F03-CHIKKASANDRA | URBAN MIXED LOAD | DLMS Meter | 2.521 | 2.1473 | 0.21 | 2.311 | 7.086 | 22.5313
3786 | BMANZ | NORTH | JALAHALLI | N9 | MEILAYOUT_66 | 1120102903010105 | F05-BAGALAGUNTE | URBAN MIXED LOAD | DLMS Meter | 1.2349 | 1.1515 | 0 | 1.2349 | 6.7596 | 17.8341
3787 | BMANZ | NORTH | PEENYA | N5 | MEILAYOUT_66 | 1120102903010106 | F06-KEMPEGOWDA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.6771 | 2.3744 | 0.115 | 2.5621 | 7.3255 | 18.742
3788 | BMANZ | NORTH | PEENYA | N5 | MEILAYOUT_66 | 1120102903020301 | F07-ACHARYA-COLLEGE-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.9504 | 3.3092 | 0.3615 | 3.5889 | 7.7942 | 25.25
3789 | BMANZ | NORTH | JALAHALLI | N9 | MEILAYOUT_66 | 1120102903020302 | F08-MEI LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.3719 | 2.2198 | 0 | 2.3719 | 6.4142 | 17.2774
3790 | BMANZ | NORTH | PEENYA | N5 | MEILAYOUT_66 | 1120102903020303 | F09-MARIGOLD PROPERTIES | DOMESTIC | DLMS Meter | 0.18969 | 0.18927 | 0 | 0.18969 | 0.21941 | 0.21941
3791 | BMANZ | NORTH | JALAHALLI | N9 | MEILAYOUT_66 | 1120102903020304 | F10-GARRISON ENGINEERING | DEFENSE ESTABLISHMENT | DLMS Meter | 0.75214 | 0.69135 | 0.039 | 0.71314 | 3.0559 | 5.7362
3792 | BMANZ | NORTH | JALAHALLI | N9 | MEILAYOUT_66 | 1120102903020305 | F11-SIDEDAHALLY MAIN ROAD | URBAN MIXED LOAD | DLMS Meter | 2.4245 | 2.1873 | 0.05 | 2.3745 | 7.884 | 22.622
3793 | BMANZ | NORTH | JALAHALLI | N9 | MEILAYOUT_66 | 1120102903010301 | F13-R R LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0.82393 | 0.76166 | 0.028036 | 0.7959 | 6.0743 | 15.7093
3794 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901010101 | F01-SHANTINAGAR | URBAN MIXED LOAD | DLMS Meter | 4.7916 | 4.5287 | 0 | 4.7916 | 5.4868 | 25.5715
3795 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901010102 | F02-DEVANUR | URBAN MIXED LOAD | DLMS Meter | 3.616 | 3.3448 | 0 | 3.616 | 7.4978 | 27.156
3796 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901010103 | F04-A-K-KAVAL | AGRI | DLMS Meter | 1.167 | 1.0503 | 0 | 1.167 | 10.0015 | 10.0015
3797 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901010104 | F05-MELEKOTE(A) | AGRI | DLMS Meter | 1.4628 | 1.2916 | 0 | 1.4628 | 11.7086 | 11.7086
3798 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901010105 | F06-BANAVARA | AGRI | DLMS Meter | 1.1388 | 1.0531 | 0 | 1.1388 | 7.5319 | 7.5319
3799 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901020301 | F07-HALANOORU | AGRI | DLMS Meter | 1.7065 | 1.51 | 0 | 1.7065 | 11.5134 | 11.5134
3800 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901020302 | F08-KUMKUMANAHALLI | AGRI | DLMS Meter | 1.1242 | 1.0118 | 0 | 1.1242 | 10.0035 | 10.0035
3801 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901020303 | F09-GULUR | AGRI | DLMS Meter | 1.703 | 1.51 | 0 | 1.703 | 11.3308 | 11.3308
3802 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | MELKOTE_66 | 1320102901020304 | F10-GVR | URBAN MIXED LOAD | DLMS Meter | 3.7646 | 3.3208 | 0.3459 | 3.4187 | 2.8626 | 2.8626
3803 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | MELKOTE_66 | 1320102901020305 | F11-GANDINAGRA | URBAN MIXED LOAD | DLMS Meter | 2.8652 | 2.4797 | 0.28578 | 2.5795 | 3.867 | 3.867
3804 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901020101 | F12-VEERASAGARA | RURAL MIXED LOAD | DLMS Meter | 2.97 | 2.2346 | 0.60717 | 2.3629 | 5.4296 | 29.3825
3805 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901010107 | F13-CNNL | LIFT IRRIGATION | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
3806 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | MELKOTE_66 | 1320102901010106 | F14-KAIDALA NJY | NJY | DLMS Meter | 1.1269 | 0.88804 | 0.1085 | 1.0184 | 12.7971 | 39.9577
3807 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | MELLAHALLI_66 | 1220103904010101 | F02-HARISANDRA | AGRI | DLMS Meter | 0.54208 | 0.48794 | 0 | 0.54208 | 9.9875 | 9.9875
3808 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | MELLAHALLI_66 | 1220103904010102 | F03-THIMMASANDRA | AGRI | DLMS Meter | 0.29002 | 0.26103 | 0 | 0.29002 | 9.9945 | 9.9945
3809 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | MELLAHALLI_66 | 1220103904010103 | F04-ANKANAHALLI | AGRI | DLMS Meter | 0.68288 | 0.52216 | 0.1028 | 0.58008 | 9.985 | 9.985
3810 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | MELLAHALLI_66 | 1220103904010104 | F05-PADARAHALLI | AGRI | DLMS Meter | 0.48704 | 0.40659 | 0.0351 | 0.45194 | 10.0345 | 10.0345
3811 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | MELLAHALLI_66 | 1220103904020301 | F06-RAMPURA | AGRI | DLMS Meter | 0.8142 | 0.73254 | 0 | 0.8142 | 10.0291 | 10.0291
3812 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | MELLAHALLI_66 | 1220103904020302 | F07-LAKSHMIPURA | AGRI | DLMS Meter | 0.70361 | 0.63277 | 0 | 0.70361 | 10.0684 | 10.0684
3813 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | MELLAHALLI_66 | 1220103904020303 | F08-SUGUNAHALLI | AGRI | DLMS Meter | 0.81278 | 0.73161 | 0 | 0.81278 | 9.9862 | 9.9862
3814 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | MELLAHALLI_66 | 1220103904020305 | F09-GUNGARAHALLI | NJY | DLMS Meter | 0.6575 | 0.45008 | 0.16115 | 0.49635 | 9.3231 | 44.4754
3815 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | MELLAHALLI_66 | 1220103904010107 | F10-MADARASABARADODDI NJY | NJY | DLMS Meter | 0.7155 | 0.56463 | 0.0931 | 0.6224 | 9.2823 | 47.0304
3816 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | MELLAHALLI_66 | 1220103904010105 | F11-LAKKASANDRA | NJY | DLMS Meter | 0.4742 | 0.38619 | 0.0473 | 0.4269 | 9.5365 | 42.52
3817 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MELLEKATTE_66 | 1310104903010101 | F01-HULIKATTE | AGRI | DLMS Meter | 1.0473 | 0.94249 | 0 | 1.0473 | 10.0107 | 10.0107
3818 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MELLEKATTE_66 | 1310104903010102 | F02-SAIBABA | AGRI | DLMS Meter | 1.6099 | 1.3452 | 0.096 | 1.5139 | 11.1448 | 11.1448
3819 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MELLEKATTE_66 | 1310104903010103 | F03-SIDDANUR | AGRI | DLMS Meter | 1.3346 | 1.201 | 0 | 1.3346 | 10.0121 | 10.0121
3820 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MELLEKATTE_66 | 1310104903020301 | F04-GUDAL | AGRI | DLMS Meter | 1.5597 | 1.4034 | 0 | 1.5597 | 10.0178 | 10.0178
3821 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MELLEKATTE_66 | 1310104903020302 | F05-ANAJI | AGRI | DLMS Meter | 1.4707 | 1.324 | 0 | 1.4707 | 9.9771 | 9.9771
3822 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MELLEKATTE_66 | 1310104903020303 | F06-KITTUR | AGRI | DLMS Meter | 1.5998 | 1.4393 | 0 | 1.5998 | 10.0366 | 10.0366
3823 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MELLEKATTE_66 | 1310104903020304 | F07-KANDANAKOVINJY | NJY | DLMS Meter | 1.3159 | 0.55675 | 0.675 | 0.64093 | 13.1346 | 24.0824
3824 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MELLEKATTE_66 | 1310104903020305 | F08-MELLAKATTENJY | NJY | DLMS Meter | 1.0493 | 0.575 | 0.389 | 0.66029 | 12.9174 | 21.4732
3825 | CTAZ | DAVANAGERE | DAVANAGERE | ANAGODU | MELLEKATTE_66 | 1310104903010104 | F09-MALLAPURA NJY | NJY | DLMS Meter | 1.1747 | 1.0205 | 0.056 | 1.1187 | 8.7803 | 13.5229
3826 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | MELUR_66 | 1230404903010101 | F01-TELEPHONE-EXCHANGE | NJY | DLMS Meter | 0.5668 | 0.49468 | 0.00134 | 0.56546 | 12.5164 | 53.462
3827 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | MELUR_66 | 1230404903020301 | F02-MELUR | AGRI | DLMS Meter | 1.1921 | 0.85313 | 0.24421 | 0.94793 | 10.0008 | 10.0008
3828 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | MELUR_66 | 1230404903020302 | F03-KAMBADAHALLI | AGRI | DLMS Meter | 1.0335 | 0.92823 | 0.002393 | 1.0311 | 9.9812 | 9.9812
3829 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | MELUR_66 | 1230404903020303 | F04-BHAKTARAHALLI | AGRI | DLMS Meter | 0.78666 | 0.7065 | 0.001758 | 0.7849 | 9.9888 | 9.9888
3830 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | MELUR_66 | 1230404903020304 | F05-NJY | NJY | DLMS Meter | 1.3917 | 1.2107 | 0.00329 | 1.3884 | 12.7953 | 77.3886
3831 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | MELUR_66 | 1230404903010104 | F06-KESHAVARA | AGRI | DLMS Meter | 1.2673 | 1.0986 | 0.008005 | 1.2593 | 12.7583 | 12.7583
3832 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | MGHALLI_66 | 1230402904020302 | F01-YENAMALAPADI | AGRI | DLMS Meter | 1.2461 | 1.1214 | 0 | 1.2461 | 10.0035 | 10.0035
3833 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | MGHALLI_66 | 1230402904020303 | F02-MUNGANAHALLI | AGRI | DLMS Meter | 0.89022 | 0.80104 | 0 | 0.89022 | 10.0182 | 10.0182
3834 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | MGHALLI_66 | 1230402904020301 | F03-M.GOLLAHALLI | AGRI | DLMS Meter | 0.9325 | 0.83915 | 0 | 0.9325 | 10.0104 | 10.0104
3835 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | MGHALLI_66 | 1230402904010102 | F04-YARAYAGARAHALLI | AGRI | DLMS Meter | 1.1847 | 1.0663 | 0 | 1.1847 | 9.9965 | 9.9965
3836 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | MGHALLI_66 | 1230402904010104 | F05-PEDDUR | AGRI | DLMS Meter | 1.0771 | 0.96928 | 0 | 1.0771 | 10.0139 | 10.0139
3837 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | MGHALLI_66 | 1230402904010101 | F06-HOSAHUDYA | AGRI | DLMS Meter | 1.077 | 0.96915 | 0 | 1.077 | 10.017 | 10.017
3838 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | MGHALLI_66 | 1230402904010103 | F07-YEGAVAKOTE-NJY | NJY | DLMS Meter | 1.6903 | 1.3405 | 0.13072 | 1.5596 | 14.0448 | 62.0878
3839 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | MITTEMARI_220 | 1230305908010101 | F01-MERUVAPALLI | AGRI | DLMS Meter | 0.42 | 0.37627 | 0 | 0.42 | 10.4129 | 10.4129
3840 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | MITTEMARI_220 | 1230305908010102 | F02-CHINNAMPALLI | AGRI | DLMS Meter | 0.8452 | 0.6839 | 0.085 | 0.7602 | 10.0366 | 10.0366
3841 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | MITTEMARI_220 | 1230305908010103 | F03-SINGANAKUDHURE | AGRI | DLMS Meter | 1.1128 | 1.0014 | 0 | 1.1128 | 10.0072 | 10.0072
3842 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | MITTEMARI_220 | 1230305908010104 | F04-GARUDADHRI | NJY | DLMS Meter | 1.1208 | 0.9818 | 0.02 | 1.1008 | 10.8099 | 78.365
3843 | BRAZ | KOLAR | KGF | MULABAGILU | MUDIYANUR_66 | 1230202905010104 | F02-MANJALANAGAR | AGRI | DLMS Meter | 0.87782 | 0.78994 | 0 | 0.87782 | 10.0108 | 10.0108
3844 | BRAZ | KOLAR | KGF | MULABAGILU | MUDIYANUR_66 | 1230202905010105 | F03-BANDARAHALLI NJY | NJY | DLMS Meter | 1.4158 | 1.2799 | 0 | 1.4158 | 9.5993 | 77.3659
3845 | BRAZ | KOLAR | KGF | MULABAGILU | MUDIYANUR_66 | 1230202905010102 | F04-HANUMANAHALLI | AGRI | DLMS Meter | 1.089 | 0.98005 | 0 | 1.089 | 10.0032 | 10.0032
3846 | BRAZ | KOLAR | KGF | MULABAGILU | MUDIYANUR_66 | 1230202905020304 | F06-POMBARAHALLI | NJY | DLMS Meter | 0.66448 | 0.60083 | 0 | 0.66448 | 9.5785 | 69.4338
3847 | BRAZ | KOLAR | KGF | MULABAGILU | MUDIYANUR_66 | 1230202905010101 | F07-MUDIYANUR | AGRI | DLMS Meter | 0.47428 | 0.42684 | 0 | 0.47428 | 10.0017 | 11.0003
3848 | BRAZ | KOLAR | KGF | MULABAGILU | MUDIYANUR_66 | 1230202905020301 | F08-UTHANUR | AGRI | DLMS Meter | 0.97758 | 0.88008 | 0 | 0.97758 | 9.9737 | 9.9737
3849 | BRAZ | KOLAR | KGF | MULABAGILU | MUDIYANUR_66 | 1230202905020302 | F09-KURADAMALE | AGRI | DLMS Meter | 1.15 | 1.0352 | 0 | 1.15 | 9.9893 | 9.9893
3850 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906010101 | F01-KHB-COLONY | RURAL MIXED LOAD | DLMS Meter | 1.361 | 1.2299 | 0 | 1.361 | 9.6371 | 38.0823
3851 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906010103 | F03-KAVATHANAHALLI | AGRI | DLMS Meter | 1.0369 | 0.93299 | 0 | 1.0369 | 10.0179 | 10.1646
3852 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906010104 | F04-SRIRANGAPURA | AGRI | DLMS Meter | 0.17716 | 0.15944 | 0 | 0.17716 | 10.0021 | 10.0021
3853 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906020301 | F05-ALANGOOR | AGRI | DLMS Meter | 16.0016 | 1.5625 | 14.2652 | 1.7364 | 10.0168 | 10.0168
3854 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906010105 | F06-CHANNAPURA | NJY | DLMS Meter | 1.986 | 1.7939 | 0 | 1.986 | 9.6755 | 77.0086
3855 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906020303 | F08-BALLA | AGRI | DLMS Meter | 1.1479 | 1.033 | 0 | 1.1479 | 10.0063 | 10.0063
3856 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906020304 | F09-ANGONDAHALLI | AGRI | DLMS Meter | 1.2705 | 1.1434 | 0 | 1.2705 | 10.0013 | 12.1959
3857 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906020305 | F10-MARANDAHALLI | AGRI | DLMS Meter | 2.2571 | 2.0317 | 0 | 2.2571 | 9.9875 | 25.012
3858 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906010106 | F12-MALLANAYAKANAHALLI | AGRI | DLMS Meter | 0.92912 | 0.83625 | 0 | 0.92912 | 9.9949 | 10.9398
3859 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906010107 | F13-NAGAMANGALA | AGRI | DLMS Meter | 1.2227 | 1.1007 | 0 | 1.2227 | 9.9832 | 9.9832
3860 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906020503 | F14-CHAMAREDDYHALLI NJY | NJY | DLMS Meter | 0.911 | 0.82166 | 0 | 0.911 | 9.8064 | 73.3354
3861 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906020504 | F16-SEEGENAHALLI | AGRI | DLMS Meter | 0.12198 | 0.1098 | 0 | 0.12198 | 9.9879 | 9.9879
3862 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906020501 | F17-DOMMASANDRA | NJY | DLMS Meter | 2.1127 | 1.0682 | 0.931 | 1.1817 | 9.5998 | 72.6067
3863 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901010101 | F01-OBALAPURA | AGRI | DLMS Meter | 1.8198 | 1.6288 | 0 | 1.8198 | 10.4985 | 10.4985
3864 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901010102 | F02-BHOGANAHALLI | AGRI | DLMS Meter | 0.49876 | 0.44897 | 0 | 0.49876 | 9.982 | 9.982
3865 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901010103 | F03-CNHALLI | AGRI | DLMS Meter | 0.968 | 0.87089 | 0 | 0.968 | 10.0316 | 10.0316
3866 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901010104 | F04-YADALAGATTE | AGRI | DLMS Meter | 0.53544 | 0.48186 | 0 | 0.53544 | 10.0067 | 10.0067
3867 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901010105 | F05-MYLENAHALLI | AGRI | DLMS Meter | 0.57496 | 0.51749 | 0 | 0.57496 | 9.9955 | 9.9955
3868 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901020301 | F06-THIPPEREDIHALLY | AGRI | DLMS Meter | 1.6528 | 1.4622 | 0 | 1.6528 | 11.5303 | 14.2339
3869 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901020302 | F07-GUDIHALLY | AGRI | DLMS Meter | 0.56492 | 0.50854 | 0 | 0.56492 | 9.9796 | 9.9796
3870 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901020303 | F08-D.ULLARTHI | AGRI | DLMS Meter | 1.0542 | 0.94869 | 0 | 1.0542 | 10.007 | 10.007
3871 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901010106 | F09-GHTAPHARTHI | NJY | DLMS Meter | 0.61525 | 0.56587 | 0 | 0.61525 | 8.0265 | 53.5068
3872 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901010107 | F10-KALUVEHALLI | NJY | DLMS Meter | 0.79684 | 0.70508 | 0 | 0.79684 | 11.5156 | 38.3232
3873 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | MYLANAHALLI_66 | 1310402901020304 | F11-KAMASAMUDRA NJY | NJY | DLMS Meter | 0.8182 | 0.70154 | 0 | 0.8182 | 14.2582 | 56.8376
3874 | BRAZ | KOLAR | KGF | BETHAMANGLA | N G HULKUR _66 | 1230203904010102 | F01-VENGASANDRA | AGRI | DLMS Meter | 1.013 | 0.9118 | 0 | 1.013 | 9.9938 | 9.9938
3875 | BRAZ | KOLAR | KGF | BETHAMANGLA | N G HULKUR _66 | 1230203904010103 | F02-SUNDRAPALYA NJY | NJY | DLMS Meter | 2.2086 | 1.9101 | 0 | 2.2086 | 13.5154 | 66.7466
3876 | BRAZ | KOLAR | KGF | BETHAMANGLA | N G HULKUR _66 | 1230203904010104 | F03-RAYASANDRA | AGRI | DLMS Meter | 0.94874 | 0.85382 | 0 | 0.94874 | 10.0045 | 10.0045
3877 | BRAZ | KOLAR | KGF | BETHAMANGLA | N G HULKUR _66 | 1230203904010301 | F05-PANTHANAHALLI | AGRI | DLMS Meter | 1.243 | 1.1186 | 0 | 1.243 | 10.0057 | 10.0057
3878 | BRAZ | KOLAR | KGF | BETHAMANGLA | N G HULKUR _66 | 1230203904010302 | F06-NG-HULKUR | AGRI | DLMS Meter | 1.2028 | 1.0824 | 0 | 1.2028 | 10.0081 | 10.0081
3879 | BRAZ | KOLAR | KGF | BETHAMANGLA | N G HULKUR _66 | 1230203904020101 | F07-KADRIGANAKUPPA | AGRI | DLMS Meter | 0.84618 | 0.76182 | 0 | 0.84618 | 9.97 | 9.97
3880 | BRAZ | KOLAR | KGF | BETHAMANGLA | N G HULKUR _66 | 1230203904020301 | F08-THALAPALLI | AGRI | DLMS Meter | 0.72864 | 0.65565 | 0 | 0.72864 | 10.0169 | 10.0169
3881 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907010101 | F01-HUSSAINPURA | AGRI | DLMS Meter | 0.63704 | 0.57317 | 0 | 0.63704 | 10.0262 | 10.0262
3882 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907010102 | F02-KODAMADAGU | AGRI | DLMS Meter | 0.61358 | 0.55216 | 0 | 0.61358 | 10.0101 | 10.0101
3883 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907010103 | F03-WATER--SUPPLY | WATER WORKS | DLMS Meter | 0.1432 | 0.13102 | 0 | 0.1432 | 8.5028 | 55.7467
3884 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907010104 | F04-S.R.PURA | AGRI | DLMS Meter | 0.96624 | 0.8698 | 0 | 0.96624 | 9.9811 | 10.6498
3885 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907020301 | F05-HOSAHALLI | AGRI | DLMS Meter | 1.1288 | 1.0155 | 0 | 1.1288 | 10.0353 | 10.0353
3886 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907020302 | F06-B.K.HALLI | AGRI | DLMS Meter | 0.8411 | 0.75701 | 0 | 0.8411 | 9.9981 | 9.9981
3887 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907020101 | F07-TIRUMANI-EXPRESS | AGRI | DLMS Meter | 0.74184 | 0.66738 | 0 | 0.74184 | 10.0375 | 10.0375
3888 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907010502 | F09-BHOOPUR NJY | NJY | DLMS Meter | 0.729 | 0.65666 | 0 | 0.729 | 9.9235 | 85.7762
3889 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907010501 | F10-NJY VALLURU | NJY | DLMS Meter | 1.2091 | 1.0925 | 0 | 1.2091 | 9.6475 | 32.0224
3890 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907010503 | F11-RYAPTE NJY | NJY | DLMS Meter | 0.4754 | 0.42852 | 0 | 0.4754 | 9.8618 | 91.8272
3891 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | NAGALMADIKE_66 | 1320306907010504 | F12-KODAMADUGU NJY | NJY | DLMS Meter | 0.6584 | 0.59291 | 0 | 0.6584 | 9.9474 | 80.6223
3892 | BMASZ | SOUTH | HSR | S8 | NAGANATHAPURA_66 | 1110303901020301 | F08-NOVEL | URBAN MIXED LOAD | DLMS Meter | 4.3269 | 3.859 | 0.175 | 4.1519 | 7.0552 | 15.6347
3893 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901020302 | F09-KUDLU | URBAN MIXED LOAD | DLMS Meter | 1.5991 | 1.5677 | 0 | 1.5991 | 1.9614 | 4.1616
3894 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901020303 | F10-MICO-BOSCH | INDUSTRIAL | DLMS Meter | 6.8071 | 3.3357 | 3.2601 | 3.547 | 5.957 | 6.038
3895 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901020304 | F11-ELECTRONIC-CITY | DOMESTIC | DLMS Meter | 5.6595 | 5.4342 | 0 | 5.6595 | 3.9805 | 4.7156
3896 | BMASZ | SOUTH | HSR | S8 | NAGANATHAPURA_66 | 1110303901020305 | F13-A.E.C.S-LAYOUT-B-BLOCK | URBAN MIXED LOAD | DLMS Meter | 2.3997 | 2.2261 | 0 | 2.3997 | 7.2349 | 7.2349
3897 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901020306 | F14-OZONE-TECH-PARK | DOMESTIC | DLMS Meter | 3.213 | 2.8869 | 0.21017 | 3.0029 | 3.8638 | 5.7538
3898 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901020108 | F15-C-K-NAGAR | DOMESTIC | DLMS Meter | 1.8154 | 1.3466 | 0.42501 | 1.3904 | 3.1481 | 8.0676
3899 | BMASZ | SOUTH | HSR | S8 | NAGANATHAPURA_66 | 1110303901010102 | F16-OMTP | IDLE | DLMS Meter | 2.6442 | 2.4179 | 0 | 2.6442 | 8.5599 | 27.1225
3900 | BMASZ | SOUTH | HSR | S8 | NAGANATHAPURA_66 | 1110303901030501 | F18-MLA LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.7079 | 2.2996 | 0.195 | 2.5129 | 8.4884 | 16.6931
3901 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901030506 | F19-DODDANAGAMANGALA | DOMESTIC | DLMS Meter | 2.3837 | 2.2898 | 0 | 2.3837 | 3.9376 | 3.9376
3902 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901030507 | F20-CHIKKATHOGUR | DOMESTIC | DLMS Meter | 5.7573 | 1.6479 | 3.9982 | 1.7591 | 6.3228 | 7.3885
3903 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901030502 | F21-PARAPPANA AGRAHARA | URBAN MIXED LOAD | DLMS Meter | 3.2588 | 2.705 | 0.40568 | 2.8531 | 5.1897 | 10.0162
3904 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901030508 | F22-METRO MARKET | DOMESTIC | DLMS Meter | 4.1027 | 3.3897 | 0.53638 | 3.5664 | 4.9548 | 5.446
3905 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901030505 | F23-BOSCH | INDUSTRIAL | DLMS Meter | 5.9995 | 5.7304 | 0 | 5.9995 | 4.485 | 4.485
3906 | BMASZ | SOUTH | HSR | S8 | NAGANATHAPURA_66 | 1110303901030503 | F24-PURVANKAR | DOMESTIC | DLMS Meter | 2.6473 | 2.1924 | 0.251 | 2.3963 | 8.5062 | 9.639
3907 | BMASZ | SOUTH | HSR | S11 | NAGANATHAPURA_66 | 1110303901030504 | F25-BELLANDUR_2 | URBAN MIXED LOAD | DLMS Meter | 4.6182 | 4.3487 | 0 | 4.6182 | 5.8363 | 11.5034
3908 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901010104 | F26-SHOBHA SILICON APARTMENT | URBAN MIXED LOAD | DLMS Meter | 1.4062 | 0.73808 | 0.63994 | 0.76631 | 3.6844 | 9.6277
3909 | BMASZ | SOUTH | HSR | S11 | NAGANATHAPURA_66 | #N/A | F27 | #N/A | DLMS Meter | 0.45979 | 0.20228 | 0.247 | 0.21279 | 4.94 | 8.5239
3910 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | NAGASAMUDRA_66 | 1310403902010101 | F01-ASHOKSIDDAPURA | AGRI | DLMS Meter | 1.0469 | 0.94191 | 0 | 1.0469 | 10.0255 | 10.0255
3911 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | NAGASAMUDRA_66 | 1310403902010102 | F02-NAGASAMUDRA | AGRI | DLMS Meter | 0.2325 | 0.20922 | 0 | 0.2325 | 10.0138 | 10.0138
3912 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | NAGASAMUDRA_66 | 1310403902010103 | F03-AMAKUNDI | AGRI | DLMS Meter | 0.9167 | 0.82503 | 0 | 0.9167 | 9.9997 | 9.9997
3913 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | NAGASAMUDRA_66 | 1310403902010104 | F04-CHIKKANAHALLI | AGRI | DLMS Meter | 0.75878 | 0.68322 | 0 | 0.75878 | 9.9574 | 9.9574
3914 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | NAGASAMUDRA_66 | 1310403902010105 | F05-NJY ROPPA | NJY | DLMS Meter | 1.8736 | 1.6056 | 0 | 1.8736 | 14.3068 | 58.1663
3915 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901010101 | F01-GOLLU | AGRI | DLMS Meter | 1.4652 | 1.3185 | 0 | 1.4652 | 10.0128 | 10.0128
3916 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901010102 | F02-VANTURU | AGRI | DLMS Meter | 0.8806 | 0.79246 | 0 | 0.8806 | 10.0094 | 10.0094
3917 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901010103 | F03-RAMADEVANAGUDI | AGRI | DLMS Meter | 1.5404 | 1.2154 | 0.19 | 1.3504 | 9.9958 | 9.9958
3918 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901010104 | F04-KETHENAHALLY | AGRI | DLMS Meter | 2.18 | 1.9618 | 0 | 2.18 | 10.0112 | 10.0112
3919 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901010105 | F05-GANGAREKALUVE | AGRI | DLMS Meter | 1.0848 | 0.95818 | 0.02 | 1.0648 | 10.0131 | 10.0131
3920 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901020301 | F06-GUNDLAGURKI | AGRI | DLMS Meter | 1.653 | 1.4875 | 0 | 1.653 | 10.015 | 10.015
3921 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901020302 | F07-DEVASTHANA-HOSAHALLY | AGRI | DLMS Meter | 1.9676 | 1.7321 | 0.04 | 1.9276 | 10.1397 | 10.1397
3922 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901020303 | F08-SHETTYVARAHALLI-NJY | NJY | DLMS Meter | 1.246 | 0.25091 | 0.965 | 0.281 | 10.7083 | 15.7061
3923 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901020304 | F09-ANGAREKANAHALLY | AGRI | DLMS Meter | 2.0336 | 1.7581 | 0.08 | 1.9536 | 10.0058 | 10.0058
3924 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901020305 | F10-KANDAKANAHALLY | AGRI | DLMS Meter | 1.3288 | 1.1016 | 0.105 | 1.2238 | 9.9887 | 9.9887
3925 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901020306 | F11-GUVALAKANAHALLI-NJY | NJY | DLMS Meter | 0.9004 | 0.21305 | 0.665 | 0.2354 | 9.4964 | 28.4787
3926 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901020307 | F12-MARGANHALLI-NJY | NJY | DLMS Meter | 1.3418 | 0.90147 | 0.35 | 0.9918 | 9.1073 | 61.9893
3927 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA URBAN | NALLIMARADANAHALLI_66 | 1230301901020308 | F13-S-GOLLAHALLI-NJY | NJY | DLMS Meter | 1.767 | 0.97549 | 0.695 | 1.072 | 9.0028 | 30.5076
3928 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | NALLUR_66 | 1310106908010101 | F01-ANAPURA IP | AGRI | DLMS Meter | 0.5688 | 0.51062 | 0 | 0.5688 | 10.2289 | 10.2289
3929 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | NALLUR_66 | 1310106908010102 | F02-BULASAGARA IP | AGRI | DLMS Meter | 1.1022 | 0.99076 | 0 | 1.1022 | 10.1104 | 10.1104
3930 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | NALLUR_66 | 1310106908010103 | F03-SIDDARAMESHWARA NJY | NJY | DLMS Meter | 0.5988 | 0.42462 | 0.127 | 0.4718 | 9.9998 | 43.4061
3931 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | NALLUR_66 | 1310106908010104 | F04-HATTI IP | AGRI | DLMS Meter | 2.2936 | 2.0645 | 0 | 2.2936 | 9.9904 | 9.9904
3932 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903010101 | F01-NELAVAGILU | AGRI | DLMS Meter | 1.0811 | 0.97345 | 0 | 1.0811 | 9.9578 | 9.9578
3933 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903010102 | F02-HINDIGNALA | AGRI | DLMS Meter | 1.0891 | 0.98 | 0 | 1.0891 | 10.0156 | 10.0156
3934 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903010103 | F03-HINDIGNALA-(CHIKKONDANAHALLI) | NJY | DLMS Meter | 1.4417 | 1.2547 | 0 | 1.4417 | 12.9712 | 77.8195
3935 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903020301 | F04-ITTASANDRA | AGRI | DLMS Meter | 0.92054 | 0.82804 | 0 | 0.92054 | 10.048 | 10.048
3936 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903020302 | F05-N.HOSAHALLI | NJY | DLMS Meter | 3.2583 | 2.8087 | 0 | 3.2583 | 13.7982 | 69.4267
3937 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903020303 | F06-NANDAGUDI-TOWN | URBAN MIXED LOAD | DLMS Meter | 2.7283 | 2.3742 | 0 | 2.7283 | 12.9786 | 38.0113
3938 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903020304 | F07-NANDAGUDI-RURAL | AGRI | DLMS Meter | 0.99908 | 0.8993 | 0 | 0.99908 | 9.987 | 9.987
3939 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903010104 | F08-ANUPAHALLI | NJY | DLMS Meter | 1.3331 | 1.1552 | 0 | 1.3331 | 13.3489 | 86.2617
3940 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903010105 | F09-SHIVANAPURA | AGRI | DLMS Meter | 1.0302 | 0.92771 | 0 | 1.0302 | 9.9523 | 9.9523
3941 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903010106 | F10 -CHEEMASANDRA | AGRI | DLMS Meter | 0.64394 | 0.57952 | 0 | 0.64394 | 10.0042 | 10.0042
3942 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | NANDAGUDI_66 | 1210203903010107 | F11-GUNDRAHALLI (AGRI) | AGRI | DLMS Meter | 1.3907 | 1.2517 | 0 | 1.3907 | 9.9968 | 9.9968
3943 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | NANDIGANAHALLI_66 | 1230401903010104 | F01-THUMMALAHALLI NJY | NJY | DLMS Meter | 0.56368 | 0.5058 | 0 | 0.56368 | 10.2683 | 80.3398
3944 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | NANDIGANAHALLI_66 | 1230401903010103 | F02-DANDUPALYA | AGRI | DLMS Meter | 0.7994 | 0.43593 | 0.315 | 0.4844 | 10.0068 | 10.0068
3945 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | NANDIGANAHALLI_66 | 1230401903010101 | F03-GOPALLI | AGRI | DLMS Meter | 1.255 | 1.1291 | 0 | 1.255 | 10.0286 | 10.0286
3946 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | NANDIGANAHALLI_66 | 1230401903010102 | F04-MUDDALAHALLI | AGRI | DLMS Meter | 1.2599 | 1.1339 | 0 | 1.2599 | 10.0032 | 10.0032
3947 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | NANDIGANAHALLI_66 | 1230401903020301 | F05-MUKTHISHWARA-NJY | NJY | DLMS Meter | 1.0053 | 0.62214 | 0.30262 | 0.70266 | 11.4591 | 58.4964
3948 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | NANDIGANAHALLI_66 | 1230401903020302 | F06-KAPALLI | AGRI | DLMS Meter | 0.91824 | 0.82653 | 0 | 0.91824 | 9.9874 | 9.9874
3949 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | NANDIGANAHALLI_66 | 1230401903020303 | F07-MURUGAMALLA | AGRI | DLMS Meter | 1.3414 | 0.98702 | 0.245 | 1.0964 | 9.9728 | 9.9728
3950 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | NANDIGANAHALLI_66 | 1230401903020304 | F08-ADEPALLI-NJY | NJY | DLMS Meter | 1.1524 | 0.98246 | 0.03138 | 1.1211 | 12.3631 | 69.0959
3951 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | NANDIGANAHALLI_66 | 1230401903020305 | F09-KAGATHI NJY | NJY | DLMS Meter | 1.3339 | 0.98984 | 0.23126 | 1.1026 | 10.2306 | 67.3614
3952 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | NANDIGANAHALLI_66 | 1230401903020306 | F10-BHOOMISHETTYHALLI | AGRI | DLMS Meter | 0.31576 | 0.21021 | 0.0822 | 0.23356 | 9.9974 | 9.9974
3953 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906010101 | F01-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 0.4714 | 0.37049 | 0.066 | 0.4054 | 8.6112 | 48.0723
3954 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906010102 | F02-NANDIGUDI | AGRI | DLMS Meter | 1.2558 | 1.1304 | 0 | 1.2558 | 9.9869 | 9.9869
3955 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906010103 | F03-K.N-HALLI | AGRI | DLMS Meter | 0.7225 | 0.65028 | 0 | 0.7225 | 9.9956 | 9.9956
3956 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906010104 | F04-BHAYRANAPADA | AGRI | DLMS Meter | 1.0044 | 0.90365 | 0 | 1.0044 | 10.0309 | 10.0309
3957 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906010106 | F05-KONANATHALE | AGRI | DLMS Meter | 0.9674 | 0.8707 | 0 | 0.9674 | 9.9963 | 9.9963
3958 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906020301 | F06-HULIGANAHOLE | AGRI | DLMS Meter | 0.7024 | 0.63221 | 0 | 0.7024 | 9.9936 | 9.9936
3959 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906020302 | F07-VASANA | AGRI | DLMS Meter | 0.6212 | 0.41929 | 0.155 | 0.4662 | 10.0624 | 10.0624
3960 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906020303 | F08-MARALAHALLI | AGRI | DLMS Meter | 0.9884 | 0.62384 | 0.295 | 0.6934 | 10.0312 | 10.0312
3961 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906010105 | F09-WATER-SUPPLY | WATER WORKS | DLMS Meter | 0.7614 | 0.52522 | 0.1835 | 0.5779 | 9.1163 | 54.7852
3962 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906010302 | F11-MARKANDESWARA | NJY | DLMS Meter | 0.6852 | 0.48304 | 0.155 | 0.5302 | 8.8953 | 49.7218
3963 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | NANDIGUDI_66 | 1310301906010301 | F12-TUNGA BHDRA | NJY | DLMS Meter | 0.4629 | 0.21174 | 0.2325 | 0.2304 | 8.0979 | 41.8255
3964 | CTAZ | TUMKUR | TUMKUR | GUBBI | NANDIHALLI CROSS_66 | 1320106908010101 | F01-KATANAHALLI | AGRI | DLMS Meter | 0.8538 | 0.62468 | 0.14635 | 0.70745 | 11.6994 | 11.6994
3965 | CTAZ | TUMKUR | TUMKUR | GUBBI | NANDIHALLI CROSS_66 | 1320106908010102 | F02-MARATIPALYA | AGRI | DLMS Meter | 0.8532 | 0.24803 | 0.57587 | 0.27733 | 10.5648 | 10.5648
3966 | CTAZ | TUMKUR | TUMKUR | GUBBI | NANDIHALLI CROSS_66 | 1320106908010103 | F03-CHINDIGERE | AGRI | DLMS Meter | 0.9118 | 0.66356 | 0.15962 | 0.75218 | 11.7808 | 11.7808
3967 | CTAZ | TUMKUR | TUMKUR | GUBBI | NANDIHALLI CROSS_66 | 1320106908010104 | F04-MMA KAVAL | AGRI | DLMS Meter | 0.7438 | 0.44476 | 0.23654 | 0.50726 | 12.3215 | 12.3215
3968 | BMANZ | NORTH | PEENYA | N7 | NANDINILAYOUT_66 | 1120103902020301 | F01-NANDINI-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.5491 | 2.9756 | 0.30751 | 3.2415 | 8.2048 | 18.957
3969 | BMANZ | NORTH | PEENYA | N7 | NANDINILAYOUT_66 | 1120103902010101 | F02-RMC | URBAN MIXED LOAD | DLMS Meter | 2.9716 | 2.602 | 0.086159 | 2.8855 | 9.8245 | 13.2395
3970 | BMANZ | NORTH | PEENYA | N7 | NANDINILAYOUT_66 | 1120103902010102 | F03-SOAP-FACTORY | URBAN MIXED LOAD | DLMS Meter | 2.8239 | 2.5563 | 0 | 2.8239 | 9.4747 | 15.9641
3971 | BMANZ | NORTH | PEENYA | N7 | NANDINILAYOUT_66 | 1120103902010103 | F05-MAHALAXMI-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.6988 | 3.4607 | 0 | 3.6988 | 6.4383 | 13.6578
3972 | BMANZ | NORTH | PEENYA | N7 | NANDINILAYOUT_66 | 1120103902020303 | F07-F-NANDINI-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.9344 | 2.6331 | 0.030998 | 2.9034 | 9.3101 | 13.0861
3973 | BMANZ | NORTH | PEENYA | N7 | NANDINILAYOUT_66 | 1120103902020304 | F08-MEI-LAYOUT-&-INDUSTRIAL-AREA | INDUSTRIAL | DLMS Meter | 6.1457 | 5.4976 | 0.31426 | 5.8314 | 5.7254 | 15.6818
3974 | BMANZ | NORTH | MALLESHWARA | C1 | NANDINILAYOUT_66 | 1120103902010104 | F09-SUBRAMANYA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.9242 | 3.6648 | 0.072 | 3.8522 | 4.8634 | 8.8545
3975 | BMANZ | NORTH | PEENYA | N7 | NANDINILAYOUT_66 | 1120103902020305 | F10-JAIMARUTHINAGARA | URBAN MIXED LOAD | DLMS Meter | 4.1876 | 2.1682 | 1.8156 | 2.372 | 8.5892 | 13.8111
3976 | BMANZ | NORTH | PEENYA | N7 | NANDINILAYOUT_66 | 1120103902020306 | F11-KURUBARAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.7376 | 3.4728 | 0.020623 | 3.717 | 6.5702 | 16.8445
3977 | BMANZ | NORTH | PEENYA | N7 | NANDINILAYOUT_66 | 1120103902020307 | F12-GANESHA-TEMPLE | URBAN MIXED LOAD | DLMS Meter | 1.3535 | 1.2678 | 0 | 1.3535 | 6.3267 | 11.3067
3978 | BMANZ | NORTH | PEENYA | N7 | NANDINILAYOUT_66 | 1120103902020308 | F13-1_2_3RD_BLOCK_NANDINI_LAYOUT | DOMESTIC | DLMS Meter | 3.8381 | 3.3926 | 0.077776 | 3.7604 | 9.78 | 35.0453
3979 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902010101 | F01-BYRKUR | AGRI | DLMS Meter | 1.0482 | 0.94322 | 0 | 1.0482 | 10.015 | 10.015
3980 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902010102 | F02-KERSAMANGALA | NJY | DLMS Meter | 1.5835 | 1.4371 | 0 | 1.5835 | 9.2433 | 63.0869
3981 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902020301 | F03-GUMMAKAL | AGRI | DLMS Meter | 0.89982 | 0.80994 | 0 | 0.89982 | 9.9887 | 10.0336
3982 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902020302 | F04-SUREKUNTE | AGRI | DLMS Meter | 0.6525 | 0.5872 | 0 | 0.6525 | 10.008 | 10.5404
3983 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902020303 | F05-THIPPADODDI | AGRI | DLMS Meter | 0.89952 | 0.80957 | 0 | 0.89952 | 10.0002 | 10.2322
3984 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902020304 | F06-HEBBANI | AGRI | DLMS Meter | 0.9074 | 0.81648 | 0 | 0.9074 | 10.0195 | 10.0195
3985 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902020305 | F07-NAGAVARA | AGRI | DLMS Meter | 0.99282 | 0.89372 | 0 | 0.99282 | 9.9812 | 9.9812
3986 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902010103 | F08-ANANTHPURA | AGRI | DLMS Meter | 0.8807 | 0.79282 | 0 | 0.8807 | 9.9787 | 9.9787
3987 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902010104 | F09-GUDIPALLI | AGRI | DLMS Meter | 0.011475 | 0.010632 | 0 | 0.011475 | 7.3464 | 7.3464
3988 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902010105 | F10-NANGLI-LOCAL | DOMESTIC | DLMS Meter | 0.58066 | 0.52776 | 0 | 0.58066 | 9.1107 | 39.9814
3989 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902010106 | F11-VODDAHALLI | AGRI | DLMS Meter | 0.9928 | 0.89351 | 0 | 0.9928 | 10.0009 | 10.0009
3990 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902020306 | F12-CHAMAKALAHALLY | AGRI | DLMS Meter | 0.76308 | 0.6869 | 0 | 0.76308 | 9.9839 | 9.9839
3991 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902020307 | F13-K.BYAPALLY | AGRI | DLMS Meter | 1.2307 | 1.1076 | 0 | 1.2307 | 10.0046 | 10.0046
3992 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902020308 | F14-SHETTIKAL-NJY | NJY | DLMS Meter | 1.0309 | 0.93232 | 0 | 1.0309 | 9.5664 | 55.6085
3993 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902010107 | F15-UGANI | AGRI | DLMS Meter | 1.0986 | 0.62669 | 0.402 | 0.69656 | 10.0304 | 10.0304
3994 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902010108 | F16-THATHIKAL NJY | NJY | DLMS Meter | 0.9622 | 0.86887 | 0 | 0.9622 | 9.6995 | 67.2082
3995 | BRAZ | KOLAR | KGF | MULABAGILU | NANGLI_66 | 1230202902020309 | F17-G.MARANDAHALLI | AGRI | DLMS Meter | 0.7369 | 0.66331 | 0 | 0.7369 | 9.987 | 10.7116
3996 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010501 | F01-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 3.3814 | 2.2501 | 0.92 | 2.4614 | 8.5862 | 22.8105
3997 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908020301 | F02-ALPIN | INDUSTRIAL | DLMS Meter | 1.5278 | 1.4223 | 0 | 1.5278 | 6.9073 | 23.0565
3998 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010110 | F04-LUMAX | INDUSTRIAL | DLMS Meter | 1.637 | 1.5752 | 0 | 1.637 | 3.7728 | 3.7728
3999 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908020302 | F05-KENDATTI | AGRI | DLMS Meter | 1.2498 | 1.1253 | 0 | 1.2498 | 9.9587 | 9.9587
4000 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908020303 | F06-NARSAPURA | AGRI | DLMS Meter | 1.1844 | 1.063 | 0 | 1.1844 | 10.2471 | 10.2471
4001 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908020304 | F07-MAHENDRA | INDUSTRIAL | DLMS Meter | 2.4154 | 1.2572 | 1.03 | 1.3854 | 9.2511 | 23.9197
4002 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908020305 | F08-JODIKRISHNAPURA | AGRI | DLMS Meter | 1.0464 | 0.93676 | 0 | 1.0464 | 10.4781 | 10.4781
4003 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010504 | F09-EXCEDY | INDUSTRIAL | DLMS Meter | 3.3992 | 3.4104 | 0 | 3.3992 | -0.32949 | -0.32949
4004 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010105 | F10-UNICOST | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4005 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010111 | F11-NJY K B HOSAHALLI | NJY | DLMS Meter | 0.2142 | 0.1915 | 0 | 0.2142 | 10.5973 | 51.7072
4006 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010505 | F12-BADAVE-(IND) | INDUSTRIAL | DLMS Meter | 1.54 | 1.4421 | 0 | 1.54 | 6.3571 | 6.3571
4007 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010106 | F13-INDO | INDUSTRIAL | DLMS Meter | 1.3654 | 1.3651 | 0 | 1.3654 | 0.020141 | 0.020141
4008 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010107 | F14-ASIAN | INDUSTRIAL | DLMS Meter | 0.2938 | 0.30415 | 0 | 0.2938 | -3.5228 | -3.5228
4009 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010502 | F15-SIPANI-FIBRES | INDUSTRIAL | DLMS Meter | 5.424 | 5.3994 | 0 | 5.424 | 0.45354 | 0.45354
4010 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010108 | F16-SCANIA | INDUSTRIAL | DLMS Meter | 0.135 | 0.1261 | 0 | 0.135 | 6.5926 | 6.5926
4011 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010109 | F17-BANDO | INDUSTRIAL | DLMS Meter | 1.4474 | 1.4152 | 0 | 1.4474 | 2.2212 | 2.2212
4012 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010117 | F18-SAMANTHA | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4013 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010118 | F19-SWASTHID | INDUSTRIAL | DLMS Meter | 2.373 | 2.2323 | 0 | 2.373 | 5.9294 | 5.9991
4014 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010112 | F20-KIADB NARASAPURA I | INDUSTRIAL | DLMS Meter | 3.3252 | 1.8432 | 1.28 | 2.0452 | 9.8771 | 11.3512
4015 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010113 | F21-KIADB NARASAPURA II | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4016 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010114 | F22-KIADB NARASAPURA III | INDUSTRIAL | DLMS Meter | 1.363 | 1.2397 | 0 | 1.363 | 9.0481 | 9.0945
4017 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010115 | F23-LAXMI INDUSTRIES | INDUSTRIAL | DLMS Meter | 0.6624 | 0.4854 | 0.13 | 0.5324 | 8.8276 | 8.8276
4018 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010116 | F24-NAGALAPURA NJY | NJY | DLMS Meter | 2.5064 | 2.2017 | 0 | 2.5064 | 12.1548 | 20.5628
4019 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010119 | F25-LITTLE FINGER | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4020 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010103 | F26-NJYBELLUR | NJY | DLMS Meter | 2.168 | 1.9097 | 0 | 2.168 | 11.9154 | 35.9272
4021 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | NARSAPUR_66 | 1230102908010102 | F27-ASK | INDUSTRIAL | DLMS Meter | 2.3136 | 2.3179 | 0 | 2.3136 | -0.18478 | -0.18478
4022 | BMASZ | WEST | RR NAGAR | W2 | NATIONAL_COLLEGE_66 | 1140202901010101 | F02-KR-ROAD,-RMU | URBAN MIXED LOAD | DLMS Meter | 2.4824 | 2.3477 | 0 | 2.4824 | 5.4268 | 14.1404
4023 | BMASZ | WEST | RR NAGAR | W2 | NATIONAL_COLLEGE_66 | 1140202901010103 | F05-SURVEYOR-STREET-COOL-CORNER | URBAN MIXED LOAD | DLMS Meter | 2.0503 | 1.7317 | 0.225 | 1.8253 | 5.1261 | 11.9842
4024 | BMASZ | WEST | RR NAGAR | W2 | NATIONAL_COLLEGE_66 | 1140202901010104 | F06-FPMK-CIRCLE | URBAN MIXED LOAD | DLMS Meter | 2.437 | 2.2423 | 0.075 | 2.362 | 5.0675 | 10.8251
4025 | BMASZ | WEST | RR NAGAR | W2 | NATIONAL_COLLEGE_66 | 1140202901020303 | F10-GANDHIBAZAAR-RMU | URBAN MIXED LOAD | DLMS Meter | 4.8875 | 4.0683 | 0.593 | 4.2945 | 5.2664 | 12.3136
4026 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908010104 | F01-DRDO | DEFENSE ESTABLISHMENT | DLMS Meter | 0.34265 | 0.34132 | 0 | 0.34265 | 0.38859 | 0.61219
4027 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908020303 | F02-DEVARAHATTY | AGRI | DLMS Meter | 1.1595 | 1.0439 | 0 | 1.1595 | 9.9677 | 9.9677
4028 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908010103 | F03-NERLAGUNTE | AGRI | DLMS Meter | 0.76443 | 0.67886 | 0 | 0.76443 | 11.1942 | 11.1942
4029 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908010102 | F04-MAHADEVAPURA | AGRI | DLMS Meter | 1.0517 | 0.94652 | 0 | 1.0517 | 9.9976 | 9.9976
4030 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908010101 | F05-GOWDIGERE | AGRI | DLMS Meter | 0.96998 | 0.87331 | 0 | 0.96998 | 9.9662 | 9.9662
4031 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908010107 | F07-GWORIPURA NJY | NJY | DLMS Meter | 0.77656 | 0.6709 | 0 | 0.77656 | 13.6068 | 46.8089
4032 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908020301 | F09-NAAYAKANAHATTY | DOMESTIC | DLMS Meter | 1.0132 | 0.90501 | 0 | 1.0132 | 10.6748 | 10.6748
4033 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908010106 | F10-HALAJOGIHATTY NJY | NJY | DLMS Meter | 0.48751 | 0.42418 | 0 | 0.48751 | 12.9907 | 39.8536
4034 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908020304 | F11-REKALAGERE | AGRI | DLMS Meter | 1.0863 | 0.97344 | 0 | 1.0863 | 10.3869 | 10.3869
4035 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908020302 | F12-NELGETHNAHATTY | AGRI | DLMS Meter | 0.79605 | 0.71589 | 0 | 0.79605 | 10.0701 | 10.0701
4036 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908020305 | F13-TOREKOLAMMANAHALLY | AGRI | DLMS Meter | 0.88404 | 0.79565 | 0 | 0.88404 | 9.9982 | 9.9982
4037 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908020306 | F14-MALLURAHALLY | AGRI | DLMS Meter | 0.8917 | 0.79352 | 0 | 0.8917 | 11.01 | 11.01
4038 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908010108 | F15-BEMAGONDANAHALLY NJY | NJY | DLMS Meter | 0.62758 | 0.54009 | 0 | 0.62758 | 13.9405 | 46.9741
4039 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NAYAKANAHATTI_66 | 1310402908020101 | F16-THIPPERUDRASWAMY NJY | NJY | DLMS Meter | 0.38404 | 0.33964 | 0 | 0.38404 | 11.56 | 64.9325
4040 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | NEELAGUNDA_220 | 1310303901010102 | F03-BYRAPURA | AGRI | DLMS Meter | 1.4462 | 1.3019 | 0 | 1.4462 | 9.9779 | 9.9779
4041 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | NEELAGUNDA_220 | 1310303901010103 | F04-NEELAGUNDA NJY | NJY | DLMS Meter | 0.67652 | 0.50121 | 0.117 | 0.55952 | 10.4213 | 55.5058
4042 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | NEELAGUNDA_220 | 1310303901010104 | F05-K.KALLAHALLI NJY | NJY | DLMS Meter | 0.34856 | 0.23978 | 0.0815 | 0.26706 | 10.2131 | 44.6946
4043 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | NEELAGUNDA_220 | 1310303901010105 | F06-MAJJIGERI | AGRI | DLMS Meter | 1.0078 | 0.90673 | 0 | 1.0078 | 10.0305 | 10.0305
4044 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | NEELAGUNDA_220 | 1310303901010109 | F09-CPT EXPRESS FEEDER | INDUSTRIAL | DLMS Meter | 0.0328 | 0.02995 | 0 | 0.0328 | 8.689 | 8.689
4045 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | NEERAGUNDA_66 | 1310204907010101 | F01-NEERAGUNDA | NJY | DLMS Meter | 0.5015 | 0.27453 | 0.19311 | 0.30839 | 10.9814 | 35.6038
4046 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | NEERAGUNDA_66 | 1310204907010102 | F02-ADRIKATTE | AGRI | DLMS Meter | 0.5676 | 0.51049 | 0 | 0.5676 | 10.0615 | 10.0615
4047 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | NEERAGUNDA_66 | 1310204907010103 | F03-SRI MATA | AGRI | DLMS Meter | 0.63931 | 0.57519 | 0 | 0.63931 | 10.0299 | 10.0299
4048 | CTAZ | DAVANAGERE | CHITRADURGA | HOSADURGA | NEERAGUNDA_66 | 1310204907010104 | F04-ALADAHALLI | AGRI | DLMS Meter | 0.9294 | 0.83651 | 0 | 0.9294 | 9.9946 | 9.9946
4049 | BMANZ | NORTH | PEENYA | N4 | NELAKEDIRENAHALLI_66 | 1120101901010101 | F02-SHOBHA-RUBY | URBAN MIXED LOAD | DLMS Meter | 3.6301 | 3.5466 | 0.025 | 3.6051 | 1.6229 | 5.2585
4050 | BMANZ | NORTH | PEENYA | N5 | NELAKEDIRENAHALLI_66 | 1120101901010102 | F03-N.G.HALLY | INDUSTRIAL | DLMS Meter | 3.5524 | 3.2576 | 0.07 | 3.4824 | 6.4562 | 9.7899
4051 | BMANZ | NORTH | PEENYA | N5 | NELAKEDIRENAHALLI_66 | 1120101901010103 | F04-ABHIMAN-PRAKASHANA | URBAN MIXED LOAD | DLMS Meter | 1.8749 | 1.1068 | 0.717 | 1.1579 | 4.4118 | 14.9334
4052 | BMANZ | NORTH | PEENYA | N5 | NELAKEDIRENAHALLI_66 | 1120101901010104 | F05-BELMAR-ESTATE | URBAN MIXED LOAD | DLMS Meter | 4.1687 | 3.7368 | 0.327 | 3.8417 | 2.7305 | 13.1262
4053 | BMASZ | WEST | KENGERI | K2 | NELAKEDIRENAHALLI_66 | 1120101901020102 | F06-ANDRAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.1809 | 1.8557 | 0.18996 | 1.9909 | 6.7907 | 10.182
4054 | BMASZ | WEST | KENGERI | K2 | NELAKEDIRENAHALLI_66 | 1120101901010105 | F07-THIGALARA PALYA | URBAN MIXED LOAD | DLMS Meter | 5.8506 | 5.2896 | 0.1861 | 5.6645 | 6.618 | 11.2102
4055 | BMASZ | WEST | KENGERI | K2 | NELAKEDIRENAHALLI_66 | 1120101901020301 | F08-KARIOBANAHALLI | URBAN MIXED LOAD | DLMS Meter | 5.8547 | 5.2364 | 0.062432 | 5.7923 | 9.5968 | 15.511
4056 | BMANZ | NORTH | PEENYA | N5 | NELAKEDIRENAHALLI_66 | 1120101901010301 | F09-REEMA-CONDUCTOR | INDUSTRIAL | DLMS Meter | 2.6347 | 2.5035 | 0.042 | 2.5927 | 3.4419 | 8.173
4057 | BMANZ | NORTH | PEENYA | N5 | NELAKEDIRENAHALLI_66 | 1120101901010302 | F10-KAPL | INDUSTRIAL | DLMS Meter | 3.3393 | 3.3195 | 0 | 3.3393 | 0.59215 | 0.59215
4058 | BMANZ | NORTH | PEENYA | N5 | NELAKEDIRENAHALLI_66 | 1120101901020302 | F11-NAGASANDRA | URBAN MIXED LOAD | DLMS Meter | 1.6959 | 1.6794 | 0 | 1.6959 | 0.9703 | 7.8478
4059 | BMASZ | WEST | KENGERI | K2 | NELAKEDIRENAHALLI_66 | 1120101901020101 | F12-THIPPENHALLI | URBAN MIXED LOAD | DLMS Meter | 4.3279 | 3.2271 | 0.78294 | 3.5449 | 8.9639 | 19.8868
4060 | BMASZ | WEST | KENGERI | K2 | NELAKEDIRENAHALLI_66 | 1120101901010107 | F14-NANDAGOKULA LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.4154 | 2.6972 | 0.45523 | 2.9601 | 8.8845 | 11.7953
4061 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010111 | F01-TATA HOUSING | RURAL MIXED LOAD | DLMS Meter | 1.7068 | 1.2363 | 0.302 | 1.4048 | 11.9912 | 11.9912
4062 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903020301 | F02-KBDL | RURAL MIXED LOAD | DLMS Meter | 3.0263 | 2.7992 | 0 | 3.0263 | 7.5035 | 10.8353
4063 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010109 | F03-KSSIDC | RURAL MIXED LOAD | DLMS Meter | 4.4556 | 3.5603 | 0.343 | 4.1126 | 13.4282 | 15.7528
4064 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010101 | F04-INDUSTRIAL | URBAN MIXED LOAD | DLMS Meter | 1.5443 | 1.4109 | 0 | 1.5443 | 8.6391 | 18.0828
4065 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010102 | F05-MADAWARA | URBAN MIXED LOAD | DLMS Meter | 2.0641 | 1.5404 | 0.3593 | 1.7048 | 9.6415 | 22.1971
4066 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | #N/A | F06-STN AUX | #N/A | DLMS Meter | 0 | 0.005771 | 0 | 0 | 0 | #DIV/0!
4067 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903020302 | F07-CHOCOLATE-FACTORY | URBAN MIXED LOAD | DLMS Meter | 2.4492 | 2.0016 | 0.235 | 2.2142 | 9.6015 | 12.7802
4068 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903020303 | F08-NELAMANGALA-TOWN | URBAN MIXED LOAD | DLMS Meter | 2.318 | 1.8455 | 0.2703 | 2.0477 | 9.8721 | 26.1671
4069 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903020304 | F09-SONDEKOPPA | AGRI | DLMS Meter | 1.89 | 1.7008 | 0 | 1.89 | 10.0121 | 11.5683
4070 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010103 | F10-HIMALAYA-DRUG | URBAN MIXED LOAD | DLMS Meter | 2.5085 | 2.0329 | 0.2753 | 2.2332 | 8.9688 | 19.8464
4071 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010104 | F11-ORGANIC | INDUSTRIAL | DLMS Meter | 4.4358 | 4.4452 | 0 | 4.4358 | -0.21044 | -0.21044
4072 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010105 | F12-V-V-PURA | URBAN MIXED LOAD | DLMS Meter | 4.6722 | 3.876 | 0.3993 | 4.2729 | 9.2898 | 22.4982
4073 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903020305 | F14-KESAR-MARBLE | URBAN MIXED LOAD | DLMS Meter | 3.7526 | 2.3658 | 1.0804 | 2.6722 | 11.4692 | 11.4692
4074 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903020306 | F15-PEPSI | RURAL MIXED LOAD | DLMS Meter | 4.3294 | 1.3799 | 2.77 | 1.5594 | 11.5063 | 11.5063
4075 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903030501 | F16-YENTAGANAHALLI | URBAN MIXED LOAD | DLMS Meter | 5.4576 | 4.8168 | 0.085 | 5.3726 | 10.3449 | 13.2302
4076 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903030502 | F17-RAMCO-BIOTECH | URBAN MIXED LOAD | DLMS Meter | 1.898 | 1.2228 | 0.529 | 1.369 | 10.6828 | 17.9782
4077 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903030503 | F18-VIJAYA-STEEL | URBAN MIXED LOAD | DLMS Meter | 2.7654 | 2.5092 | 0 | 2.7654 | 9.2657 | 9.2657
4078 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903030504 | F19-T-BEGUR-AGRI | AGRI | DLMS Meter | 0.70964 | 0.59937 | 0.045 | 0.66464 | 9.8205 | 9.8205
4079 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903030505 | F20-GOLLAHALLI | RURAL MIXED LOAD | DLMS Meter | 2.6166 | 2.081 | 0.27 | 2.3466 | 11.3183 | 13.5285
4080 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903030506 | F21-ABB | INDUSTRIAL | DLMS Meter | 0.92352 | 0.92593 | 0 | 0.92352 | -0.26074 | -0.195
4081 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903030507 | F22-DENSO | INDUSTRIAL | DLMS Meter | 2.0124 | 1.9981 | 0 | 2.0124 | 0.71128 | 0.72128
4082 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010112 | F23-RAMKY | URBAN MIXED LOAD | DLMS Meter | 3.3641 | 3.0297 | 0.025 | 3.3391 | 9.2661 | 37.4914
4083 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010106 | F24-SOLADEVANAHALLI | NJY | DLMS Meter | 2.2532 | 1.6465 | 0.4632 | 1.79 | 8.0138 | 24.5504
4084 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010107 | F25-MODALAKOTE-NJY | NJY | DLMS Meter | 0.89384 | 0.81514 | 0 | 0.89384 | 8.8046 | 16.4362
4085 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903010501 | F26-NIRMAN_LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.6952 | 2.2014 | 0.2604 | 2.4348 | 9.5894 | 12.5494
4086 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903030508 | F27-TELECOM_LAYOUT | RURAL MIXED LOAD | DLMS Meter | 0.05305 | 0.05109 | 0 | 0.05305 | 3.6946 | 29.6251
4087 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | NELMANGALA_66 | 1210104903030509 | F28-GOPALPURA-NJY | NJY | DLMS Meter | 2.6882 | 2.4801 | 0 | 2.6882 | 7.7427 | 8.8484
4088 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NERALAGUNTE_66 | 1310404905010103 | F01-BHEEMANAKERE | AGRI | DLMS Meter | 0.9068 | 0.81578 | 0 | 0.9068 | 10.0377 | 10.0377
4089 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NERALAGUNTE_66 | 1310404905010104 | F02-HOSAHALLY | NJY | DLMS Meter | 0.2666 | 0.2389 | 0 | 0.2666 | 10.3886 | 59.0667
4090 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NERALAGUNTE_66 | 1310404905010101 | F03-YARAMANCHAIAHNAHATTY | AGRI | DLMS Meter | 0.6735 | 0.60611 | 0 | 0.6735 | 10.0055 | 10.0055
4091 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NERALAGUNTE_66 | 1310404905010102 | F04-KANIVE MARAMMA NJY | NJY | DLMS Meter | 0.5358 | 0.46168 | 0 | 0.5358 | 13.8333 | 70.8344
4092 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | NERALAGUNTE_66 | 1310404905010105 | F06-KATAVVANAHALLY | AGRI | DLMS Meter | 0.327 | 0.29423 | 0 | 0.327 | 10.0205 | 10.0205
4093 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903010101 | F31-APC-II | INDUSTRIAL | DLMS Meter | 1.2928 | 1.3046 | 0 | 1.2928 | -0.912 | -0.912
4094 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903010102 | F32-BILL FORGE | INDUSTRIAL | DLMS Meter | 5.7804 | 5.8164 | 0 | 5.7804 | -0.62349 | -0.62349
4095 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903010103 | F33-LAMISTICK-APPAREL | INDUSTRIAL | DLMS Meter | 2.3704 | 2.3868 | 0 | 2.3704 | -0.69357 | -0.69357
4096 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903010104 | F34-KLEN-PACK | INDUSTRIAL | DLMS Meter | 2.374 | 2.3839 | 0 | 2.374 | -0.41617 | -0.41617
4097 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903010105 | F35-NISARGA | URBAN MIXED LOAD | DLMS Meter | 2.0735 | 1.453 | 0.514 | 1.5595 | 6.8327 | 8.1936
4098 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903010106 | F36-KOPPA | URBAN MIXED LOAD | DLMS Meter | 1.5983 | 1.3848 | 0.1 | 1.4983 | 7.5754 | 19.1827
4099 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903010107 | F37-KIRLOSKAR-TOYOTO | INDUSTRIAL | DLMS Meter | 4.7001 | 4.134 | 0.2202 | 4.4799 | 7.7207 | 8.4123
4100 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903020302 | F40-VINORAM | INDUSTRIAL | DLMS Meter | 7.454 | 7.1715 | 0 | 7.454 | 3.7902 | 4.1574
4101 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903020303 | F41-AMBEDKAR INDUSTRIAL AREA-2 | INDUSTRIAL | DLMS Meter | 4.1346 | 3.8858 | 0.02 | 4.1146 | 5.5606 | 5.5606
4102 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903020304 | F42-TATA-ADVANCE | INDUSTRIAL | DLMS Meter | 3.722 | 3.5811 | 0 | 3.722 | 3.7857 | 3.7929
4103 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903020305 | F43-DELPHI | INDUSTRIAL | DLMS Meter | 3.9628 | 3.7067 | 0.1766 | 3.7862 | 2.0987 | 2.2054
4104 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903020306 | F44-HIKAL | INDUSTRIAL | DLMS Meter | 6.9601 | 6.9123 | 0 | 6.9601 | 0.6872 | 0.77326
4105 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903020307 | F45-JADE-MURTHY | AGRI | DLMS Meter | 0.10182 | 0.091665 | 0 | 0.10182 | 9.9735 | 9.9735
4106 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903020308 | F46-ANAND SWEETS | URBAN MIXED LOAD | DLMS Meter | 3.6152 | 3.4534 | 0 | 3.6152 | 4.4745 | 4.9897
4107 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903020309 | F47-VAKIL-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0.65919 | 0.61991 | 0 | 0.65919 | 5.9588 | 8.2509
4108 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903010108 | F48-LAPP-CABLE | INDUSTRIAL | DLMS Meter | 3.7273 | 0.93653 | 2.8152 | 0.9121 | -2.6779 | -2.6779
4109 | BRAZ | RAMANAGAR | CHANDAPURA | JIGANI | NEW JIGANI_66 | 1220204903010112 | F49-MYLAN | INDUSTRIAL | DLMS Meter | 4.3476 | 0 | 4.3476 | 0 | 0 | #DIV/0!
4110 | BMANZ | EAST | INDIRA NAGAR | E10 | NGEF_66 | 1130205901020301 | F01-BN-PURA | URBAN MIXED LOAD | DLMS Meter | 2.6569 | 2.3582 | 0.12086 | 2.536 | 7.0124 | 8.4915
4111 | BMANZ | EAST | INDIRA NAGAR | E10 | NGEF_66 | 1130205901010101 | F02-DRDO | URBAN MIXED LOAD | DLMS Meter | 4.4219 | 3.645 | 0.43707 | 3.9848 | 8.5265 | 10.2695
4112 | BMANZ | EAST | INDIRA NAGAR | E6 | NGEF_66 | 1130205901010102 | F03-RMU | HOSPITAL | DLMS Meter | 2.889 | 2.6083 | 0.15261 | 2.7364 | 4.6815 | 9.3487
4113 | BMANZ | EAST | INDIRA NAGAR | E6 | NGEF_66 | 1130205901010103 | F04-RMU | HOSPITAL | DLMS Meter | 2.79 | 2.2122 | 0.46581 | 2.3242 | 4.8194 | 6.0582
4114 | BMANZ | EAST | INDIRA NAGAR | E10 | NGEF_66 | 1130205901010104 | F05-OM-ROAD | URBAN MIXED LOAD | DLMS Meter | 1.9297 | 1.4183 | 0.40914 | 1.5206 | 6.7231 | 12.2331
4115 | BMANZ | EAST | INDIRA NAGAR | E3 | NGEF_66 | 1130205901010107 | F06-CANARA BANK | URBAN MIXED LOAD | DLMS Meter | 2.1986 | 2.1145 | 0 | 2.1986 | 3.8254 | 3.8254
4116 | BMANZ | EAST | INDIRA NAGAR | E10 | NGEF_66 | 1130205901020302 | F08-UDAYANAGAR | URBAN MIXED LOAD | DLMS Meter | 4.8587 | 4.4206 | 0.21424 | 4.6444 | 4.82 | 8.1982
4117 | BMANZ | EAST | INDIRA NAGAR | E10 | NGEF_66 | 1130205901020303 | F10-NGEF-FEEDER | URBAN MIXED LOAD | DLMS Meter | 5.7243 | 5.3169 | 0 | 5.7243 | 7.1172 | 10.8419
4118 | BMANZ | EAST | INDIRA NAGAR | E10 | NGEF_66 | 1130205901010201 | F11-BYRASANDRA | URBAN MIXED LOAD | DLMS Meter | 2.1102 | 1.2806 | 0.72165 | 1.3886 | 7.7755 | 12.7624
4119 | BMANZ | EAST | INDIRA NAGAR | E6 | NGEF_66 | 1130205901010202 | F12-CMH-ROAD | URBAN MIXED LOAD | DLMS Meter | 5.5112 | 5.2366 | 0 | 5.5112 | 4.9825 | 6.213
4120 | BMANZ | EAST | INDIRA NAGAR | E3 | NGEF_66 | 1130205901010203 | F13-PHILIPS-RMU | COMMERCIAL | DLMS Meter | 2.6824 | 1.492 | 1.1599 | 1.5225 | 2.0069 | 2.0069
4121 | BMANZ | EAST | INDIRA NAGAR | E3 | NGEF_66 | 1130205901020401 | F14-HEALTH-OFFICE--RMU | URBAN MIXED LOAD | DLMS Meter | 3.7911 | 2.1869 | 1.453 | 2.3381 | 6.465 | 11.6474
4122 | BMANZ | EAST | INDIRA NAGAR | E10 | NGEF_66 | 1130205901020402 | F15-RMZ | COMMERCIAL | DLMS Meter | 3.6632 | 3.6164 | 0 | 3.6632 | 1.2766 | 1.2766
4123 | BMANZ | EAST | INDIRA NAGAR | E10 | NGEF_66 | 1130205901020403 | F16-SALARPURIA-NOVA | URBAN MIXED LOAD | DLMS Meter | 5.0307 | 4.5984 | 0.12831 | 4.9024 | 6.2017 | 6.9577
4124 | BMANZ | EAST | INDIRA NAGAR | E10 | NGEF_66 | 1130205901020404 | F17-AFNHBI | URBAN MIXED LOAD | DLMS Meter | 2.3259 | 2.1411 | 0.031303 | 2.2946 | 6.6905 | 9.325
4125 | BMANZ | EAST | INDIRA NAGAR | E10 | NGEF_66 | 1130205901010204 | F18-AFNHBII | DOMESTIC | DLMS Meter | 0.38023 | 0.35231 | 0 | 0.38023 | 7.3444 | 7.3444
4126 | BMANZ | EAST | SHIVAJINAGAR | E5 | NGEF_66 | 1130205901010205 | F19-SMVB RAILWAY STATION | COMMERCIAL | DLMS Meter | 0.32552 | 0.32187 | 0 | 0.32552 | 1.121 | 4.849
4127 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | NIDASALE_66 | 1320109907010201 | F01-HUNUGANAHALLI | AGRI | DLMS Meter | 0.7525 | 0.67724 | 0 | 0.7525 | 10.0011 | 10.0011
4128 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | NIDASALE_66 | 1320109907010202 | F02-SHIVANAHALLI NJY | NJY | DLMS Meter | 0.76034 | 0.69984 | 0 | 0.76034 | 7.9571 | 66.4265
4129 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | NIDASALE_66 | 1320109907010203 | F03-YKR | AGRI | DLMS Meter | 0.747 | 0.67222 | 0 | 0.747 | 10.0112 | 10.0112
4130 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | NIDASALE_66 | 1320109907010204 | F04-HITHLAPURA | AGRI | DLMS Meter | 0.71936 | 0.64731 | 0 | 0.71936 | 10.0163 | 10.0163
4131 | BMASZ | SOUTH | JAYANAGAR | S1 | NIMHANS_66 | 1110101902010101 | F02-WILSON-MANOR | URBAN MIXED LOAD | DLMS Meter | 1.6112 | 0.9716 | 0.53415 | 1.077 | 9.7894 | 9.7894
4132 | BMASZ | SOUTH | JAYANAGAR | S1 | NIMHANS_66 | 1110101902010102 | F03-NIMHANS-RMU | URBAN MIXED LOAD | DLMS Meter | 1.9391 | 1.663 | 0.092 | 1.8471 | 9.9647 | 15.687
4133 | BMASZ | SOUTH | JAYANAGAR | S1 | NIMHANS_66 | 1110101902010103 | F04-RBI-RMU | HOSPITAL | DLMS Meter | 3.7524 | 3.1958 | 0.287 | 3.4654 | 7.7808 | 10.684
4134 | BMASZ | SOUTH | JAYANAGAR | S1 | NIMHANS_66 | 1110101902010104 | F05-JAYANAGARII | URBAN MIXED LOAD | DLMS Meter | 3.2888 | 3.0169 | 0 | 3.2888 | 8.2688 | 8.9064
4135 | BMASZ | SOUTH | JAYANAGAR | S1 | NIMHANS_66 | 1110101902010105 | F06-MANTHRI-GARDEN | URBAN MIXED LOAD | DLMS Meter | 0.80159 | 0.6509 | 0.0927 | 0.70889 | 8.1802 | 8.7558
4136 | BMASZ | SOUTH | KORAMANGALA | S16 | NIMHANS_66 | 1110101902010301 | F07-IBM-ST-BLOCK | URBAN MIXED LOAD | DLMS Meter | 1.5573 | 1.4891 | 0 | 1.5573 | 4.3781 | 4.3781
4137 | BMASZ | SOUTH | KORAMANGALA | S16 | NIMHANS_66 | 1110101902020301 | F08-ACCENTURE | URBAN MIXED LOAD | DLMS Meter | 3.1942 | 3.0263 | 0.125 | 3.0692 | 1.4004 | 1.4004
4138 | BMASZ | WEST | RR NAGAR | W2 | NIMHANS_66 | 1110101902020302 | F09-MMK-PARK-RMU | URBAN MIXED LOAD | DLMS Meter | 2.2127 | 2.0015 | 0.1126 | 2.1001 | 4.6967 | 11.4785
4139 | BMASZ | SOUTH | JAYANAGAR | S1 | NIMHANS_66 | 1110101902010106 | F12-IBC-PARK-KNOWLEDGE | URBAN MIXED LOAD | DLMS Meter | 1.0519 | 0.70138 | 0.3185 | 0.7334 | 4.3656 | 9.1482
4140 | BMASZ | SOUTH | JAYANAGAR | S2 | NIMHANS_66 | 1110101902010107 | F13-GARUDA-SWAGATH | URBAN MIXED LOAD | DLMS Meter | 2.3253 | 2.2303 | 0 | 2.3253 | 4.0836 | 5.1101
4141 | BMASZ | SOUTH | JAYANAGAR | S1 | NIMHANS_66 | 1110101902010109 | F15-KIDWAI-HOSPITAL | HOSPITAL | DLMS Meter | 1.402 | 1.3729 | 0 | 1.402 | 2.0689 | 2.0689
4142 | BMASZ | SOUTH | JAYANAGAR | S1 | NIMHANS_66 | 1110101902010201 | F16- BMRCL | RAILWAYS OR METRO | DLMS Meter | 1.9643 | 1.9166 | 0 | 1.9643 | 2.4251 | 2.5105
4143 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902020101 | F01-NITRAHALLI | AGRI | DLMS Meter | 0.8346 | 0.7511 | 0 | 0.8346 | 10.0052 | 10.0052
4144 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902020102 | F02-ARSAPURA | AGRI | DLMS Meter | 1.4252 | 1.2799 | 0 | 1.4252 | 10.1952 | 10.1952
4145 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902020103 | F03-KONDAVADI | AGRI | DLMS Meter | 0.82188 | 0.7397 | 0 | 0.82188 | 9.9989 | 9.9989
4146 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902020104 | F04-AKKIRAMPURA | AGRI | DLMS Meter | 1.7796 | 1.6013 | 0 | 1.7796 | 10.0165 | 10.0165
4147 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902010301 | F05-BYALYA | AGRI | DLMS Meter | 0.73168 | 0.65888 | 0 | 0.73168 | 9.9494 | 9.9494
4148 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902020301 | F06-BYRENAHALLI | NJY | DLMS Meter | 1.5762 | 0.74849 | 0.733 | 0.84324 | 11.2369 | 47.1728
4149 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902010302 | F07-TAGIHALLI | AGRI | DLMS Meter | 0.37756 | 0.33966 | 0 | 0.37756 | 10.0379 | 10.0379
4150 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902010303 | F08-BATTIGERE | AGRI | DLMS Meter | 0.99572 | 0.89578 | 0 | 0.99572 | 10.0366 | 10.0366
4151 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902010304 | F09-SANKAPURA | NJY | DLMS Meter | 0.57589 | 0.51137 | 0 | 0.57589 | 11.204 | 56.2156
4152 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902010305 | F10-BADACHOWDANAHALLI | NJY | DLMS Meter | 0.27183 | 0.24178 | 0 | 0.27183 | 11.0558 | 52.3627
4153 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | NITRAHALLI_66 | 1320304902010306 | F11-HUNSAVADI NJY | NJY | DLMS Meter | 0.2819 | 0.2538 | 0 | 0.2819 | 9.9684 | 61.9057
4154 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903010101 | F01-KODIHALLY | AGRI | DLMS Meter | 1.7131 | 1.4373 | 0.085 | 1.6281 | 11.7179 | 11.7179
4155 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903010102 | F02-YELLAPUR | AGRI | DLMS Meter | 2.2231 | 1.9719 | 0 | 2.2231 | 11.2993 | 11.2993
4156 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903010103 | F03-SAGARANAHALLY | AGRI | DLMS Meter | 1.6564 | 1.4908 | 0 | 1.6564 | 9.9925 | 9.9925
4157 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903010104 | F04-MARASHATTIHALLI | AGRI | DLMS Meter | 2.849 | 1.8759 | 0.73 | 2.119 | 11.4744 | 11.4744
4158 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903010105 | F05-M-N-KOTE | AGRI | DLMS Meter | 1.8428 | 0.68034 | 1.08 | 0.7628 | 10.81 | 10.81
4159 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903020301 | F06-TYAGATUR | AGRI | DLMS Meter | 3.206 | 1.653 | 1.34 | 1.866 | 11.4117 | 11.4117
4160 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903020302 | F07-MATHIGATTA | AGRI | DLMS Meter | 1.5454 | 1.3906 | 0 | 1.5454 | 10.012 | 10.012
4161 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903020303 | F08-HESARALLI | AGRI | DLMS Meter | 1.1009 | 0.99088 | 0 | 1.1009 | 9.9955 | 9.9955
4162 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903020304 | F09-BELVATA | AGRI | DLMS Meter | 1.8254 | 1.0987 | 0.575 | 1.2504 | 12.1354 | 12.1354
4163 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903030501 | F11-BENACHIGERE | AGRI | DLMS Meter | 0.82738 | 0.5532 | 0.205 | 0.62238 | 11.1151 | 15.4991
4164 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903030502 | F12-BANDIHALLY | AGRI | DLMS Meter | 0 | 0.000377 | 0 | 0 | 0 | #DIV/0!
4165 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903030503 | F13-HEMAVATI | AGRI | DLMS Meter | 0.93798 | 0.84403 | 0 | 0.93798 | 10.0164 | 10.0164
4166 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903030504 | F14-RAMPURA | AGRI | DLMS Meter | 0.75422 | 0.67871 | 0 | 0.75422 | 10.0119 | 10.0119
4167 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903030505 | F15-NITTUR | DOMESTIC | DLMS Meter | 1.0498 | 0.77893 | 0.165 | 0.88484 | 11.969 | 25.8625
4168 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903030506 | F16-SOPANALHALLI | NJY | DLMS Meter | 0.58596 | 0.5173 | 0.024 | 0.56196 | 7.9471 | 28.9358
4169 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903030507 | F17-CNNL | LIFT IRRIGATION | DLMS Meter | 0.0021 | 0.00055 | 0.001548 | 0.000552 | 0.36232 | 0.36232
4170 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903010107 | F18-PURA NJY | NJY | DLMS Meter | 0.2138 | 0.19091 | 0.004 | 0.2098 | 9.0047 | 45.0433
4171 | CTAZ | TUMKUR | TUMKUR | NITTUR | NITTUR_220 | 1320107903010108 | F19-BOMMENAHALLY NJY | NJY | DLMS Meter | 0.3927 | 0.35818 | 0 | 0.3927 | 8.7915 | 25.3869
4172 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907010101 | F01-KAIDAALA | RURAL MIXED LOAD | DLMS Meter | 1.8983 | 1.666 | 0 | 1.8983 | 12.237 | 12.237
4173 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907010102 | F02-NELLIKERE | AGRI | DLMS Meter | 0.81514 | 0.68393 | 0.055 | 0.76014 | 10.0263 | 10.0263
4174 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907010103 | F03-GUNGURUMALE | AGRI | DLMS Meter | 0.96078 | 0.86481 | 0 | 0.96078 | 9.9889 | 9.9889
4175 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907010104 | F04-ALBUR | AGRI | DLMS Meter | 0.46308 | 0.41629 | 0 | 0.46308 | 10.1032 | 10.1032
4176 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907020101 | F05-MASAVANAGHATTA | AGRI | DLMS Meter | 0.78628 | 0.66253 | 0.05 | 0.73628 | 10.0167 | 10.0167
4177 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907020301 | F06-RAYASHETTIHALLI | AGRI | DLMS Meter | 0.89044 | 0.80119 | 0 | 0.89044 | 10.0237 | 10.0237
4178 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907020302 | F07-NINAVINAKERE | RURAL MIXED LOAD | DLMS Meter | 2.4316 | 2.1484 | 0 | 2.4316 | 11.6466 | 11.6466
4179 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907020303 | F08-SUGURU | AGRI | DLMS Meter | 0.76546 | 0.58072 | 0.12 | 0.64546 | 10.0297 | 10.0297
4180 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907020304 | F09-NJY-KARIKERE | NJY | DLMS Meter | 0.37824 | 0.32876 | 0.006 | 0.37224 | 11.6796 | 27.1579
4181 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907010105 | F10- BURADEGHATTA | AGRI | DLMS Meter | 0.84866 | 0.76385 | 0 | 0.84866 | 9.9932 | 9.9932
4182 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907020305 | F11-NJY-VENKATAPURA | NJY | DLMS Meter | 0.22232 | 0.15312 | 0.045 | 0.17732 | 13.6482 | 21.6626
4183 | CTAZ | TUMKUR | TIPTUR | TIPTUR | NONAVINAKERE_110 | 1320201907010106 | F12-KODIHALLI | NJY | DLMS Meter | 0.3301 | 0.28955 | 0.003 | 0.3271 | 11.4784 | 24.8972
4184 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901010101 | F01-HARE-RAMA-HARE-KRISHNA | DOMESTIC | DLMS Meter | 0.79742 | 0.77621 | 0 | 0.79742 | 2.6594 | 3.8625
4185 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901040701 | F02-TH-BLOCK | DOMESTIC | DLMS Meter | 1.1246 | 0.94414 | 0.14392 | 0.98071 | 3.7287 | 6.5436
4186 | BMASZ | WEST | RAJAJINAGAR | N3 | NRS_220 | 1140101901020301 | F03-INDUSTRIAL-TOWN/SHIVANAGARA | URBAN MIXED LOAD | DLMS Meter | 2.3082 | 2.1721 | 0 | 2.3082 | 5.8949 | 8.6846
4187 | BMANZ | NORTH | MALLESHWARA | C1 | NRS_220 | 1140101901050909 | F04-DEVAIAH-PARK | URBAN MIXED LOAD | DLMS Meter | 3.9191 | 3.7246 | 0 | 3.9191 | 4.962 | 7.5427
4188 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901040702 | F05-ST-AND-ND-BLOCK | DOMESTIC | DLMS Meter | 1.8245 | 1.7144 | 0.041812 | 1.7827 | 3.8333 | 6.3189
4189 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901020302 | F06-F--ST-&-ND-BLOCK | DOMESTIC | DLMS Meter | 1.135 | 0.90662 | 0.18318 | 0.95181 | 4.7471 | 5.8633
4190 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901030501 | F08-BHASHYAM-CIRCLE | DOMESTIC | DLMS Meter | 2.9225 | 2.6587 | 0.0755 | 2.847 | 6.6135 | 9.5243
4191 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901030502 | F09-INDUSTRIAL-ESTATE | INDUSTRIAL | DLMS Meter | 3.2959 | 3.0728 | 0.0085 | 3.2874 | 6.5273 | 7.4199
4192 | BMANZ | NORTH | MALLESHWARA | C1 | NRS_220 | 1140101901050901 | F10-SUBRAMANY-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.8151 | 2.4518 | 0.165 | 2.6501 | 7.4835 | 10.2455
4193 | BMANZ | NORTH | MALLESHWARA | C1 | NRS_220 | 1140101901010110 | F11-PRAKASH NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.5385 | 3.0474 | 0.25 | 3.2885 | 7.3312 | 10.6018
4194 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901010501 | F12-DIXIT-RMU-TH-BLOCK | URBAN MIXED LOAD | DLMS Meter | 1.9558 | 1.8493 | 0 | 1.9558 | 5.4481 | 18.0334
4195 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901010502 | F13-TH-BLOCK,-RR-RMU | DOMESTIC | DLMS Meter | 1.3045 | 0.77999 | 0.48501 | 0.81951 | 4.8223 | 9.4015
4196 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901040703 | F14-CHOLURPALYA | DOMESTIC | DLMS Meter | 1.7652 | 1.6016 | 0.064152 | 1.701 | 5.8476 | 15.5292
4197 | BMASZ | WEST | RAJAJINAGAR | N2 | NRS_220 | 1140101901010102 | F15-HOSAHALLY-W/S | HOSPITAL | DLMS Meter | 1.3006 | 1.1483 | 0.072231 | 1.2284 | 6.5203 | 7.3167
4198 | BMASZ | WEST | RAJAJINAGAR | N3 | NRS_220 | 1140101901010503 | F16-BASAWESHWARA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.6248 | 3.3542 | 0 | 3.6248 | 7.4652 | 11.2918
4199 | BMASZ | WEST | RAJAJINAGAR | N3 | NRS_220 | 1140101901020304 | F17-MODI-HOSPITAL/M-NAGARA | URBAN MIXED LOAD | DLMS Meter | 2.1313 | 2.0171 | 0 | 2.1313 | 5.3566 | 8.7517
4200 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901010302 | F19-ND-&TH-BLOCK | DOMESTIC | DLMS Meter | 2.7879 | 2.5673 | 0.065418 | 2.7224 | 5.6973 | 10.7976
4201 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901050902 | F20-ESI | DOMESTIC | DLMS Meter | 3.6048 | 1.3649 | 2.1785 | 1.4263 | 4.3039 | 6.5584
4202 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901040704 | F22-IT&-BT-PARK | COMMERCIAL | DLMS Meter | 1.1225 | 1.1002 | 0 | 1.1225 | 1.9942 | 1.9942
4203 | BMASZ | WEST | RAJAJINAGAR | N3 | NRS_220 | 1140101901050903 | F23-INDUSTRIAL-TOWN-JP-LIGHT | INDUSTRIAL | DLMS Meter | 2.2347 | 2.1059 | 0 | 2.2347 | 5.7601 | 7.3655
4204 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901050904 | F24-KSSIDC | INDUSTRIAL | DLMS Meter | 2.3358 | 1.5336 | 0.71553 | 1.6203 | 5.3491 | 11.822
4205 | BMANZ | NORTH | MALLESHWARA | C1 | NRS_220 | 1140101901050905 | F25-TVS-SUZUKI-SHOW-ROOM | URBAN MIXED LOAD | DLMS Meter | 3.5844 | 3.3059 | 0 | 3.5844 | 7.7699 | 13.5562
4206 | BMANZ | NORTH | MALLESHWARA | C1 | NRS_220 | 1140101901010111 | F26-SAI MANDIRA | URBAN MIXED LOAD | DLMS Meter | 2.4261 | 2.108 | 0.2 | 2.2261 | 5.3036 | 7.2093
4207 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901010103 | F27-RTO-COMPLEX | DOMESTIC | DLMS Meter | 1.7825 | 1.5359 | 0.167 | 1.6155 | 4.9273 | 9.7742
4208 | BMANZ | NORTH | MALLESHWARA | C1 | NRS_220 | 1140101901010104 | F28-BYRAPPA-RMU | URBAN MIXED LOAD | DLMS Meter | 3.4657 | 2.2707 | 1.06 | 2.4057 | 5.6126 | 8.1159
4209 | BMANZ | EAST | VIDHANASOUDHA | W3 | NRS_220 | 1140101901050906 | F29-ST-&-TH-MAIN-MAGADI-ROAD-(MAGADI-ROAD) | INDUSTRIAL | DLMS Meter | 2.8713 | 2.4863 | 0.02 | 2.8513 | 12.802 | 17.9395
4210 | BMANZ | EAST | VIDHANASOUDHA | W3 | NRS_220 | 1140101901050907 | F30-MAIN--MAGADI-ROAD(SIDE-ANAJAN) | URBAN MIXED LOAD | DLMS Meter | 4.8789 | 4.2433 | 0 | 4.8789 | 13.0272 | 26.0232
4211 | BMASZ | WEST | RAJAJINAGAR | N3 | NRS_220 | 1140101901010105 | F31-MODIHOSPITAL-ROAD | URBAN MIXED LOAD | DLMS Meter | 1.2857 | 1.242 | 0 | 1.2857 | 3.3971 | 5.3512
4212 | BMASZ | WEST | RAJAJINAGAR | N3 | NRS_220 | 1140101901010106 | F32-KABBADI-RMU-/INDUSTIAL-TOWN | INDUSTRIAL | DLMS Meter | 3.4604 | 3.2954 | 0 | 3.4604 | 4.7695 | 5.6951
4213 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901050908 | F33-SUMANGALA-PROPERTIES | COMMERCIAL | DLMS Meter | 3.2966 | 1.474 | 1.7677 | 1.5288 | 3.586 | 3.586
4214 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901040705 | F34-ESI-HOSPITAL | HOSPITAL | DLMS Meter | 1.9594 | 1.7915 | 0.09901 | 1.8604 | 3.7011 | 3.7011
4215 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901050910 | F35-GT WORLD MALL | COMMERCIAL | DLMS Meter | 0.84511 | 0.8329 | 0 | 0.84511 | 1.4448 | 10.4423
4216 | BMASZ | WEST | RAJAJINAGAR | N1 | NRS_220 | 1140101901050911 | F36-PALLADIUM | DOMESTIC | DLMS Meter | 1.2884 | 1.2074 | 0.030003 | 1.2584 | 4.0536 | 4.1773
4217 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902010301 | F01-KODIKOPPA | AGRI | DLMS Meter | 0.48066 | 0.43267 | 0 | 0.48066 | 9.9852 | 9.9852
4218 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902010101 | F02-VADERAHATTUR | NJY | DLMS Meter | 0.41366 | 0.31117 | 0.058298 | 0.35536 | 12.4352 | 36.465
4219 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902010103 | F03-KUNKOVA | AGRI | DLMS Meter | 0.93886 | 0.845 | 0 | 0.93886 | 9.9981 | 9.9981
4220 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902010102 | F04-KUDUREKONDA | AGRI | DLMS Meter | 0.6965 | 0.61946 | 0 | 0.6965 | 11.0616 | 11.0616
4221 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902020305 | F05-SALABALU | AGRI | DLMS Meter | 0.7912 | 0.70078 | 0 | 0.7912 | 11.4276 | 11.4276
4222 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902020306 | F06-MADANABAVI | AGRI | DLMS Meter | 0.6451 | 0.58063 | 0 | 0.6451 | 9.9943 | 9.9943
4223 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902020303 | F07-BIJAGATTE | AGRI | DLMS Meter | 1.2944 | 1.1451 | 0 | 1.2944 | 11.5318 | 11.5318
4224 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902020301 | F08-RAMESHWARA | AGRI | DLMS Meter | 0.84589 | 0.73727 | 0 | 0.84589 | 12.8406 | 12.8406
4225 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902020307 | F09-SURAHONNE NJY | NJY | DLMS Meter | 0.56654 | 0.52046 | 0.005122 | 0.56142 | 7.2956 | 14.3873
4226 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902010104 | F10-YARAGANALU NJY | NJY | DLMS Meter | 0.19224 | 0.16057 | 0.008969 | 0.18327 | 12.3884 | 12.3884
4227 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902020304 | F11-GANGANAKOTE | NJY | DLMS Meter | 0.6151 | 0.34301 | 0.22419 | 0.39091 | 12.2543 | 34.7927
4228 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | NYAMATHI_66 | 1310302902020302 | F12-NYAMTHI | NJY | DLMS Meter | 0.61746 | 0.55678 | 0.005184 | 0.61228 | 9.0637 | 12.4318
4229 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | OBAJJIHALLI_66 | 1310103902010101 | F01-ANJANEYA | AGRI | DLMS Meter | 0.85662 | 0.7569 | 0 | 0.85662 | 11.6415 | 11.6415
4230 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | OBAJJIHALLI_66 | 1310103902010102 | F02-ARASAPURA | AGRI | DLMS Meter | 0.74662 | 0.6678 | 0 | 0.74662 | 10.5562 | 10.5562
4231 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | OBAJJIHALLI_66 | 1310103902010103 | F03-MAGANAHALLY | AGRI | DLMS Meter | 0.74168 | 0.65621 | 0 | 0.74168 | 11.524 | 11.524
4232 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | OBAJJIHALLI_66 | 1310103902010104 | F04-OBAJJIHALLI | AGRI | DLMS Meter | 0.8238 | 0.74126 | 0 | 0.8238 | 10.0198 | 10.0198
4233 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | OBAJJIHALLI_66 | 1310103902010105 | F05-WATER-SUPPLY | NJY | DLMS Meter | 0.75103 | 0.4036 | 0.2885 | 0.46253 | 12.7411 | 50.6356
4234 | BMASZ | SOUTH | JAYANAGAR | S9 | PADMANABHANAGAR_66 | 1110105901010101 | F01-BANAGIRI-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.6545 | 2.4533 | 0.07 | 2.5845 | 5.0787 | 6.9733
4235 | BMASZ | SOUTH | JAYANAGAR | S1 | PADMANABHANAGAR_66 | 1110105901010201 | F02-JAYANAGAR | URBAN MIXED LOAD | DLMS Meter | 1.7902 | 1.6715 | 0 | 1.7902 | 6.6329 | 6.6329
4236 | BMASZ | SOUTH | JAYANAGAR | S9 | PADMANABHANAGAR_66 | 1110105901010102 | F03-S9 SUB DIVISION | URBAN MIXED LOAD | DLMS Meter | 3.2711 | 2.5334 | 0.59259 | 2.6786 | 5.4183 | 9.4109
4237 | BMASZ | SOUTH | JAYANAGAR | S9 | PADMANABHANAGAR_66 | 1110105901010103 | F04-BDA-COMPLEX | URBAN MIXED LOAD | DLMS Meter | 2.7948 | 2.2754 | 0.40658 | 2.3882 | 4.7224 | 9.5493
4238 | BMASZ | SOUTH | JAYANAGAR | S9 | PADMANABHANAGAR_66 | 1110105901010104 | F05-9TH-MAIN-BATA-SHOWROOM | URBAN MIXED LOAD | DLMS Meter | 5.3203 | 4.1118 | 0.94069 | 4.3796 | 6.1142 | 10.9645
4239 | BMASZ | SOUTH | JAYANAGAR | S9 | PADMANABHANAGAR_66 | 1110105901020301 | F07-CHANNAMMANA KERE | URBAN MIXED LOAD | DLMS Meter | 1.5826 | 1.5042 | 0.00492 | 1.5777 | 4.6556 | 10.4864
4240 | BMASZ | SOUTH | JAYANAGAR | S9 | PADMANABHANAGAR_66 | 1110105901020302 | F08-RAJIV-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.7564 | 2.6324 | 0 | 2.7564 | 4.4982 | 5.4245
4241 | BMASZ | SOUTH | JAYANAGAR | S9 | PADMANABHANAGAR_66 | 1110105901020303 | F09-PADMANABHANAGAR | URBAN MIXED LOAD | DLMS Meter | 4.0353 | 3.7924 | 0 | 4.0353 | 6.0203 | 8.2178
4242 | BMASZ | WEST | RR NAGAR | W8 | PADMANABHANAGAR_66 | 1110105901010105 | F12-SHASTRI-NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.6926 | 3.4699 | 0.02065 | 3.672 | 5.5026 | 12.8421
4243 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903010101 | F01-KAMALAPURA | AGRI | DLMS Meter | 0.7515 | 0.67637 | 0 | 0.7515 | 9.9967 | 9.9967
4244 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903010102 | F02-ASAGODU | AGRI | DLMS Meter | 0.8708 | 0.78376 | 0 | 0.8708 | 9.9953 | 9.9953
4245 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903010103 | F03-BASAVANAKOTE | AGRI | DLMS Meter | 0.96109 | 0.86494 | 0 | 0.96109 | 10.0041 | 10.0041
4246 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903010104 | F04-HOSADURGA | AGRI | DLMS Meter | 0.93062 | 0.81532 | 0 | 0.93062 | 12.3899 | 12.3899
4247 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903020301 | F05-KATENHALLI | AGRI | DLMS Meter | 0.71718 | 0.6456 | 0 | 0.71718 | 9.9813 | 9.9813
4248 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903020302 | F06-KODADHAGUDDA | AGRI | DLMS Meter | 0.8074 | 0.70747 | 0 | 0.8074 | 12.3768 | 12.3768
4249 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903020303 | F07-MADRAHALLI | AGRI | DLMS Meter | 1.0189 | 0.89315 | 0 | 1.0189 | 12.3404 | 12.3404
4250 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903030501 | F08-THUPPADAHALLI NJY | NJY | DLMS Meter | 0.68452 | 0.43089 | 0.1921 | 0.49242 | 12.4954 | 44.7754
4251 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903030502 | F09-AYYANAHALLI | NJY | DLMS Meter | 0.8247 | 0.36939 | 0.40332 | 0.42138 | 12.3379 | 61.8401
4252 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903030503 | F10-PALLAGATTE | NJY | DLMS Meter | 0.48908 | 0.30491 | 0.14516 | 0.34392 | 11.3423 | 31.1185
4253 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | PALLAGATTE_66 | 1310105903030504 | F11-BASAVAPURA | AGRI | DLMS Meter | 0.67309 | 0.58931 | 0 | 0.67309 | 12.4475 | 12.4475
4254 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | PALLICHERLU_66 | 1230404907010204 | F01-KUTHANDAHALLI | AGRI | DLMS Meter | 0.69758 | 0.62785 | 0 | 0.69758 | 9.9962 | 9.9962
4255 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | PALLICHERLU_66 | 1230404907010201 | F02-SADDAHALLI | AGRI | DLMS Meter | 1.175 | 0.7168 | 0.37859 | 0.79641 | 9.9958 | 9.9958
4256 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | PALLICHERLU_66 | 1230404907010202 | F03-MARIHALLI | AGRI | DLMS Meter | 1.0745 | 0.96686 | 0 | 1.0745 | 10.0178 | 10.0178
4257 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | PALLICHERLU_66 | 1230404907010203 | F04-CHOWDAREDDYAHALLI NJY | NJY | DLMS Meter | 0.44195 | 0.38854 | 0 | 0.44195 | 12.0866 | 66.165
4258 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | PALLICHERLU_66 | 1230404907010205 | F06-KOTAHALLI | AGRI | DLMS Meter | 1.2535 | 1.0564 | 0.08 | 1.1735 | 9.981 | 9.981
4259 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | PALLICHERLU_66 | 1230404907010206 | F07-SIDDAPURA | AGRI | DLMS Meter | 0.44085 | 0.38669 | 0 | 0.44085 | 12.2864 | 12.2864
4260 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905010101 | F01-ANNEHAL | AGRI | DLMS Meter | 1.6393 | 1.2791 | 0.17598 | 1.4633 | 12.5889 | 12.5889
4261 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905010102 | F02-(A)HULLUR NJY | NJY | DLMS Meter | 0.88894 | 0.64499 | 0.14601 | 0.74293 | 13.1829 | 47.9662
4262 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905010104 | F03-PANDRAHALLI-KAVALAHATTI | AGRI | DLMS Meter | 0.65695 | 0.58523 | 0 | 0.65695 | 10.9174 | 10.9174
4263 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905010105 | F04-JANAKONDA | AGRI | DLMS Meter | 1.4313 | 1.0678 | 0.21544 | 1.2158 | 12.1714 | 12.1714
4264 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905010106 | F05-(A)SIDDAPURA | AGRI | DLMS Meter | 0.99402 | 0.86895 | 0 | 0.99402 | 12.5817 | 12.5817
4265 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905020301 | F06-GODABANAL | AGRI | DLMS Meter | 1.3905 | 1.2088 | 0 | 1.3905 | 13.062 | 13.062
4266 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905020302 | F07-SONDEKOLA | AGRI | DLMS Meter | 2.4124 | 1.6124 | 0.56214 | 1.8502 | 12.8524 | 12.8524
4267 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905020303 | F08-SOLLAPURA NJY | NJY | DLMS Meter | 1.7446 | 1.1327 | 0.43741 | 1.3072 | 13.3453 | 35.4913
4268 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905020304 | F09-KURUBARAHALLI | AGRI | DLMS Meter | 1.5593 | 1.2167 | 0.19869 | 1.3606 | 10.579 | 10.579
4269 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905020305 | F10-BETTADANAGENAHALLI | AGRI | DLMS Meter | 0.90035 | 0.80983 | 0.002422 | 0.89793 | 9.8113 | 9.8113
4270 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905020306 | F11-B-MAHADEVANAKATTE | AGRI | DLMS Meter | 2.5547 | 2.2994 | 0 | 2.5547 | 9.9904 | 9.9904
4271 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905020307 | F11-SINGAPURA | AGRI | DLMS Meter | 1.9913 | 0.88294 | 1.0236 | 0.96772 | 8.7607 | 8.7607
4272 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | PANDARAHALLI_66 | 1310202905010103 | F13-KAKKERU NJY | NJY | DLMS Meter | 2.0258 | 0.73495 | 1.1839 | 0.84186 | 12.6997 | 42.7284
4273 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | PATHAPALYA_66 | 1230305906010101 | F01-NEERAGANTIPALLI | AGRI | DLMS Meter | 0.87788 | 0.58741 | 0.225 | 0.65288 | 10.0276 | 10.0276
4274 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | PATHAPALYA_66 | 1230305906010102 | F02-BALAREDDYPALLI | AGRI | DLMS Meter | 0.9392 | 0.84514 | 0 | 0.9392 | 10.0145 | 10.0145
4275 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | PATHAPALYA_66 | 1230305906010103 | F04-DEVARAJAPALLI | NJY | DLMS Meter | 0.75392 | 0.60936 | 0.0605 | 0.69342 | 12.1222 | 70.1074
4276 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | PATHAPALYA_66 | 1230305906010104 | F05-PATHAPALYA | AGRI | DLMS Meter | 1.1376 | 1.024 | 0 | 1.1376 | 9.9838 | 9.9838
4277 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | PATHAPALYA_66 | 1230305906010106 | F06-GUDIPALLI | AGRI | DLMS Meter | 0.93172 | 0.83841 | 0 | 0.93172 | 10.0152 | 10.0976
4278 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901010101 | F01-HULIGERE | AGRI | DLMS Meter | 1.1814 | 1.0154 | 0.028328 | 1.1531 | 11.9402 | 11.9402
4279 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901010102 | F02-HUCCHAGIRANAHALLI | AGRI | DLMS Meter | 1.286 | 1.1134 | 0 | 1.286 | 13.4178 | 13.4178
4280 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901010103 | F03-RANGAPURA | AGRI | DLMS Meter | 0.6372 | 0.55682 | 0.003607 | 0.63359 | 12.1177 | 12.1177
4281 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901010104 | F04-KYADIGUNTE | AGRI | DLMS Meter | 0.6718 | 0.60471 | 0 | 0.6718 | 9.9872 | 9.9872
4282 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901020301 | F05-NADUR | AGRI | DLMS Meter | 1.0002 | 0.87886 | 0 | 1.0002 | 12.132 | 12.132
4283 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901010105 | F06-KALLAHALLI | AGRI | DLMS Meter | 1.073 | 0.80777 | 0.14135 | 0.93165 | 13.2969 | 13.2969
4284 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901020302 | F07-P-M-HALLI | AGRI | DLMS Meter | 0.9026 | 0.81227 | 0 | 0.9026 | 10.0073 | 10.0073
4285 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901020303 | F08-KEREYAGALAHALLI | AGRI | DLMS Meter | 1.3416 | 1.0821 | 0.092063 | 1.2495 | 13.3969 | 13.3969
4286 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901020304 | F09-SIDDANAHALLI-NJY | NJY | DLMS Meter | 0.6488 | 0.58144 | 0 | 0.6488 | 10.382 | 57.4774
4287 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901020305 | F10-RAGALAHALLI-NJY | NJY | DLMS Meter | 0.6256 | 0.56079 | 0 | 0.6256 | 10.3599 | 77.2025
4288 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | PATTANAYAKANAHALLI_66 | 1320302901020306 | F11-MELKUNTE-NJY | NJY | DLMS Meter | 0.5786 | 0.5226 | 0 | 0.5786 | 9.6781 | 63.3902
4289 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_220 | 1320306908010101 | F01-NALIGANAHALLY | AGRI | DLMS Meter | 0.3498 | 0.31481 | 0 | 0.3498 | 10.0034 | 10.0034
4290 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_220 | 1320306908010102 | F02-ARLAHALLY | AGRI | DLMS Meter | 0.4494 | 0.40439 | 0 | 0.4494 | 10.016 | 10.016
4291 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_220 | 1320306908010103 | F03-DODDAHATTI NJY | NJY | DLMS Meter | 0.2444 | 0.22169 | 0 | 0.2444 | 9.2924 | 48.2382
4292 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_220 | 1320306908010104 | F04-SINGAREDDYHALLY | AGRI | DLMS Meter | 0.7768 | 0.70515 | 0 | 0.7768 | 9.2237 | 9.2237
4293 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902010301 | F01-PAVAGADA | URBAN MIXED LOAD | DLMS Meter | 4.3191 | 3.7844 | 0.025 | 4.2941 | 11.8692 | 11.8692
4294 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902010302 | F02-C.K.PURA | AGRI | DLMS Meter | 1.5192 | 1.3674 | 0 | 1.5192 | 9.9934 | 9.9934
4295 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902010303 | F03-GANGASAGARA | AGRI | DLMS Meter | 0.18978 | 0.17068 | 0 | 0.18978 | 10.0638 | 13.4182
4296 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902020101 | F04-BOMMATHALAHALLY | AGRI | DLMS Meter | 0.4842 | 0.43582 | 0 | 0.4842 | 9.9917 | 9.9917
4297 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902020102 | F05-NEELAMMANAHALLY | AGRI | DLMS Meter | 0.63248 | 0.56937 | 0 | 0.63248 | 9.9783 | 9.9783
4298 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902020103 | F06-RAJAVANTI | AGRI | DLMS Meter | 1.063 | 0.96094 | 0 | 1.063 | 9.5993 | 9.5993
4299 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902020104 | F07-PALLAVALLI | AGRI | DLMS Meter | 1.0813 | 0.97079 | 0 | 1.0813 | 10.2164 | 10.4305
4300 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902010106 | F08-BYRAPURA | AGRI | DLMS Meter | 0.97692 | 0.87922 | 0 | 0.97692 | 10.0006 | 10.892
4301 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902010104 | F09-BYADNUR NJY | NJY | DLMS Meter | 0.4477 | 0.40109 | 0 | 0.4477 | 10.4119 | 71.9533
4302 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902010105 | F10-BUDDAREDDY HALLI NJY | NJY | DLMS Meter | 0.4961 | 0.4464 | 0 | 0.4961 | 10.0184 | 76.9231
4303 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902010103 | F11-NJY PONNASAMUDRA | NJY | DLMS Meter | 0.7943 | 0.71024 | 0 | 0.7943 | 10.5827 | 74.4362
4304 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | PAVAGADA_66 | 1320306902010107 | F12-KHB COLONY | DOMESTIC | DLMS Meter | 0.0532 | 0.04885 | 0 | 0.0532 | 8.1767 | 8.1767
4305 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | PD KOTE_66 | 1310401908010107 | F01-KARIDASARAHALLI | AGRI | DLMS Meter | 0.2557 | 0.22336 | 0 | 0.2557 | 12.6474 | 12.6474
4306 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | PD KOTE_66 | 1310401908010102 | F02-PD-KOTE | AGRI | DLMS Meter | 0.78436 | 0.70572 | 0 | 0.78436 | 10.0258 | 10.0258
4307 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | PD KOTE_66 | 1310401908010103 | F03-BEJJIHALLI | AGRI | DLMS Meter | 1.1522 | 1.0079 | 0 | 1.1522 | 12.5293 | 12.5293
4308 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | PD KOTE_66 | 1310401908010104 | F04-CHIRTHAHALLI | AGRI | DLMS Meter | 1.2435 | 1.1193 | 0 | 1.2435 | 9.9895 | 9.9895
4309 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | PD KOTE_66 | 1310401908010105 | F05-HALAGALADDI NJY | NJY | DLMS Meter | 0.5575 | 0.50719 | 0 | 0.5575 | 9.0239 | 69.3691
4310 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | PD KOTE_66 | 1310401908010108 | F07-BASAVESHWARA | AGRI | DLMS Meter | 0.3044 | 0.27399 | 0 | 0.3044 | 9.9905 | 9.9905
4311 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | PD KOTE_66 | 1310401908010106 | F08-ESHWARA | AGRI | DLMS Meter | 0.8538 | 0.76783 | 0 | 0.8538 | 10.0688 | 10.0688
4312 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | PD KOTE_66 | 1310401908010101 | F09-MADDIHALLY | AGRI | DLMS Meter | 1.0752 | 0.96497 | 0 | 1.0752 | 10.2516 | 10.2516
4313 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901010101 | F01-PYLAGURKI | AGRI | DLMS Meter | 1.7643 | 1.5388 | 0.054222 | 1.7101 | 10.0154 | 10.0154
4314 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901010102 | F02-VARLAKONDA | AGRI | DLMS Meter | 1.0331 | 0.92962 | 0 | 1.0331 | 10.0145 | 10.0145
4315 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901010103 | F03-PERESANDRA | AGRI | DLMS Meter | 1.5704 | 1.2886 | 0.13849 | 1.4319 | 10.0058 | 10.0058
4316 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901010104 | F04-MANDIKAL-OLD | AGRI | DLMS Meter | 0.35002 | 0.31502 | 0 | 0.35002 | 10.0006 | 10.0006
4317 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901010105 | F05-KNR | INDUSTRIAL | DLMS Meter | 2.5822 | 2.5019 | 0 | 2.5822 | 3.112 | 7.032
4318 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901020301 | F08-BOGAPARTHY | AGRI | DLMS Meter | 0.96622 | 0.82884 | 0.045293 | 0.92093 | 9.9989 | 9.9989
4319 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901020302 | F09-CBPURA-EXPRESS | AGRI | DLMS Meter | 0.97972 | 0.47979 | 0.44627 | 0.53345 | 10.0594 | 10.0594
4320 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901020303 | F10-MANDIKAL-EXPRESS | AGRI | DLMS Meter | 0.67982 | 0.61165 | 0 | 0.67982 | 10.0272 | 10.0272
4321 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901020304 | F11-SADALI | AGRI | DLMS Meter | 1.6424 | 1.4783 | 0 | 1.6424 | 9.9917 | 9.9917
4322 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901010106 | F12-LAXMISAGARA-NJY | NJY | DLMS Meter | 0.90952 | 0.72631 | 0.09206 | 0.81746 | 11.1503 | 52.3107
4323 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901020305 | F13-HARISTHALA-NJY | NJY | DLMS Meter | 1.2582 | 1.023 | 0.10533 | 1.1529 | 11.2605 | 28.4891
4324 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901020306 | F14-CHIKKANAGAVALLI-NJY | NJY | DLMS Meter | 0.5376 | 0.48017 | 0 | 0.5376 | 10.6819 | 25.788
4325 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901020307 | F15-SHETTYGERE | AGRI | DLMS Meter | 1.2048 | 1.0845 | 0 | 1.2048 | 9.9876 | 9.9876
4326 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901020308 | F16-BESTO-MINING | INDUSTRIAL | DLMS Meter | 0.40126 | 0.39635 | 0 | 0.40126 | 1.2236 | 1.2236
4327 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901010108 | F17-YALAGALAHALLI | INDUSTRIAL | DLMS Meter | 1.4175 | 1.3752 | 0 | 1.4175 | 2.9826 | 8.8833
4328 | BRAZ | KOLAR | CHIKKABALLAPURA | CHIKKABALLAPURA RURAL | PERESANDRA_66 | 1230302901020309 | F18-KAMMATHANAHALLI | AGRI | DLMS Meter | 0.82378 | 0.7416 | 0 | 0.82378 | 9.9762 | 9.9762
4329 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904010101 | F01-KURUBARAHALLI | NJY | DLMS Meter | 4.1993 | 3.4729 | 0.18652 | 4.0128 | 13.4547 | 28.4691
4330 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904010102 | F02-ATTIVATTA | AGRI | DLMS Meter | 1.0554 | 0.94961 | 0 | 1.0554 | 10.0233 | 10.0233
4331 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904010103 | F03-VIVEK-AGRO-FOOD | INDUSTRIAL | DLMS Meter | 6.9382 | 6.3404 | 0 | 6.9382 | 8.6157 | 9.1311
4332 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904010104 | F04-INDUSTRIAL-AREA | INDUSTRIAL | DLMS Meter | 3.8555 | 3.3614 | 0.17359 | 3.6819 | 8.7068 | 8.7068
4333 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904010302 | F05 K.SATHYAWARA | NJY | DLMS Meter | 2.8855 | 2.511 | 0 | 2.8855 | 12.9782 | 78.359
4334 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904020301 | F06-MILK-DIARY | INDUSTRIAL | DLMS Meter | 2.8678 | 2.5795 | 0.10135 | 2.7665 | 6.7589 | 6.9151
4335 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904020302 | F07-DODDAHULLURU | AGRI | DLMS Meter | 2.1298 | 1.9164 | 0 | 2.1298 | 10.0186 | 10.0561
4336 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904010301 | F08 KORATI | AGRI | DLMS Meter | 0.92154 | 0.82957 | 0 | 0.92154 | 9.9798 | 9.9798
4337 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904010105 | F09-COURTAULDS-COATING | INDUSTRIAL | DLMS Meter | 1.255 | 1.2264 | 0 | 1.255 | 2.2761 | 2.2761
4338 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904010106 | F10-K-I-A-D-B | INDUSTRIAL | DLMS Meter | 6.2297 | 5.0414 | 0.66337 | 5.5664 | 9.4305 | 9.4305
4339 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904020303 | F11-DAKSHIN-FOUNDRY | INDUSTRIAL | DLMS Meter | 4.8308 | 4.6962 | 0 | 4.8308 | 2.7874 | 2.7874
4340 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904020304 | F12-INDOUS-MIMTECH | INDUSTRIAL | DLMS Meter | 2.7357 | 2.7083 | 0 | 2.7357 | 1.0041 | 1.0041
4341 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904020305 | F13-AKZONOBEL | INDUSTRIAL | DLMS Meter | 1.4233 | 1.4133 | 0 | 1.4233 | 0.70399 | 0.70399
4342 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | PILAGUMPA_66 | 1210201904020306 | F14-PILLAGUMPA | INDUSTRIAL | DLMS Meter | 2.2369 | 1.9906 | 0 | 2.2369 | 11.0105 | 18.5219
4343 | BMANZ | NORTH | PEENYA | N5 | PLATINUM_CITY_66 | 1120102904010101 | F01-SOUTHREN RAILWAY | URBAN MIXED LOAD | DLMS Meter | 2.9051 | 2.8865 | 0 | 2.9051 | 0.63991 | 0.63991
4344 | BMANZ | NORTH | PEENYA | N5 | PLATINUM_CITY_66 | 1120102904010102 | F02-RAGHAVENDRA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.7175 | 3.1829 | 0.465 | 3.2525 | 2.1383 | 2.1383
4345 | BMANZ | NORTH | PEENYA | N5 | PLATINUM_CITY_66 | 1120102904010103 | F03-PROFFETIONAL CLOTHING | URBAN MIXED LOAD | DLMS Meter | 3.5765 | 2.1608 | 1.352 | 2.2245 | 2.8632 | 3.3634
4346 | BMANZ | NORTH | PEENYA | N5 | PLATINUM_CITY_66 | 1120102904010104 | F04-VAISHNAVI NAKSHATRA | DOMESTIC | DLMS Meter | 1.418 | 0.48057 | 0.929 | 0.48905 | 1.7333 | 2.5737
4347 | BMANZ | NORTH | PEENYA | N5 | PLATINUM_CITY_66 | 1120102904010301 | F05-ISRO LAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.0445 | 0.87461 | 0.14 | 0.9045 | 3.304 | 5.4334
4348 | BMANZ | NORTH | PEENYA | N5 | PLATINUM_CITY_66 | 1120102904010302 | F06-HANUMAN-RMU | URBAN MIXED LOAD | DLMS Meter | 0.89291 | 0.65963 | 0.218 | 0.67491 | 2.2651 | 7.4355
4349 | BMANZ | NORTH | PEENYA | N5 | PLATINUM_CITY_66 | 1120102904010303 | F07- BFW-RMU | URBAN MIXED LOAD | DLMS Meter | 2.5442 | 2.5232 | 0 | 2.5442 | 0.82287 | 2.2838
4350 | BMANZ | EAST | SHIVAJINAGAR | E5 | POTTERYROAD_66 | 1130303901010101 | F01-ITI-COOKTOWN | URBAN MIXED LOAD | DLMS Meter | 3.304 | 2.5064 | 0.63207 | 2.6719 | 6.1934 | 20.6645
4351 | BMANZ | EAST | SHIVAJINAGAR | E2 | POTTERYROAD_66 | 1130303901010102 | F02-BSTATION | URBAN MIXED LOAD | DLMS Meter | 2.1148 | 1.9918 | 0.003528 | 2.1113 | 5.6587 | 11.8501
4352 | BMANZ | EAST | SHIVAJINAGAR | E1 | POTTERYROAD_66 | 1130303901010104 | F04-RMU-PC | URBAN MIXED LOAD | DLMS Meter | 4.5622 | 4.125 | 0 | 4.5622 | 9.5829 | 20.2959
4353 | BMANZ | EAST | SHIVAJINAGAR | E5 | POTTERYROAD_66 | 1130303901010105 | F05-CHANDRA-SHEKHAR-SPEECH-&-HEARING | URBAN MIXED LOAD | DLMS Meter | 4.3198 | 3.125 | 0.97622 | 3.3436 | 6.5373 | 17.2075
4354 | BMANZ | EAST | SHIVAJINAGAR | E1 | POTTERYROAD_66 | 1130303901010106 | F06-F-FRAZER-TOWN | URBAN MIXED LOAD | DLMS Meter | 2.9345 | 2.2368 | 0.43438 | 2.5001 | 10.5322 | 16.1954
4355 | BMANZ | EAST | SHIVAJINAGAR | E5 | POTTERYROAD_66 | 1130303901020301 | F07-F-TELECOM | URBAN MIXED LOAD | DLMS Meter | 5.341 | 4.9928 | 0 | 5.341 | 6.5209 | 11.022
4356 | BMANZ | EAST | SHIVAJINAGAR | E5 | POTTERYROAD_66 | 1130303901020302 | F08-RMU-C--COOK-TOWN | URBAN MIXED LOAD | DLMS Meter | 3.0111 | 1.0722 | 1.8775 | 1.1336 | 5.4167 | 12.6091
4357 | BMANZ | EAST | SHIVAJINAGAR | E1 | POTTERYROAD_66 | 1130303901020303 | F09-VGP-RMU | URBAN MIXED LOAD | DLMS Meter | 3.8018 | 3.5412 | 0 | 3.8018 | 6.8563 | 9.4812
4358 | BMANZ | EAST | SHIVAJINAGAR | E5 | POTTERYROAD_66 | 1130303901020304 | F10-L-R-PURAM | URBAN MIXED LOAD | DLMS Meter | 4.9513 | 2.8438 | 1.9392 | 3.0121 | 5.5883 | 17.3906
4359 | BMANZ | EAST | SHIVAJINAGAR | E1 | POTTERYROAD_66 | 1130303901020305 | F11-RMU-C--FRAZERB-TOWN | URBAN MIXED LOAD | DLMS Meter | 2.6335 | 1.2998 | 1.2112 | 1.4222 | 8.6092 | 13.5401
4360 | BMANZ | EAST | SHIVAJINAGAR | E1 | POTTERYROAD_66 | 1130303901020306 | F12-VENKATESHPURA | URBAN MIXED LOAD | DLMS Meter | 4.882 | 3.6972 | 0.795 | 4.087 | 9.537 | 20.4889
4361 | BMANZ | EAST | SHIVAJINAGAR | E5 | POTTERYROAD_66 | 1130303901020307 | F13-PURVANKARA--APARTMENT | URBAN MIXED LOAD | DLMS Meter | 3.2358 | 3.0305 | 0.017671 | 3.2181 | 5.8315 | 14.7255
4362 | BMANZ | EAST | SHIVAJINAGAR | E1 | POTTERYROAD_66 | 1130303901010107 | F14-R-K-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.1845 | 2.8725 | 0 | 3.1845 | 9.7964 | 13.0259
4363 | BMANZ | EAST | SHIVAJINAGAR | E5 | POTTERYROAD_66 | 1130303901020308 | F16-ITC | COMMERCIAL | DLMS Meter | 2.549 | 2.1887 | 0.17418 | 2.3748 | 7.835 | 13.0091
4364 | BMASZ | SOUTH | KORAMANGALA | S7 | PRIMAL_66 | 1110203908010201 | F01-12TH BLOCK | COMMERCIAL | DLMS Meter | 2.0151 | 1.8763 | 0.15 | 1.8651 | -0.59972 | 9.2443
4365 | BMASZ | SOUTH | KORAMANGALA | S7 | PRIMAL_66 | 1110203908010202 | F02-10TH BLOCK | COMMERCIAL | DLMS Meter | 2.7983 | 2.8178 | 0 | 2.7983 | -0.69696 | 0.020548
4366 | BMASZ | SOUTH | KORAMANGALA | S7 | PRIMAL_66 | 1110203908010203 | F03-7TH BLOCK | COMMERCIAL | DLMS Meter | 3.2858 | 3.3208 | 0 | 3.2858 | -1.0646 | -0.55438
4367 | BMASZ | SOUTH | HSR | S11 | PRIMAL_66 | 1110203908010204 | F04-RGA INFRASTRUCTURE-1 | URBAN MIXED LOAD | DLMS Meter | 3.0397 | 0.393 | 2.625 | 0.41472 | 5.237 | 7.9269
4368 | BMASZ | SOUTH | KORAMANGALA | S7 | PRIMAL_66 | 1110203908010205 | F06-INTEL | COMMERCIAL | DLMS Meter | 6.2037 | 6.1875 | 0 | 6.2037 | 0.26086 | 0.97671
4369 | BMASZ | SOUTH | KORAMANGALA | S7 | PRIMAL_66 | 1110203908020201 | F07-UTILITY BLOCK | COMMERCIAL | DLMS Meter | 4.6193 | 4.6304 | 0 | 4.6193 | -0.24072 | 3.8524
4370 | BMASZ | SOUTH | KORAMANGALA | S7 | PRIMAL_66 | 1110203908020202 | F08-9TH B BLOCK | COMMERCIAL | DLMS Meter | 0.81692 | 0.8206 | 0 | 0.81692 | -0.45102 | -0.45102
4371 | BMASZ | SOUTH | KORAMANGALA | S7 | PRIMAL_66 | 1110203908020203 | F09-9TH A BLOCK | COMMERCIAL | DLMS Meter | 1.2525 | 1.262 | 0 | 1.2525 | -0.75883 | -0.75883
4372 | BMASZ | SOUTH | HSR | S11 | PRIMAL_66 | 1110203908020204 | F10-RGA INFRASTRUCTURE-2 | DOMESTIC | DLMS Meter | 4.6085 | 3.4412 | 0.96 | 3.6485 | 5.6811 | 5.6811
4373 | BMASZ | SOUTH | KORAMANGALA | S17 | PRIMAL_66 | 1110203908020206 | F11-SAKRA HOSPITAL ROAD | DOMESTIC | DLMS Meter | 0.7723 | 0.73152 | 0 | 0.7723 | 5.2805 | 5.2805
4374 | BMASZ | SOUTH | HSR | S11 | PRIMAL_66 | 1110203908020205 | F13-PRESTIGE FERNS SQUARE | URBAN MIXED LOAD | DLMS Meter | 2.1318 | 2.1146 | 0 | 2.1318 | 0.80604 | 0.80604
4375 | BMASZ | WEST | KENGERI | K1 | PROVIDENT_66 | 1140301904010101 | F03-PROVIDENT | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4376 | BMASZ | WEST | KENGERI | K1 | PROVIDENT_66 | 1140301904010102 | F04-PROVIDENT | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4377 | BMASZ | WEST | KENGERI | K1 | PROVIDENT_66 | 1140301904010103 | F05-RRHOSPITAL | HOSPITAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4378 | BMASZ | WEST | KENGERI | K1 | PROVIDENT_66 | 1140301904010104 | F06-DODDABELE | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4379 | BMASZ | WEST | KENGERI | K1 | PROVIDENT_66 | 1140301904010105 | F07-PROVIDENT | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4380 | BMASZ | WEST | KENGERI | K1 | PROVIDENT_66 | 1140301904010106 | F08-AUXILLARY | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4381 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902010101 | F01-T.N.KOTE | AGRI | DLMS Meter | 1.3893 | 1.2503 | 0 | 1.3893 | 10.0072 | 10.0072
4382 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902010102 | F02-GOSIKERE | AGRI | DLMS Meter | 0.64848 | 0.58377 | 0 | 0.64848 | 9.9787 | 9.9787
4383 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902010103 | F03-DODDACHELLURU | AGRI | DLMS Meter | 1.5571 | 1.4014 | 0 | 1.5571 | 9.9982 | 9.9982
4384 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902020301 | F04-MAHADEVPURA | AGRI | DLMS Meter | 1.3067 | 1.1762 | 0 | 1.3067 | 9.9849 | 9.9849
4385 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902020101 | F05-P.R.PURATOWN | RURAL MIXED LOAD | DLMS Meter | 0.73854 | 0.66891 | 0 | 0.73854 | 9.4279 | 27.8603
4386 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902010104 | F06-KYADIGUNTE | AGRI | DLMS Meter | 1.3748 | 1.2375 | 0 | 1.3748 | 9.9809 | 9.9809
4387 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902020302 | F07-JAJUR | AGRI | DLMS Meter | 0.84568 | 0.76133 | 0 | 0.84568 | 9.974 | 9.974
4388 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902020303 | F08-KORLAKUNTE | AGRI | DLMS Meter | 0.93008 | 0.81946 | 0 | 0.93008 | 11.8938 | 11.8938
4389 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902010106 | F09-SIDDESWARADURGA NJY | NJY | DLMS Meter | 0.68422 | 0.60058 | 0 | 0.68422 | 12.2248 | 57.4267
4390 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902010107 | F10-D.B.HALLI NJY | NJY | DLMS Meter | 0.62453 | 0.43883 | 0.1264 | 0.49813 | 11.9041 | 52.4597
4391 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902010108 | F12-CHOWLURU | AGRI | DLMS Meter | 0.8586 | 0.75034 | 0 | 0.8586 | 12.6094 | 12.6094
4392 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902010109 | F13-C.B.HALLI | AGRI | DLMS Meter | 0.3659 | 0.32921 | 0 | 0.3659 | 10.0279 | 10.0279
4393 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902020305 | F14-P.GOWRIPURA | AGRI | DLMS Meter | 1.0234 | 0.90935 | 0 | 1.0234 | 11.1441 | 11.1441
4394 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902020304 | F15-HULLIKATTE NJY | NJY | DLMS Meter | 0.8702 | 0.76213 | 0 | 0.8702 | 12.4192 | 56.7139
4395 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | PRPURA_66 | 1310402902020306 | F16-PAGADALABANDE | AGRI | DLMS Meter | 0.7424 | 0.65649 | 0 | 0.7424 | 11.5721 | 11.5721
4396 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | PULAMG_66 | 1320301906010101 | F01-RANTAVALA | AGRI | DLMS Meter | 1.5032 | 1.3528 | 0 | 1.5032 | 10.0051 | 10.0051
4397 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | PULAMG_66 | 1320301906010102 | F02-KOTAGARALAHALLY | AGRI | DLMS Meter | 0.92092 | 0.82866 | 0 | 0.92092 | 10.0181 | 10.0181
4398 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | PULAMG_66 | 1320301906010103 | F03-BASAVANAHALLY | AGRI | DLMS Meter | 1.4145 | 1.2624 | 0 | 1.4145 | 10.7556 | 10.7556
4399 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | PULAMG_66 | 1320301906010105 | F04-SARJAMMANAHALLI NJY | NJY | DLMS Meter | 0.41874 | 0.37307 | 0 | 0.41874 | 10.9056 | 51.6288
4400 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | PULAMG_66 | 1320301906020301 | F05-SHIVANAGERE | AGRI | DLMS Meter | 1.1288 | 1.0159 | 0 | 1.1288 | 9.9982 | 10.08
4401 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | PULAMG_66 | 1320301906020302 | F06-THONACHAGONDANAHALLY | AGRI | DLMS Meter | 0.6091 | 0.54803 | 0 | 0.6091 | 10.0256 | 10.0256
4402 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | PULAMG_66 | 1320301906020303 | F07-KITHAGALI | AGRI | DLMS Meter | 1.0266 | 0.92395 | 0 | 1.0266 | 10.0021 | 10.0021
4403 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | PULAMG_66 | 1320301906010104 | F08-B BETTA | AGRI | DLMS Meter | 1.0235 | 0.92117 | 0 | 1.0235 | 9.9961 | 9.9961
4404 | CTAZ | TUMKUR | MADHUGIRI | MADHUGIRI | PULAMG_66 | 1320301906020304 | F09-BADIGONDANAHALLY NJY | NJY | DLMS Meter | 0.42257 | 0.30865 | 0.085658 | 0.33691 | 8.3871 | 39.8967
4405 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903010101 | F01-HIREMEGALAGERE | AGRI | DLMS Meter | 1.0707 | 0.96397 | 0 | 1.0707 | 9.9719 | 9.9719
4406 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903010102 | F02-KANCHIKERE | AGRI | DLMS Meter | 0.84376 | 0.75911 | 0 | 0.84376 | 10.0331 | 10.0331
4407 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903010103 | F03-KYAKETTE | AGRI | DLMS Meter | 0.94832 | 0.85331 | 0 | 0.94832 | 10.0187 | 10.0187
4408 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903020301 | F04-PUNABHAGHATTA NJY | NJY | DLMS Meter | 2.2882 | 1.3066 | 0.8285 | 1.4597 | 10.4873 | 37.3078
4409 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903010104 | F05-HOSAKOTI | AGRI | DLMS Meter | 1.0993 | 0.98915 | 0 | 1.0993 | 10.0186 | 10.0186
4410 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903020302 | F06-ARASIKERE | AGRI | DLMS Meter | 1.3761 | 1.2454 | 0 | 1.3761 | 9.5 | 9.5
4411 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903020303 | F07-LAXMIPURA | AGRI | DLMS Meter | 1.1675 | 0.85262 | 0.22 | 0.94748 | 10.0115 | 10.0115
4412 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903020304 | F08-KAVALAHALLI | NJY | DLMS Meter | 1.2695 | 0.73658 | 0.4405 | 0.82898 | 11.1463 | 49.2119
4413 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903020101 | F09-ADAVIMALLAPURA | AGRI | DLMS Meter | 0.71342 | 0.6421 | 0 | 0.71342 | 9.9966 | 9.9966
4414 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903010105 | F10-KODI SIDDESWARA IP | AGRI | DLMS Meter | 0.87432 | 0.69238 | 0.105 | 0.76932 | 10.001 | 10.001
4415 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | PUNABHAGHATTA_66 | 1310303903010106 | F11-J L HALLI NJY | NJY | DLMS Meter | 0.7588 | 0.41418 | 0.2948 | 0.464 | 10.7361 | 42.5044
4416 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | PURAVARA_66 | 1320304903010201 | F01-SIDDANAHALLI | AGRI | DLMS Meter | 0.6894 | 0.62036 | 0 | 0.6894 | 10.0139 | 10.0139
4417 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | PURAVARA_66 | 1320304903010202 | F02-THIMMALAPURA | AGRI | DLMS Meter | 0.567 | 0.51026 | 0 | 0.567 | 10.0076 | 10.0076
4418 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | PURAVARA_66 | 1320304903010203 | F03-GUMKARNAHALLI | AGRI | DLMS Meter | 0.7336 | 0.66004 | 0 | 0.7336 | 10.0266 | 10.0266
4419 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | PURAVARA_66 | 1320304903010204 | F04-IMMADAGONDANAHALLI | AGRI | DLMS Meter | 1.0058 | 0.90502 | 0 | 1.0058 | 10.0197 | 10.0197
4420 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | PURAVARA_66 | 1320304903020101 | F06-HALETHIMMANAHALLI NJY | NJY | DLMS Meter | 0.406 | 0.36563 | 0 | 0.406 | 9.9438 | 53.4898
4421 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | PURAVARA_66 | 1320304903020102 | F07-TALAKERE NJY | NJY | DLMS Meter | 0.2738 | 0.24477 | 0 | 0.2738 | 10.6023 | 54.896
4422 | BMANZ | EAST | SHIVAJINAGAR | E8 | PURUVANKARA_66 | 1130304902010101 | F02-PURUVANKARA | DOMESTIC | DLMS Meter | 0.89117 | 0.87235 | 0 | 0.89117 | 2.1118 | 2.1118
4423 | BMANZ | EAST | SHIVAJINAGAR | E8 | PURUVANKARA_66 | 1130304902010102 | F09-PURUVANKARA | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4424 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020205 | F01-AIR FORCE KATTIGENAHALLI | DEFENSE ESTABLISHMENT | DLMS Meter | 7.476 | 7.2438 | 0 | 7.476 | 3.1056 | 15.6223
4425 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020206 | F02-ANANTHPURA DUO MARVEL LAYOUT | DOMESTIC | DLMS Meter | 4.0754 | 3.5046 | 0.39 | 3.6854 | 4.9051 | 6.7535
4426 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020207 | F03-CRPF PUTTENAHALLI | DOMESTIC | DLMS Meter | 5.8027 | 5.7307 | 0 | 5.8027 | 1.2407 | 19.7189
4427 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020208 | F04-ISRO LAYOUT KENCHENAHALLI | DOMESTIC | DLMS Meter | 4.391 | 4.2218 | 0 | 4.391 | 3.8529 | 20.4733
4428 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020211 | F05-MASJID FEEDER | URBAN MIXED LOAD | DLMS Meter | 3.3784 | 3.2002 | 0 | 3.3784 | 5.2745 | 10.0372
4429 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020212 | F06-VIKAS NAGARA | URBAN MIXED LOAD | DLMS Meter | 5.0886 | 2.073 | 2.8168 | 2.2718 | 8.7504 | 10.473
4430 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020210 | F07-RAMKEY NORTH-1 | DOMESTIC | DLMS Meter | 0.57084 | 0.44835 | 0.09 | 0.48084 | 6.7566 | 8.3465
4431 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904010201 | F11-PRESTIGE ROYAL GARDEN | DOMESTIC | DLMS Meter | 1.0067 | 0.9805 | 0 | 1.0067 | 2.5984 | 5.4638
4432 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020201 | F12-MARUTHI NAGARA | URBAN MIXED LOAD | DLMS Meter | 7.184 | 5.4201 | 1.4022 | 5.7818 | 6.2562 | 8.9497
4433 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020202 | F13-VENKATALA | URBAN MIXED LOAD | DLMS Meter | 5.7174 | 5.2043 | 0.14 | 5.5774 | 6.6899 | 6.6899
4434 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020209 | F14-YELAHANKA NEW TOWN | DOMESTIC | DLMS Meter | 4.4949 | 4.4068 | 0 | 4.4949 | 1.96 | 9.2584
4435 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020203 | F15-SINGANAYAKANAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.1851 | 3.0445 | 0 | 3.1851 | 4.4121 | 30.1897
4436 | BMANZ | NORTH | HEBBAL | C7 | PUTTENAHALLI_220 | 1120303904020204 | F16-MYLAPPANAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.6334 | 1.5456 | 0 | 1.6334 | 5.3759 | 10.8735
4437 | BMANZ | NORTH | HEBBAL | C7 | RAJANUKUNTE_66 | 1120303903010102 | F01-MLA-SINGANAYAKANAHALLY | URBAN MIXED LOAD | DLMS Meter | 1.6728 | 1.599 | 0 | 1.6728 | 4.4129 | 43.6402
4438 | BMANZ | NORTH | HEBBAL | C7 | RAJANUKUNTE_66 | 1120303903010103 | F02-HT-RELIANCE | INDUSTRIAL | DLMS Meter | 4.6408 | 3.7568 | 0.57001 | 4.0708 | 7.7144 | 8.7693
4439 | BMANZ | NORTH | HEBBAL | C7 | RAJANUKUNTE_66 | 1120303903010104 | F03-GANTIGANAHALLY | URBAN MIXED LOAD | DLMS Meter | 1.9946 | 1.9324 | 0 | 1.9946 | 3.1177 | 8.7175
4440 | BMANZ | NORTH | HEBBAL | C7 | RAJANUKUNTE_66 | 1120303903010105 | F04-ADDEVISHWANATHAPURA | URBAN MIXED LOAD | DLMS Meter | 1.6657 | 1.5946 | 0 | 1.6657 | 4.2667 | 41.4555
4441 | BMANZ | NORTH | HEBBAL | C7 | RAJANUKUNTE_66 | 1120303903010106 | F05-MARASANDRA | URBAN MIXED LOAD | DLMS Meter | 4.1836 | 4.0218 | 0 | 4.1836 | 3.8671 | 10.2415
4442 | BMANZ | NORTH | HEBBAL | C7 | RAJANUKUNTE_66 | 1120303903020301 | F06-FKMF | INDUSTRIAL | DLMS Meter | 1.0467 | 0.99684 | 0.01 | 1.0367 | 3.8448 | 7.8839
4443 | BMANZ | NORTH | HEBBAL | C7 | RAJANUKUNTE_66 | 1120303903020101 | F08-BYATHA | URBAN MIXED LOAD | DLMS Meter | 4.8538 | 4.6039 | 0.0231 | 4.8307 | 4.6943 | 22.1575
4444 | BMANZ | NORTH | HEBBAL | C7 | RAJANUKUNTE_66 | 1120303903020302 | F09-CENTURY-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.2612 | 1.9975 | 0.15422 | 2.1069 | 5.1929 | 8.7837
4445 | BMANZ | NORTH | HEBBAL | C7 | RAJANUKUNTE_66 | 1120303903010101 | F10-SHOBHA | DOMESTIC | DLMS Meter | 1.9595 | 1.7912 | 0.12 | 1.8395 | 2.6265 | 2.6265
4446 | BMANZ | NORTH | HEBBAL | C7 | RAJANUKUNTE_66 | 1120303903020303 | F11-PGCL | INDUSTRIAL | DLMS Meter | 0.33593 | 0.3284 | 0 | 0.33593 | 2.2408 | 3.6437
4447 | BMASZ | WEST | RR NAGAR | W7 | RAJARAJESHWARINAGAR_66 | 1140204901010101 | F01-SACHIDANANDA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 4.5623 | 4.3443 | 0.049315 | 4.513 | 3.7386 | 3.7386
4448 | BMASZ | WEST | KENGERI | K1 | RAJARAJESHWARINAGAR_66 | 1140204901010102 | F03-BWSSB | WATER WORKS | DLMS Meter | 5.7747 | 3.4049 | 2.151 | 3.6236 | 6.0353 | 11.1383
4449 | BMASZ | WEST | KENGERI | K1 | RAJARAJESHWARINAGAR_66 | 1140204901010103 | F04-BDA-TH-STAGE | URBAN MIXED LOAD | DLMS Meter | 3.3014 | 1.8844 | 1.2845 | 2.0169 | 6.5697 | 6.5697
4450 | BMASZ | WEST | KENGERI | K1 | RAJARAJESHWARINAGAR_66 | 1140204901010104 | F05-KENGERI | URBAN MIXED LOAD | DLMS Meter | 5.4458 | 4.2275 | 1.0765 | 4.3693 | 3.2443 | 14.4243
4451 | BMASZ | SOUTH | JAYANAGAR | S18 | RAJARAJESHWARINAGAR_66 | 1140204901010105 | F06-UTTARAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.686 | 3.5141 | 0 | 3.686 | 4.6629 | 7.8826
4452 | BMASZ | WEST | RR NAGAR | W7 | RAJARAJESHWARINAGAR_66 | 1140204901010301 | F07-BEML-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.9061 | 2.8235 | 0 | 2.9061 | 2.8426 | 2.8426
4453 | BMASZ | WEST | RR NAGAR | W7 | RAJARAJESHWARINAGAR_66 | 1140204901010302 | F08-R-R-NAGAR-TEMPLE | URBAN MIXED LOAD | DLMS Meter | 3.7594 | 3.6399 | 0 | 3.7594 | 3.1793 | 11.9733
4454 | BMASZ | WEST | KENGERI | K1 | RAJARAJESHWARINAGAR_66 | 1140204901010303 | F09-PATTANA-GERE | URBAN MIXED LOAD | DLMS Meter | 5.3015 | 3.9911 | 1.0835 | 4.2179 | 5.3786 | 20.9643
4455 | BMASZ | WEST | KENGERI | K1 | RAJARAJESHWARINAGAR_66 | 1140204901010108 | F11-IDLE | IDLE | DLMS Meter | 3.2823 | 2.7813 | 0.39614 | 2.8862 | 3.6327 | 23.9065
4456 | BMASZ | WEST | RR NAGAR | W7 | RAJARAJESHWARINAGAR_66 | 1140204901010305 | F12-CHANNASANDRA | URBAN MIXED LOAD | DLMS Meter | 3.6339 | 3.5278 | 0 | 3.6339 | 2.9195 | 32.5213
4457 | BMASZ | SOUTH | JAYANAGAR | S18 | RAJARAJESHWARINAGAR_66 | 1140204901010106 | F13-VADDARAPALYA | URBAN MIXED LOAD | DLMS Meter | 1.5237 | 1.377 | 0.04 | 1.4837 | 7.1903 | 12.0316
4458 | BMASZ | WEST | RR NAGAR | W7 | RAJARAJESHWARINAGAR_66 | 1140204901010107 | F14-IDEAL-HOMES | URBAN MIXED LOAD | DLMS Meter | 6.3736 | 5.8262 | 0.25688 | 6.1167 | 4.7502 | 4.7502
4459 | BMASZ | SOUTH | JAYANAGAR | S18 | RAJARAJESHWARINAGAR_66 | 1140204901020401 | F15-MANTRI ALPHINES | DOMESTIC | DLMS Meter | 2.7172 | 2.4577 | 0.115 | 2.6022 | 5.5532 | 7.4761
4460 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901010101 | F01-THALAKATTA | AGRI | DLMS Meter | 0.68538 | 0.61676 | 0 | 0.68538 | 10.0114 | 10.0114
4461 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901010102 | F02-GOWDIHALLI | AGRI | DLMS Meter | 1.3838 | 1.2305 | 0 | 1.3838 | 11.078 | 11.078
4462 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901010103 | F03-GUNDASAMUDRA | AGRI | DLMS Meter | 1.437 | 1.2427 | 0.0176 | 1.4194 | 12.452 | 12.452
4463 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901010104 | F04-RAMAGIRI | AGRI | DLMS Meter | 0.92286 | 0.83036 | 0 | 0.92286 | 10.023 | 10.023
4464 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901020307 | F05-KANIVEHALLI | AGRI | DLMS Meter | 1.4233 | 1.2805 | 0 | 1.4233 | 10.0287 | 10.0287
4465 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901020301 | F06-TUPPADAHALLI | AGRI | DLMS Meter | 1.349 | 1.2137 | 0 | 1.349 | 10.0329 | 10.0329
4466 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901020302 | F07-KALAKERE | AGRI | DLMS Meter | 1.6097 | 1.4492 | 0 | 1.6097 | 9.9712 | 9.9712
4467 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901020303 | F08-RNULANUR | AGRI | DLMS Meter | 1.0433 | 0.91743 | 0 | 1.0433 | 12.0665 | 12.0665
4468 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901020304 | F09-RD-KAVALA NJY | NJY | DLMS Meter | 0.50104 | 0.30428 | 0.15367 | 0.34737 | 12.4038 | 53.4106
4469 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901020305 | F10-HANUMALI NJY | NJY | DLMS Meter | 1.166 | 0.77709 | 0.28063 | 0.88537 | 12.2302 | 52.9059
4470 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901020306 | F11-MUDDAPURA NJY | NJY | DLMS Meter | 0.83196 | 0.50585 | 0.26369 | 0.56827 | 10.9851 | 46.3838
4471 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | RAMAGIRI_66 | 1310203901010106 | F12-RANGAPURA NJY | NJY | DLMS Meter | 0.6132 | 0.53383 | 0.006 | 0.6072 | 12.084 | 42.9165
4472 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901020101 | F01-JANAPADALOKA | URBAN MIXED LOAD | DLMS Meter | 1.619 | 1.0536 | 0.4175 | 1.2015 | 12.3126 | 30.6261
4473 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901010101 | F02-TOWN | URBAN MIXED LOAD | DLMS Meter | 3.7368 | 3.3555 | 0.047 | 3.6898 | 9.0612 | 21.2517
4474 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901010102 | F03-BALAGERI | URBAN MIXED LOAD | DLMS Meter | 2.7395 | 2.4472 | 0.0231 | 2.7164 | 9.9119 | 9.9119
4475 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901010103 | F04-INDUSTRIAL | RURAL MIXED LOAD | DLMS Meter | 0.39496 | 0.28742 | 0.0785 | 0.31646 | 9.1775 | 39.8651
4476 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901010104 | F05-BASAVANAPURA | AGRI | DLMS Meter | 0.61767 | 0.55275 | 0.0025 | 0.61517 | 10.1461 | 10.1461
4477 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901020302 | F07-HUNUSENAHALLY | AGRI | DLMS Meter | 1.3212 | 1.1513 | 0.04185 | 1.2794 | 10.0131 | 10.0131
4478 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901020303 | F08-TOWN | URBAN MIXED LOAD | DLMS Meter | 4.6685 | 4.3895 | 0 | 4.6685 | 5.9756 | 13.132
4479 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901020304 | F09-BILAGUMBA | AGRI | DLMS Meter | 0.46207 | 0.40355 | 0.0112 | 0.45087 | 10.4943 | 10.4943
4480 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901020305 | F10-TOWN | URBAN MIXED LOAD | DLMS Meter | 4.2531 | 3.9362 | 0 | 4.2531 | 7.4515 | 16.686
4481 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901010107 | F12-HUNASANAHALLI NJY | NJY | DLMS Meter | 0.6367 | 0.33174 | 0.2707 | 0.366 | 9.3607 | 52.028
4482 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901010109 | F13-VADERAHALLI NJY | NJY | DLMS Meter | 0.54247 | 0.29003 | 0.22832 | 0.31415 | 7.6762 | 25.1694
4483 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA URBAN | RAMNAGAR_66 | 1220102901010108 | F14-RAYARADODDI RAPDRP | URBAN MIXED LOAD | DLMS Meter | 1.8607 | 1.7162 | 0 | 1.8607 | 7.7628 | 9.521
4484 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903010101 | F01-DEVASAMUDRA | AGRI | DLMS Meter | 1.1053 | 0.99475 | 0 | 1.1053 | 9.9999 | 9.9999
4485 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903010102 | F02-JBHALLI | AGRI | DLMS Meter | 1.2317 | 1.0637 | 0 | 1.2317 | 13.6371 | 13.6371
4486 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903020305 | F03-N.R.K.PURA | AGRI | DLMS Meter | 1.1511 | 0.98478 | 0 | 1.1511 | 14.4456 | 14.4456
4487 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903010105 | F04-NJY SRJ | NJY | DLMS Meter | 0.66046 | 0.58203 | 0 | 0.66046 | 11.8746 | 77.0723
4488 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903020301 | F05-RAMPURA | AGRI | DLMS Meter | 0.53796 | 0.48409 | 0 | 0.53796 | 10.0141 | 10.0141
4489 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903020302 | F06-MURUDI | AGRI | DLMS Meter | 0.78294 | 0.70466 | 0 | 0.78294 | 9.9987 | 9.9987
4490 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903020303 | F07-BANDRAVI | RURAL MIXED LOAD | DLMS Meter | 1.7675 | 1.5355 | 0 | 1.7675 | 13.1267 | 26.1332
4491 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903020304 | F08-THAMMENAHALLI | AGRI | DLMS Meter | 1.3921 | 1.2319 | 0 | 1.3921 | 11.5042 | 11.5042
4492 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903010103 | F09-RAMASAGARINDUSTRIAL | INDUSTRIAL | DLMS Meter | 0.90375 | 0.89294 | 0 | 0.90375 | 1.1966 | 1.1966
4493 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903010104 | F10-TOWN NJY | NJY | DLMS Meter | 1.386 | 1.223 | 0 | 1.386 | 11.7621 | 40.8431
4494 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903020306 | F11- NJY HANUMANAGUDDA | NJY | DLMS Meter | 0.67937 | 0.59614 | 0 | 0.67937 | 12.2512 | 68.6192
4495 | CTAZ | DAVANAGERE | HIRIYURU | MOLAKALMURU | RAMPURA_66 | 1310403903020307 | F12-NJY BOMMADEVARAHALLY | NJY | DLMS Meter | 0.98037 | 0.85738 | 0 | 0.98037 | 12.5454 | 66.4599
4496 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010101 | F01-NARAYANAPURA-F | AGRI | DLMS Meter | 0.54867 | 0.49392 | 0 | 0.54867 | 9.9792 | 9.9792
4497 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010102 | F02-KOLLIGANAHALLI-F | AGRI | DLMS Meter | 0.6777 | 0.60996 | 0 | 0.6777 | 9.9953 | 9.9953
4498 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010103 | F03-CHILUR-F | AGRI | DLMS Meter | 0.82868 | 0.74587 | 0 | 0.82868 | 9.9929 | 9.9929
4499 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010104 | F05-DYAVASANDRA-F | AGRI | DLMS Meter | 1.2852 | 1.1567 | 0 | 1.2852 | 10.0033 | 10.0033
4500 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902020301 | F06-SONA | URBAN MIXED LOAD | DLMS Meter | 0.56392 | 0.5112 | 0 | 0.56392 | 9.3483 | 11.6768
4501 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010105 | F07-RAMPURA NJY | NJY | DLMS Meter | 0.27484 | 0.20958 | 0.0435 | 0.23134 | 9.4052 | 44.7953
4502 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902020302 | F08-HAROHALLI-TOWN-F | URBAN MIXED LOAD | DLMS Meter | 2.9448 | 2.5938 | 0.111 | 2.8338 | 8.4673 | 13.4186
4503 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902020303 | F09-FORGEPRO | INDUSTRIAL | DLMS Meter | 1.8111 | 1.6551 | 0.087 | 1.7241 | 4.0047 | 5.7467
4504 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902020304 | F10-KIADB-01 | INDUSTRIAL | DLMS Meter | 3.5397 | 3.4096 | 0 | 3.5397 | 3.6758 | 3.6758
4505 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010106 | F11-KIADB-02 | INDUSTRIAL | DLMS Meter | 3.5893 | 3.4544 | 0 | 3.5893 | 3.759 | 4.2059
4506 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010107 | F12-EASUN-REYROLLE-F | INDUSTRIAL | DLMS Meter | 0.0104 | 0.009274 | 0.0008 | 0.0096 | 3.3958 | 74.7081
4507 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010108 | F13-JAKKASANDRA-NJY-F | NJY | DLMS Meter | 1.1323 | 0.53374 | 0.5405 | 0.5918 | 9.8105 | 26.1286
4508 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010109 | F14-DEVARAGOLLAHALLI-NJY-F | NJY | DLMS Meter | 1.4432 | 0.98563 | 0.35 | 1.0932 | 9.8397 | 47.0983
4509 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902020305 | F15-KIADB-03 | INDUSTRIAL | DLMS Meter | 3.588 | 3.4422 | 0 | 3.588 | 4.0647 | 5.4801
4510 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010111 | F16-ANTHEM | INDUSTRIAL | DLMS Meter | 5.3904 | 5.3778 | 0 | 5.3904 | 0.23449 | 0.23449
4511 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010112 | F17-DAIRY CLASSIC | INDUSTRIAL | DLMS Meter | 4.4969 | 4.4417 | 0 | 4.4969 | 1.2268 | 1.2268
4512 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902020306 | F18-KIADB-04 | INDUSTRIAL | DLMS Meter | 1.8164 | 1.7618 | 0 | 1.8164 | 3.0063 | 4.4232
4513 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010113 | F19-STOVE KRAFT | INDUSTRIAL | DLMS Meter | 3.4854 | 3.4454 | 0 | 3.4854 | 1.147 | 1.147
4514 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902020307 | F20-PAROSONS NUTRITION | INDUSTRIAL | DLMS Meter | 4.9121 | 4.8708 | 0 | 4.9121 | 0.84118 | 0.84118
4515 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010114 | F21-KIADB-07 PRINTERS PARK ROAD | INDUSTRIAL | DLMS Meter | 0.01139 | 0.010945 | 0 | 0.01139 | 3.9069 | 11.9011
4516 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | RANGANADODDI_66 | 1220304902010115 | F22-KIADB TOKAI RUBBER ROAD | INDUSTRIAL | DLMS Meter | 4.1959 | 3.2676 | 0.795 | 3.4009 | 3.9189 | 4.1759
4517 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGANATHAPURA_66 | 1310401901010101 | F01-KUNDALAGURA | AGRI | DLMS Meter | 1.8105 | 1.6147 | 0 | 1.8105 | 10.8127 | 10.8127
4518 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGANATHAPURA_66 | 1310401901010102 | F02-KODIHALLI | AGRI | DLMS Meter | 1.2944 | 1.1649 | 0 | 1.2944 | 10.0008 | 10.0008
4519 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGANATHAPURA_66 | 1310401901010103 | F03-UPPALAGERE | AGRI | DLMS Meter | 0.90506 | 0.81425 | 0 | 0.90506 | 10.0336 | 10.0336
4520 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGANATHAPURA_66 | 1310401901010104 | F04-SHIVAPURA | AGRI | DLMS Meter | 1.0289 | 0.92416 | 0 | 1.0289 | 10.1813 | 10.1813
4521 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGANATHAPURA_66 | 1310401901020301 | F05-PITTLALI | AGRI | DLMS Meter | 0.99638 | 0.89709 | 0 | 0.99638 | 9.9647 | 9.9647
4522 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGANATHAPURA_66 | 1310401901020302 | F06-ALURU | AGRI | DLMS Meter | 0.79408 | 0.71469 | 0 | 0.79408 | 9.9971 | 9.9971
4523 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGANATHAPURA_66 | 1310401901020303 | F07-NJYARANAKATTE | NJY | DLMS Meter | 0.82772 | 0.75182 | 0 | 0.82772 | 9.1696 | 59.4824
4524 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGANATHAPURA_66 | 1310401901010105 | F08-NJY LAKSHMIPURA | NJY | DLMS Meter | 0.9086 | 0.82906 | 0 | 0.9086 | 8.7541 | 64.053
4525 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGENAHALLI_66 | 1310401907010101 | F01-BIDARAKERE | AGRI | DLMS Meter | 0.2628 | 0.23498 | 0 | 0.2628 | 10.5862 | 10.5862
4526 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGENAHALLI_66 | 1310401907010102 | F02-SHIVAGANGA | AGRI | DLMS Meter | 0.34424 | 0.30987 | 0 | 0.34424 | 9.9849 | 9.9849
4527 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGENAHALLI_66 | 1310401907010103 | F03-AMBALAGERE | AGRI | DLMS Meter | 0.84638 | 0.7616 | 0 | 0.84638 | 10.0164 | 10.0164
4528 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGENAHALLI_66 | 1310401907010104 | F04-BAGAVATI | AGRI | DLMS Meter | 0.7845 | 0.69755 | 0 | 0.7845 | 11.0831 | 11.0831
4529 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGENAHALLI_66 | 1310401907010106 | F05-NJY RANGENAHALLY | NJY | DLMS Meter | 0.31562 | 0.29337 | 0 | 0.31562 | 7.0487 | 66.306
4530 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGENAHALLI_66 | 1310401907020301 | F06-SIDDESHWARA | AGRI | DLMS Meter | 1.027 | 0.92061 | 0 | 1.027 | 10.3591 | 11.7143
4531 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGENAHALLI_66 | 1310401907010105 | F07-NJYAINAHALLY | NJY | DLMS Meter | 0.3897 | 0.35801 | 0 | 0.3897 | 8.1322 | 63.1075
4532 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGENAHALLI_66 | 1310401907020302 | F08-T OBENAHALLY | AGRI | DLMS Meter | 0.6244 | 0.56207 | 0 | 0.6244 | 9.9824 | 9.9824
4533 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | RANGENAHALLI_66 | 1310401907010301 | F09-BYADARAHALLY | AGRI | DLMS Meter | 1.0092 | 0.90804 | 0 | 1.0092 | 10.0235 | 10.0235
4534 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | RAYALPADU_66 | 1230103909020101 | F06-MANJEVARIPALLI | AGRI | DLMS Meter | 0.3988 | 0.35893 | 0 | 0.3988 | 9.997 | 9.997
4535 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | RAYALPADU_66 | 1230103909020102 | F07-RAYALPADU LOCAL NJY | NJY | DLMS Meter | 1.0861 | 0.99582 | 0 | 1.0861 | 8.3122 | 85.0049
4536 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | RAYALPADU_66 | 1230103909020103 | F08-DEVANAGARIPALLI | AGRI | DLMS Meter | 0.4306 | 0.38776 | 0 | 0.4306 | 9.9487 | 9.9487
4537 | BMASZ | SOUTH | JAYANAGAR | S6 | RBI_66 | 1110104903020105 | F01-CHUNNCHUGATTA | DOMESTIC | DLMS Meter | 3.0884 | 2.7411 | 0.20591 | 2.8825 | 4.9047 | 9.6031
4538 | BMASZ | SOUTH | JAYANAGAR | S6 | RBI_66 | 1110104903020112 | F02-GLASS-FACTORY | DOMESTIC | DLMS Meter | 2.9358 | 2.5678 | 0.25644 | 2.6794 | 4.1642 | 8.0096
4539 | BMASZ | SOUTH | HSR | S19 | RBI_66 | 1110104903020103 | F03-K-C-HALLI | URBAN MIXED LOAD | DLMS Meter | 4.1039 | 3.9148 | 0 | 4.1039 | 4.6075 | 4.8856
4540 | BMASZ | SOUTH | JAYANAGAR | S6 | RBI_66 | 1110104903010101 | F04-RBI1 | DOMESTIC | DLMS Meter | 1.9116 | 1.8251 | 0 | 1.9116 | 4.5238 | 10.1126
4541 | BMASZ | SOUTH | JAYANAGAR | S6 | RBI_66 | 1110104903010102 | F05-RBI2 | DOMESTIC | DLMS Meter | 1.2793 | 1.1902 | 0.037521 | 1.2417 | 4.1509 | 7.6025
4542 | BMASZ | SOUTH | HSR | S12 | RBI_66 | 1110104903020301 | F06-FKLEAN-PACKS-LIMITED | COMMERCIAL | DLMS Meter | 1.3496 | 1.2582 | 0.015 | 1.3346 | 5.7235 | 5.7235
4543 | BMASZ | SOUTH | HSR | S19 | RBI_66 | 1110104903020104 | F08-SOUTH-CITY | DOMESTIC | DLMS Meter | 2.2062 | 1.9889 | 0.07 | 2.1362 | 6.891 | 13.0333
4544 | BMASZ | SOUTH | HSR | S12 | RBI_66 | 1110104903020302 | F09-NRUPATHUNGANAGAR | DOMESTIC | DLMS Meter | 4.2317 | 3.7931 | 0 | 4.2317 | 10.3652 | 13.3511
4545 | BMASZ | SOUTH | HSR | S12 | RBI_66 | 1110104903020303 | F10-KOTHNUR | DOMESTIC | DLMS Meter | 3.8375 | 3.3377 | 0.132 | 3.7055 | 9.9254 | 11.9172
4546 | BMASZ | SOUTH | JAYANAGAR | S14 | RBI_66 | 1110104903020106 | F11-JP-NAGAR-TH-PHASE | DOMESTIC | DLMS Meter | 1.8651 | 1.5521 | 0.25085 | 1.6143 | 3.8519 | 8.7543
4547 | BMASZ | SOUTH | JAYANAGAR | S6 | RBI_66 | 1110104903020107 | F12-PUTTENAHALLI | DOMESTIC | DLMS Meter | 3.957 | 3.8621 | 0 | 3.957 | 2.398 | 3.4268
4548 | BMASZ | SOUTH | JAYANAGAR | S6 | RBI_66 | 1110104903020108 | F13-BRIGADE-MILLENIUM | DOMESTIC | DLMS Meter | 1.5297 | 1.1703 | 0.32461 | 1.2051 | 2.8833 | 4.7274
4549 | BMASZ | SOUTH | JAYANAGAR | S6 | RBI_66 | 1110104903020109 | F14-BRIGADE-MILLENIUM | DOMESTIC | DLMS Meter | 0.95946 | 0.92138 | 0.012565 | 0.94689 | 2.6946 | 2.6946
4550 | BMASZ | SOUTH | JAYANAGAR | S6 | RBI_66 | 1110104903020110 | F15-BRIGADE-GARDENIA | DOMESTIC | DLMS Meter | 2.5944 | 2.3587 | 0.15038 | 2.4441 | 3.4908 | 12.9087
4551 | BMASZ | SOUTH | JAYANAGAR | S6 | RBI_66 | 1110104903020111 | F16 -BRIGADE-GARDENIA | DOMESTIC | DLMS Meter | 0.53713 | 0.5148 | 0 | 0.53713 | 4.1587 | 4.1587
4552 | BMASZ | SOUTH | JAYANAGAR | S14 | RBI_66 | 1110104903020401 | F17-KALYANI VISTA | COMMERCIAL | DLMS Meter | 1.6562 | 1.6558 | 0 | 1.6562 | 0.025684 | 0.025684
4553 | BMASZ | WEST | RAJAJINAGAR | N2 | REMCO_66 | 1140203902020101 | F01-VIJAYANAGAR | URBAN MIXED LOAD | DLMS Meter | 2.2985 | 1.9241 | 0.2479 | 2.0506 | 6.1712 | 9.8428
4554 | BMASZ | WEST | RR NAGAR | W6 | REMCO_66 | 1140203902020102 | F02-BHEL | INDUSTRIAL | DLMS Meter | 1.2715 | 1.2455 | 0 | 1.2715 | 2.0453 | 2.0453
4555 | BMASZ | WEST | RR NAGAR | W6 | REMCO_66 | 1140203902010301 | F03-BHAPUJI-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.2316 | 2.0278 | 0 | 2.2316 | 9.1348 | 11.3352
4556 | BMASZ | WEST | RR NAGAR | W6 | REMCO_66 | 1140203902020103 | F04-RMU | URBAN MIXED LOAD | DLMS Meter | 4.2107 | 3.5192 | 0.35081 | 3.8599 | 8.8279 | 18.8868
4557 | BMASZ | WEST | RR NAGAR | W6 | REMCO_66 | 1140203902010302 | F08-MUTHACHARI-IND-ESTATE | INDUSTRIAL | DLMS Meter | 5.6326 | 4.447 | 0.82472 | 4.8079 | 7.5047 | 9.0124
4558 | BMANZ | EAST | VIDHANASOUDHA | W3 | REMCO_66 | 1140203902020104 | F10-VICTORIA-(PIPE-LINE) | URBAN MIXED LOAD | DLMS Meter | 5.6646 | 4.6071 | 0.337 | 5.3276 | 13.5243 | 20.5563
4559 | BMASZ | WEST | RR NAGAR | W6 | REMCO_66 | 1140203902020105 | F13-AJEET-SAIT-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 3.1308 | 2.1562 | 0.85205 | 2.2788 | 5.3806 | 7.7049
4560 | BMASZ | WEST | RR NAGAR | W6 | REMCO_66 | 1140203902010306 | F14-GANGONDANAHALLY | URBAN MIXED LOAD | DLMS Meter | 5.3227 | 3.5319 | 1.4985 | 3.8241 | 7.6431 | 16.329
4561 | BMANZ | EAST | VIDHANASOUDHA | W3 | REMCO_66 | 1140203902020106 | F15-RMU-(GUDDADAHALLI) | URBAN MIXED LOAD | DLMS Meter | 2.5443 | 1.879 | 0.3518 | 2.1925 | 14.2967 | 15.2876
4562 | BMASZ | WEST | RR NAGAR | W6 | REMCO_66 | 1140203902010307 | F16-RANGANATHA-COLONY | URBAN MIXED LOAD | DLMS Meter | 2.024 | 1.8477 | 0.02481 | 1.9992 | 7.5776 | 11.1144
4563 | BMASZ | WEST | RR NAGAR | W6 | REMCO_66 | 1140203902020107 | F17-PATIL-PUTTAPPA-IND | URBAN MIXED LOAD | DLMS Meter | 1.9368 | 1.7571 | 0.05154 | 1.8853 | 6.799 | 7.7198
4564 | BMANZ | NORTH | MALLESHWARA | C6 | RMV_66 | 1120204902010102 | F02-DOLLARS-COLONY | DOMESTIC | DLMS Meter | 0.58778 | 0.53349 | 0.004 | 0.58378 | 8.6146 | 18.086
4565 | BMANZ | NORTH | HEBBAL | C4 | RMV_66 | 1120204902010103 | F03-NAGSHETYHALLISTNAUX | DOMESTIC | DLMS Meter | 3.5307 | 3.2279 | 0.11 | 3.4207 | 5.6384 | 15.2959
4566 | BMANZ | NORTH | MALLESHWARA | C6 | RMV_66 | 1120204902010104 | F04-RMV-II-&-NEWBEL-ROAD | URBAN MIXED LOAD | DLMS Meter | 2.8406 | 2.5814 | 0.0042 | 2.8364 | 8.9893 | 16.7494
4567 | BMANZ | NORTH | MALLESHWARA | C6 | RMV_66 | 1120204902020101 | F05-MSR-INDUSTRIAL-ESTATE | URBAN MIXED LOAD | DLMS Meter | 3.4357 | 3.1934 | 0 | 3.4357 | 7.0547 | 13.2561
4568 | BMANZ | NORTH | HEBBAL | C4 | RMV_66 | 1120204902020301 | F07-FVSNL | COMMERCIAL | DLMS Meter | 3.2468 | 3.0609 | 0 | 3.2468 | 5.7244 | 14.0799
4569 | BMANZ | NORTH | HEBBAL | C4 | RMV_66 | 1120204902010301 | F10-KOLTE-PATIL | DOMESTIC | DLMS Meter | 3.2254 | 3.0718 | 0 | 3.2254 | 4.7611 | 15.7057
4570 | BMANZ | NORTH | JALAHALLI | C9 | RMV_66 | 1120204902010105 | F12-DEVI-NAGAR | DOMESTIC | DLMS Meter | 4.0199 | 3.8314 | 0 | 4.0199 | 4.6893 | 11.5836
4571 | BMANZ | NORTH | JALAHALLI | C9 | RMV_66 | 1120204902020302 | F13-AADHAR | COMMERCIAL | DLMS Meter | 4.0944 | 4.0887 | 0 | 4.0944 | 0.13945 | 17.6544
4572 | BMANZ | NORTH | MALLESHWARA | C6 | RMV_66 | 1120204902020308 | F14-CHIKKAMARANAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.2222 | 1.9068 | 0.1275 | 2.0947 | 8.9704 | 18.4167
4573 | BMASZ | SOUTH | KORAMANGALA | S7 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905020203 | F01-RMZ | COMMERCIAL | DLMS Meter | 2.1844 | 2.1896 | 0 | 2.1844 | -0.23773 | -0.23773
4574 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905020204 | F02-S11BHT145_S11BHT146 | URBAN MIXED LOAD | DLMS Meter | 2.2021 | 0 | 2.2021 | 0 | 0 | #DIV/0!
4575 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905020201 | F03-BLOCK 7 | DOMESTIC | DLMS Meter | 1.8454 | 1.8544 | 0 | 1.8454 | -0.4887 | 2.1284
4576 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905020202 | F04-ADARSHA CAMPUS | COMMERCIAL | DLMS Meter | 3.3114 | 3.2415 | 0.05 | 3.2614 | 0.61143 | 1.9083
4577 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905010201 | F09-HONEY WELL | COMMERCIAL | DLMS Meter | 3.7402 | 3.6959 | 0 | 3.7402 | 1.1828 | 1.1828
4578 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905010203 | F10-S11BHT236 | URBAN MIXED LOAD | DLMS Meter | 3.7402 | 0 | 3.7402 | 0 | 0 | #DIV/0!
4579 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905010202 | F11-BLOCK 6A | DOMESTIC | DLMS Meter | 2.5071 | 2.3959 | 0.1 | 2.4071 | 0.46202 | 2.8791
4580 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905010204 | F12-ADARSHA WATER PUMP | URBAN MIXED LOAD | DLMS Meter | 0.26181 | 0 | 0.26181 | 2.3572e-08 | 0 | #DIV/0!
4581 | BMASZ | SOUTH | KORAMANGALA | S7 | RMZ_ADARSHA_ECOWORLD_66 | #N/A | F14-RMZ | #N/A | DLMS Meter | 1.1127 | 1.1168 | 0 | 1.1127 | -0.36774 | 3.7523
4582 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905030201 | F15-ADARSHA CAMPUS 5A | COMMERCIAL | DLMS Meter | 1.9696 | 1.9617 | 0 | 1.9696 | 0.39861 | 3.1068
4583 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905030203 | F16-S11BHT234_S11BHT235 | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4584 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905030204 | F17-S11BHT134_S11BHT126 | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4585 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905030205 | F18-S11BHT237_S11BHT233 | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4586 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905030206 | F19-DODDAKKANAHALLLI | URBAN MIXED LOAD | DLMS Meter | 2.678 | 0.69837 | 1.925 | 0.75301 | 7.2563 | 10.7226
4587 | BMASZ | SOUTH | HSR | S11 | RMZ_ADARSHA_ECOWORLD_66 | 1110303905030202 | F20-SARJAPURA ROAD | URBAN MIXED LOAD | DLMS Meter | 7.1847 | 6.541 | 0.189 | 6.9957 | 6.4993 | 6.4993
4588 | BMASZ | SOUTH | KORAMANGALA | S7 | RMZ_ADARSHA_ECOWORLD_66 | #N/A | F8-RMZ-Campus 4C | #N/A | DLMS Meter | 0.6227 | 0.625 | 0 | 0.6227 | -0.36983 | 1.2404
4589 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | SADALI_66 | 1230404902010101 | F01-HT-FEEDER | INDUSTRIAL | DLMS Meter | 0.005215 | 0.00525 | 0 | 0.005215 | -0.67114 | -0.67062
4590 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | SADALI_66 | 1230404902010102 | F02-GADIMICHENAHALLI | AGRI | DLMS Meter | 0.63325 | 0.57006 | 0 | 0.63325 | 9.9789 | 9.9789
4591 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | SADALI_66 | 1230404902010103 | F03-NJY-SONNAGANAHALLI | NJY | DLMS Meter | 0.47338 | 0.41276 | 0 | 0.47338 | 12.8059 | 81.6061
4592 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | SADALI_66 | 1230404902010104 | F04-S VENKATAPURA | AGRI | DLMS Meter | 0.78976 | 0.71045 | 0 | 0.78976 | 10.0414 | 10.0414
4593 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | SADALI_66 | 1230404902020301 | F06-NALLAPANAHALLI | NJY | DLMS Meter | 0.98387 | 0.8601 | 0 | 0.98387 | 12.5797 | 52.5753
4594 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | SADALI_66 | 1230404902020302 | F07-MITTEMARI | AGRI | DLMS Meter | 0.55538 | 0.39242 | 0.11911 | 0.43627 | 10.0496 | 10.0496
4595 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | SADALI_66 | 1230404902020303 | F08-S-DEVAGANAHALLI | AGRI | DLMS Meter | 1.1429 | 1.0287 | 0 | 1.1429 | 9.9903 | 9.9903
4596 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA RURAL | SADALI_66 | 1230404902010106 | F09-SONNAGANAHALLI | AGRI | DLMS Meter | 0.69057 | 0.62142 | 0 | 0.69057 | 10.0132 | 10.0132
4597 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901020101 | F01-A-BLOCK | URBAN MIXED LOAD | DLMS Meter | 2.6041 | 1.4668 | 0.9955 | 1.6086 | 8.8194 | 13.3006
4598 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901020102 | F02-PAI-HOUSE | URBAN MIXED LOAD | DLMS Meter | 4.4601 | 4.1097 | 0 | 4.4601 | 7.8558 | 7.8558
4599 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901020103 | F03-BYATARAYANAPURA | URBAN MIXED LOAD | DLMS Meter | 4.8549 | 4.4156 | 0.03 | 4.8249 | 8.4845 | 10.5222
4600 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901020104 | F04-L-&-T | DOMESTIC | DLMS Meter | 1.4625 | 1.3732 | 0 | 1.4625 | 6.1099 | 6.1099
4601 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901020105 | F05-UAS-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 5.1312 | 4.6715 | 0 | 5.1312 | 8.9586 | 11.5171
4602 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901020301 | F07-SAHAKARANAGARA | URBAN MIXED LOAD | DLMS Meter | 5.4171 | 5.0196 | 0 | 5.4171 | 7.3366 | 11.418
4603 | BMANZ | NORTH | JALAHALLI | C9 | SAHAKARINAGAR_66 | 1120304901020302 | F08-KODIGEHALLI | URBAN MIXED LOAD | DLMS Meter | 2.8652 | 2.4765 | 0.255 | 2.6102 | 5.1243 | 8.3689
4604 | BMANZ | NORTH | JALAHALLI | C9 | SAHAKARINAGAR_66 | 1120304901020303 | F09-CANARA-BANK-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.2052 | 1.9569 | 0.104 | 2.1012 | 6.8683 | 9.744
4605 | BMANZ | NORTH | HEBBAL | C4 | SAHAKARINAGAR_66 | 1120304901020304 | F10-KB-PARK | HOSPITAL | DLMS Meter | 1.1456 | 1.0949 | 0.021561 | 1.124 | 2.5899 | 36.0183
4606 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901020305 | F11-DEFENCE-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.3062 | 2.1156 | 0 | 2.3062 | 8.2613 | 13.9265
4607 | BMANZ | NORTH | JALAHALLI | C9 | SAHAKARINAGAR_66 | 1120304901020307 | F13-VIRUPAKSHAPURA | URBAN MIXED LOAD | DLMS Meter | 3.9766 | 3.7131 | 0 | 3.9766 | 6.6271 | 14.215
4608 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901020308 | F14-TELECOM-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.9677 | 1.7118 | 0.1 | 1.8677 | 8.3446 | 16.871
4609 | BMANZ | NORTH | HEBBAL | C4 | SAHAKARINAGAR_66 | 1120304901020309 | F15-GODREJ | URBAN MIXED LOAD | DLMS Meter | 2.4674 | 2.3196 | 0 | 2.4674 | 5.9899 | 9.2031
4610 | BMANZ | NORTH | JALAHALLI | C9 | SAHAKARINAGAR_66 | 1120304901030501 | F17-SHANTHIVANA | URBAN MIXED LOAD | DLMS Meter | 3.692 | 3.4938 | 0.005 | 3.687 | 5.241 | 8.464
4611 | BMANZ | NORTH | JALAHALLI | C9 | SAHAKARINAGAR_66 | 1120304901030502 | F18-UIDAI | URBAN MIXED LOAD | DLMS Meter | 0.84253 | 0.57373 | 0.238 | 0.60453 | 5.0948 | 11.4289
4612 | BMANZ | NORTH | JALAHALLI | C9 | SAHAKARINAGAR_66 | 1120304901030503 | F19-FORTUNA | URBAN MIXED LOAD | DLMS Meter | 3.1177 | 2.718 | 0.205 | 2.9127 | 6.6831 | 13.8197
4613 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901030504 | F20-AGRAHARA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.739 | 1.5961 | 0 | 1.739 | 8.2175 | 14.5648
4614 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901030506 | F21-KOGILU-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.4275 | 3.8166 | 0.285 | 4.1425 | 7.8673 | 18.1881
4615 | BMANZ | NORTH | HEBBAL | C8 | SAHAKARINAGAR_66 | 1120304901010107 | F22-MILSTONE | COMMERCIAL | DLMS Meter | 2.801 | 2.544 | 0.0325 | 2.7685 | 8.1068 | 15.0774
4616 | BMANZ | NORTH | JALAHALLI | C9 | SAHAKARINAGAR_66 | 1120304901010109 | F23-HIRANANDANI | DOMESTIC | DLMS Meter | 0.45755 | 0.41986 | 0.01 | 0.44755 | 6.1858 | 6.1858
4617 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | SAMANDURU_66 | 1220201907010101 | F03-GUDDANAHALLI NJY | NJY | DLMS Meter | 1.2198 | 0.56426 | 0.592 | 0.6278 | 10.121 | 67.348
4618 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | SAMANDURU_66 | 1220201907010102 | F04-GANDHI GRAMA | AGRI | DLMS Meter | 0.4662 | 0.41974 | 0 | 0.4662 | 9.9655 | 15.8391
4619 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | SAMANDURU_66 | 1220201907020101 | F05-HALEHALLI | AGRI | DLMS Meter | 1.3566 | 1.2174 | 0 | 1.3566 | 10.2618 | 10.7137
4620 | BRAZ | RAMANAGAR | CHANDAPURA | ANEKAL | SAMANDURU_66 | 1220201907020102 | F06-KODLIPURA | URBAN MIXED LOAD | DLMS Meter | 1.3734 | 0.61731 | 0.697 | 0.6764 | 8.7363 | 31.7952
4621 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902010101 | F01-THOVINAKERE | AGRI | DLMS Meter | 1.6636 | 1.4737 | 0 | 1.6636 | 11.418 | 11.418
4622 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902010102 | F02-SARIGEHALLI | AGRI | DLMS Meter | 1.7797 | 1.5746 | 0 | 1.7797 | 11.5234 | 11.5234
4623 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902010103 | F03-BYADRAHALLI | AGRI | DLMS Meter | 0.8287 | 0.74558 | 0 | 0.8287 | 10.0303 | 10.0303
4624 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902010104 | F04-RAMADIHALLI | AGRI | DLMS Meter | 0.99168 | 0.87685 | 0 | 0.99168 | 11.5792 | 11.5792
4625 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902020301 | F05-MALLENAHALLI | AGRI | DLMS Meter | 1.7465 | 1.3573 | 0.23 | 1.5165 | 10.4946 | 10.4946
4626 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902020302 | F06-SAMPIGE | AGRI | DLMS Meter | 1.6073 | 1.4468 | 0 | 1.6073 | 9.9836 | 9.9836
4627 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902020303 | F07-ANGARICANAHALLI | AGRI | DLMS Meter | 0.71482 | 0.64316 | 0 | 0.71482 | 10.0256 | 10.0256
4628 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902020304 | F08-HALESAMPIGE | AGRI | DLMS Meter | 0.81532 | 0.73372 | 0 | 0.81532 | 10.0078 | 10.0078
4629 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902020305 | F09-MACHENAHALLI NJY | NJY | DLMS Meter | 0.41166 | 0.30378 | 0.063 | 0.34866 | 12.8714 | 34.5561
4630 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902020306 | F10-BASAVAPURA NJY | NJY | DLMS Meter | 0.51609 | 0.37866 | 0.079 | 0.43709 | 13.3686 | 37.4888
4631 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902020307 | F11-RAGADEVAHALLI NJY | NJY | DLMS Meter | 0.0998 | 0.088012 | 0 | 0.0998 | 11.8116 | 26.074
4632 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902020308 | F12-DODDATTI | AGRI | DLMS Meter | 1.5528 | 1.3942 | 0 | 1.5528 | 10.2148 | 10.2148
4633 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902020309 | F13-BC KAWALU | AGRI | DLMS Meter | 0.9288 | 0.82307 | 0 | 0.9288 | 11.3832 | 11.3832
4634 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | SAMPIGE_110 | 1320202902020310 | F14-YALLADABHAGI | AGRI | DLMS Meter | 0.5116 | 0.45502 | 0 | 0.5116 | 11.059 | 11.059
4635 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903020301 | F01-HULIKUNTE | AGRI | DLMS Meter | 1.2092 | 1.0824 | 0 | 1.2092 | 10.4869 | 10.4869
4636 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903010101 | F02-KAMMATHMARIKUNTE | AGRI | DLMS Meter | 0.967 | 0.85437 | 0 | 0.967 | 11.6472 | 11.6472
4637 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903010102 | F03-CHIKKANAHALLY | AGRI | DLMS Meter | 1.0677 | 0.94965 | 0 | 1.0677 | 11.0584 | 11.0584
4638 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903010103 | F04-SANIKERE | AGRI | DLMS Meter | 0.9264 | 0.83384 | 0 | 0.9264 | 9.9909 | 9.9909
4639 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903010104 | F05-SONDEKERE | AGRI | DLMS Meter | 0.74564 | 0.27583 | 0 | 0.74564 | 11.0442 | 11.0442
4640 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903020302 | F06-HEGGERE | AGRI | DLMS Meter | 0.7906 | 0.69859 | 0 | 0.7906 | 11.6381 | 11.6381
4641 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903020303 | F07-GOPANAHALLY | AGRI | DLMS Meter | 0.63032 | 0.56417 | 0 | 0.63032 | 10.495 | 10.495
4642 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903010105 | F08-IDLE1 | IDLE | DLMS Meter | 0 | 24.7616 | 0 | 0 | 0 | #DIV/0!
4643 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903020304 | F09-BHAGAVANTHA NJY | NJY | DLMS Meter | 0.95444 | 0.43138 | 0.4627 | 0.49174 | 12.275 | 68.4905
4644 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903020305 | F10-KAPARAHALLY NJY | NJY | DLMS Meter | 0.3075 | 0.27213 | 0 | 0.3075 | 11.5037 | 64.0107
4645 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | SANIKERE_66 | 1310402903020306 | F12-UJJANI NJY | NJY | DLMS Meter | 0.8399 | 0.74277 | 0 | 0.8399 | 11.5647 | 49.3333
4646 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | SANKALAGERE_66 | 1220104905010201 | F01-HOSURUDODDI | AGRI | DLMS Meter | 0.65828 | 0.59225 | 0 | 0.65828 | 10.0311 | 10.0311
4647 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | SANKALAGERE_66 | 1220104905010202 | F02- SEEBANAHALLY IP | AGRI | DLMS Meter | 1.0842 | 0.9758 | 0 | 1.0842 | 9.9986 | 9.9986
4648 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | SANKALAGERE_66 | 1220104905010203 | F03-KOLURU NJY | NJY | DLMS Meter | 0.74986 | 0.58349 | 0.11333 | 0.63653 | 8.3321 | 21.7265
4649 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | SANKALAGERE_66 | 1220104905010204 | F04-MYLANAYKANAHALLY | NJY | DLMS Meter | 0.68156 | 0.47978 | 0.1539 | 0.52766 | 9.0737 | 26.7201
4650 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | SANKALAGERE_66 | 1220104905010205 | F05-THORE HOSURU | AGRI | DLMS Meter | 0.6945 | 0.62499 | 0 | 0.6945 | 10.0082 | 10.0082
4651 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | SANKALAGERE_66 | 1220104905010206 | F06-BELAKERE | AGRI | DLMS Meter | 1.0678 | 0.80331 | 0.175 | 0.8928 | 10.0235 | 10.0235
4652 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901010101 | F01-DODDAMALLAPURA IP | AGRI | DLMS Meter | 1.1008 | 0.89532 | 0.106 | 0.99478 | 9.9978 | 9.9978
4653 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901010102 | F02-SIDDANAMATA | AGRI | DLMS Meter | 2.2883 | 2.0604 | 0 | 2.2883 | 9.9611 | 9.9611
4654 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901010103 | F03-KAKANURU IP | AGRI | DLMS Meter | 1.0711 | 0.96408 | 0 | 1.0711 | 9.9901 | 9.9901
4655 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901010104 | F04-SANTEBENNUR | NJY | DLMS Meter | 0.83328 | 0.73905 | 0.0265 | 0.80678 | 8.3953 | 22.428
4656 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901020301 | F05-BELLIGANODU | AGRI | DLMS Meter | 1.1744 | 1.0576 | 0 | 1.1744 | 9.9515 | 9.9515
4657 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901010105 | F06-CHIKKUDA IP | AGRI | DLMS Meter | 0.95886 | 0.86279 | 0 | 0.95886 | 10.0187 | 10.0187
4658 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901020302 | F07-ARALIKATTE IP | AGRI | DLMS Meter | 1.0986 | 0.98892 | 0 | 1.0986 | 9.9822 | 9.9822
4659 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901020303 | F08-THANIGERE | AGRI | DLMS Meter | 2.2838 | 2.0554 | 0 | 2.2838 | 10.0011 | 10.0011
4660 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901020304 | F09-CHIKKABENNURU | NJY | DLMS Meter | 1.7729 | 0.35723 | 1.373 | 0.39992 | 10.6739 | 35.7424
4661 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901020305 | F10-HIREKOGALUR | NJY | DLMS Meter | 2.0969 | 0.96736 | 1.011 | 1.0859 | 10.9199 | 35.6441
4662 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901020306 | F11-DODDAABBIGERE | NJY | DLMS Meter | 0.78068 | 0.55183 | 0.1585 | 0.62218 | 11.3064 | 47.4569
4663 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SANTEBENNUR_66 | 1310107901020308 | F12-ABBIGERE IP | AGRI | DLMS Meter | 0.8956 | 0.60083 | 0.228 | 0.6676 | 10.0018 | 10.0018
4664 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | SANTEMAVATTUR_66 | 1320109902010101 | F01-BORASANDRA | AGRI | DLMS Meter | 0.49156 | 0.4425 | 0 | 0.49156 | 9.9815 | 9.9815
4665 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | SANTEMAVATTUR_66 | 1320109902010102 | F02-SANTEMAVATTUR | AGRI | DLMS Meter | 0.61258 | 0.55113 | 0 | 0.61258 | 10.031 | 10.031
4666 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | SANTEMAVATTUR_66 | 1320109902010103 | F03-MODUR | AGRI | DLMS Meter | 0.63032 | 0.5672 | 0 | 0.63032 | 10.0144 | 10.0144
4667 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | SANTEMAVATTUR_66 | 1320109902010105 | F04-DODDAMAVATHURU | AGRI | DLMS Meter | 0.63756 | 0.57354 | 0 | 0.63756 | 10.0409 | 10.0409
4668 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | SANTEMAVATTUR_66 | 1320109902020301 | F05-S.KEMPANAHALLI NJY | NJY | DLMS Meter | 1.2641 | 1.1631 | 0 | 1.2641 | 7.9866 | 16.9958
4669 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | SANTEMAVATTUR_66 | 1320109902020302 | F06-THARIKERE | AGRI | DLMS Meter | 0.71678 | 0.63962 | 0 | 0.71678 | 10.7645 | 10.7645
4670 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | SANTEMAVATTUR_66 | 1320109902010106 | F07-HITHALAHALLI | AGRI | DLMS Meter | 0.49306 | 0.44176 | 0 | 0.49306 | 10.4036 | 10.4036
4671 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | SANTEMAVATTUR_66 | 1320109902020303 | F08-KITHNAMANGALA | AGRI | DLMS Meter | 0.6059 | 0.54529 | 0 | 0.6059 | 10.0038 | 10.0038
4672 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | SANTEMAVATTUR_66 | 1320109902010104 | F09-IPPADI | AGRI | DLMS Meter | 0.43591 | 0.3922 | 0 | 0.43591 | 10.0282 | 10.0282
4673 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | SANTEMAVATTUR_66 | 1320109902020304 | F10-T.HOSAHALLI NJY | NJY | DLMS Meter | 2.2234 | 1.7345 | 0.323 | 1.9004 | 8.7273 | 29.6936
4674 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902010101 | F01-MUGLOOR | URBAN MIXED LOAD | DLMS Meter | 2.2347 | 1.3718 | 0.782 | 1.4527 | 5.5668 | 12.3459
4675 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902010102 | F02-DASARHALLI | AGRI | DLMS Meter | 1.596 | 1.4368 | 0 | 1.596 | 9.9743 | 10.7806
4676 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902010103 | F03-SARJAPURA-TOWN | URBAN MIXED LOAD | DLMS Meter | 4.2259 | 3.2426 | 0.72 | 3.5059 | 7.5115 | 13.4112
4677 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902010104 | F04-HANDENAHALLI | AGRI | DLMS Meter | 0.72828 | 0.65546 | 0 | 0.72828 | 9.999 | 11.2201
4678 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902010105 | F05-MUGLOOR-URBAN | URBAN MIXED LOAD | DLMS Meter | 1.8947 | 1.7424 | 0 | 1.8947 | 8.0378 | 8.0378
4679 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902020301 | F08-S-MEDIHALLY | URBAN MIXED LOAD | DLMS Meter | 3.2906 | 2.7416 | 0.3 | 2.9906 | 8.3258 | 14.0599
4680 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902020302 | F09-BILLAPURA SJP | AGRI | DLMS Meter | 2.715 | 2.4438 | 0 | 2.715 | 9.9877 | 9.9877
4681 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902020304 | F10-KUTHAGNAHALLY URBAN | URBAN MIXED LOAD | DLMS Meter | 2.3144 | 1.3823 | 0.824 | 1.4904 | 7.2518 | 23.3394
4682 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902020305 | F11-NJY HANDENAHALLY | NJY | DLMS Meter | 0.21 | 0.19464 | 0 | 0.21 | 7.3122 | 65.6614
4683 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902020303 | F12-BIDARAGUPPE | URBAN MIXED LOAD | DLMS Meter | 3.7459 | 2.6846 | 0.861 | 2.8849 | 6.943 | 6.943
4684 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902020306 | F13-CITY LIGHT | URBAN MIXED LOAD | DLMS Meter | 4.7444 | 1.3652 | 3.265 | 1.4794 | 7.7171 | 18.7749
4685 | BRAZ | RAMANAGAR | CHANDAPURA | ATTIBELE | SARAJAPURA_220 | 1220202902010108 | F14-KNS LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0.32224 | 0.0022398 | 0.31989 | 0.002347 | 4.5675 | 22.6435
4686 | BMASZ | SOUTH | JAYANAGAR | S6 | SARAKKI_66 | 1110104901010201 | F01-BRIGADE SOFTWARE | COMMERCIAL | DLMS Meter | 1.3852 | 1.2902 | 0.013256 | 1.372 | 5.958 | 17.8508
4687 | BMASZ | SOUTH | JAYANAGAR | S6 | SARAKKI_66 | 1110104901010205 | F02-NAGARJUNA-ENCLAVE | DOMESTIC | DLMS Meter | 3.078 | 2.5616 | 0.35034 | 2.7277 | 6.0864 | 12.2281
4688 | BMASZ | SOUTH | JAYANAGAR | S1 | SARAKKI_66 | 1110104901010202 | F03-RAJA-LAKSHMI-RMU-TH-BLOCK | URBAN MIXED LOAD | DLMS Meter | 1.3274 | 1.2174 | 0 | 1.3274 | 8.2888 | 8.2888
4689 | BMASZ | SOUTH | JAYANAGAR | S6 | SARAKKI_66 | 1110104901010203 | F04-RMU-JP-NAGAR | DOMESTIC | DLMS Meter | 5.4319 | 5.1256 | 0.025652 | 5.4063 | 5.1917 | 9.4509
4690 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901020401 | F05-BANNERGHATTA-RURAL | DOMESTIC | DLMS Meter | 2.6536 | 2.5245 | 0 | 2.6536 | 4.865 | 17.0241
4691 | BMASZ | SOUTH | JAYANAGAR | S1 | SARAKKI_66 | 1110104901010102 | F07-FJAYANAGAR-TH-CROSS-RMU | URBAN MIXED LOAD | DLMS Meter | 2.664 | 2.1401 | 0.2895 | 2.3745 | 9.8731 | 12.5508
4692 | BMASZ | SOUTH | JAYANAGAR | S6 | SARAKKI_66 | 1110104901010103 | F08-JP-NAGAR-TH-PHASE | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4693 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901010105 | F09-IDLE | IDLE | DLMS Meter | 0.36899 | 0.35701 | 0 | 0.36899 | 3.2476 | 5.1719
4694 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901020402 | F10-DOLLARS-COLONY | DOMESTIC | DLMS Meter | 4.5076 | 4.2961 | 0 | 4.5076 | 4.6917 | 8.1672
4695 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901020403 | F11-BANNERGHATTA-IND-AREA | URBAN MIXED LOAD | DLMS Meter | 4.5958 | 4.1087 | 0.40454 | 4.1913 | 1.9709 | 1.9709
4696 | BMASZ | SOUTH | JAYANAGAR | S1 | SARAKKI_66 | 1110104901010204 | F12-JSS | URBAN MIXED LOAD | DLMS Meter | 1.6385 | 1.4856 | 0 | 1.6385 | 9.3334 | 11.5297
4697 | BMASZ | SOUTH | JAYANAGAR | S6 | SARAKKI_66 | 1110104901030501 | F13-JARAGANAHALLI | DOMESTIC | DLMS Meter | 2.9654 | 1.86 | 0.99613 | 1.9693 | 5.5475 | 9.1432
4698 | BMASZ | SOUTH | JAYANAGAR | S6 | SARAKKI_66 | 1110104901030502 | F14-SARAKKI-VILLAGE | DOMESTIC | DLMS Meter | 2.8879 | 2.6705 | 0.11627 | 2.7716 | 3.6504 | 9.358
4699 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901030504 | F16-SHANTI-APPARTMENTS | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4700 | BMASZ | SOUTH | JAYANAGAR | S1 | SARAKKI_66 | 1110104901030505 | F17-TH-MAIN-RMU-JAYANAGAR | URBAN MIXED LOAD | DLMS Meter | 2.7153 | 2.4424 | 0.0075 | 2.7078 | 9.8025 | 11.8202
4701 | BMASZ | SOUTH | JAYANAGAR | S6 | SARAKKI_66 | 1110104901030601 | F18-WMS-COMPOUND | DOMESTIC | DLMS Meter | 1.6136 | 1.5168 | 0 | 1.6136 | 5.9981 | 5.9981
4702 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901030101 | F19-RMU-JP-NAGAR-TH-PHASE | DOMESTIC | DLMS Meter | 1.9824 | 1.5104 | 0.39239 | 1.59 | 5.0065 | 5.8806
4703 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901030602 | F20-SAD-RMU | DOMESTIC | DLMS Meter | 2.2626 | 2.0045 | 0.13545 | 2.1271 | 5.7632 | 7.0023
4704 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901010104 | F21-F2124TH MAIN 5TH PHASE JP NAGAR | DOMESTIC | DLMS Meter | 3.1735 | 2.7758 | 0.23632 | 2.9372 | 5.4948 | 10.5428
4705 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901010206 | F23-KR-LAYOUT | DOMESTIC | DLMS Meter | 2.5565 | 1.6307 | 0.78645 | 1.77 | 7.8708 | 12.3906
4706 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901020404 | F24-JP-NAGAR-ND-PHASE | DOMESTIC | DLMS Meter | 4.5686 | 4.3487 | 0 | 4.5686 | 4.8148 | 9.9008
4707 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901030507 | F26-KALYANI-MAGNUM | COMMERCIAL | DLMS Meter | 2.6995 | 2.6816 | 0.004945 | 2.6945 | 0.48052 | 0.48052
4708 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901010207 | F27-MANTRI-JUNCTION | COMMERCIAL | DLMS Meter | 1.201 | 1.0837 | 0.035551 | 1.1655 | 7.0175 | 44.2362
4709 | BMASZ | SOUTH | JAYANAGAR | S14 | SARAKKI_66 | 1110104901020406 | F28-KRISHNA-MAGNUM | COMMERCIAL | DLMS Meter | 1.2769 | 1.278 | -0.002845 | 1.2798 | 0.13956 | 0.13956
4710 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904010101 | F01-GYAREHALLI | AGRI | DLMS Meter | 1.325 | 1.1667 | 0 | 1.325 | 11.9512 | 11.9512
4711 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904010102 | F02-TBNAGARA | AGRI | DLMS Meter | 0.15842 | 0.13963 | 0 | 0.15842 | 11.8615 | 11.8615
4712 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904010103 | F03-MUTTUGADURU | AGRI | DLMS Meter | 1.27 | 1.1071 | 0 | 1.27 | 12.8322 | 12.8322
4713 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904010104 | F04-KALGHATTA | AGRI | DLMS Meter | 1.2615 | 1.1049 | 0 | 1.2615 | 12.4132 | 12.4132
4714 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904020301 | F05-ANDANUR | AGRI | DLMS Meter | 0.7097 | 0.63869 | 0 | 0.7097 | 10.0056 | 10.0056
4715 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904020302 | F06-PGCL | INDUSTRIAL | DLMS Meter | 0.26726 | 0.2684 | 0 | 0.26726 | -0.42636 | 1.0773
4716 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904020303 | F07-DANDIGENAHALLI | AGRI | DLMS Meter | 1.3369 | 1.1691 | 0 | 1.3369 | 12.5466 | 12.5466
4717 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904020304 | F08-HIREHEMMIGANUR | AGRI | DLMS Meter | 2.305 | 1.9831 | 0 | 2.305 | 13.9641 | 13.9641
4718 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904020305 | F09-THOPPENAHALLI NJY | NJY | DLMS Meter | 1.5088 | 0.60263 | 0.82617 | 0.68264 | 11.7207 | 56.0892
4719 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904010105 | F10-UDUGIRI NJY | NJY | DLMS Meter | 0.90438 | 0.38347 | 0.46938 | 0.435 | 11.8457 | 48.8339
4720 | CTAZ | DAVANAGERE | CHITRADURGA | HOLALKERE | SASALUHALLA_66 | 1310203904010106 | F11-SIRIGERE WATER SUPPLY | WATER WORKS | DLMS Meter | 0.35315 | 0.35505 | 0 | 0.35315 | -0.53802 | -0.53802
4721 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906010101 | F01-CHANNENAHALLI AGRI | AGRI | DLMS Meter | 1.7595 | 1.583 | 0 | 1.7595 | 10.032 | 10.032
4722 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906010102 | F02-KYSINKERE | AGRI | DLMS Meter | 1.7784 | 1.5993 | 0 | 1.7784 | 10.0669 | 10.0669
4723 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906010103 | F03-LINGAPURA | AGRI | DLMS Meter | 1.3409 | 1.2072 | 0 | 1.3409 | 9.9733 | 9.9733
4724 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906010104 | F04-RAMPURA | AGRI | DLMS Meter | 0.45389 | 0.40885 | 0 | 0.45389 | 9.9229 | 9.9229
4725 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906020301 | F05-KULAGATTE NJY | NJY | DLMS Meter | 1.8478 | 0.56256 | 1.2176 | 0.63017 | 10.7292 | 25.4963
4726 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906020302 | F06-BAGEWADI | AGRI | DLMS Meter | 1.1453 | 1.0005 | 0 | 1.1453 | 12.6423 | 12.6423
4727 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906020303 | F07-TYAGADAKATTE IP | AGRI | DLMS Meter | 0.91692 | 0.81963 | 0 | 0.91692 | 10.6099 | 10.6099
4728 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906020304 | F08-SASUVEHALLI | NJY | DLMS Meter | 0.7598 | 0.59264 | 0.095469 | 0.66433 | 10.7908 | 17.3933
4729 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906020305 | F09-CHIKKABASURU THANDA NJY | NJY | DLMS Meter | 1.1062 | 0.51134 | 0.53235 | 0.57385 | 10.8923 | 30.179
4730 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906020306 | F10-HANAGAVADI NJY | NJY | DLMS Meter | 2.7718 | 0.71403 | 1.9688 | 0.80298 | 11.0771 | 14.1399
4731 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906010107 | F11-HOTYAPURA AGRI | AGRI | DLMS Meter | 0.4328 | 0.38942 | 0 | 0.4328 | 10.0226 | 10.0226
4732 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906010105 | F12-BENAKANAHALLI AGRI | AGRI | DLMS Meter | 1.0843 | 0.97576 | 0 | 1.0843 | 10.0086 | 10.0086
4733 | CTAZ | DAVANAGERE | HARIHARA | HONNALI | SASUVEHALLI_66 | 1310302906010106 | F13-HIREBASURU AGRI | AGRI | DLMS Meter | 0.6696 | 0.60316 | 0 | 0.6696 | 9.9226 | 9.9226
4734 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | SAVALANGA_66 | 1310302908010101 | F01-SAVALANGA | NJY | DLMS Meter | 0.78785 | 0.6641 | 0.03836 | 0.74949 | 11.3933 | 39.6874
4735 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | SAVALANGA_66 | 1310302908010102 | F02-GANJENAHALLI | AGRI | DLMS Meter | 0.78794 | 0.6972 | 0 | 0.78794 | 11.5167 | 11.5167
4736 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | SAVALANGA_66 | 1310302908010104 | F03-CHINNIKATTE | AGRI | DLMS Meter | 0.79212 | 0.71273 | 0 | 0.79212 | 10.0229 | 10.0229
4737 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | SAVALANGA_66 | 1310302908010103 | F04-MACHAGONDANAHALLI | AGRI | DLMS Meter | 0.73456 | 0.6611 | 0 | 0.73456 | 10.0003 | 10.0003
4738 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | SAVALANGA_66 | 1310302908010105 | F05-KODATALU | NJY | DLMS Meter | 0.6177 | 0.51872 | 0.0315 | 0.5862 | 11.5118 | 52.4458
4739 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | SAVALANGA_66 | 1310302908020301 | F06-MADAPURA | AGRI | DLMS Meter | 0.9098 | 0.80567 | 0 | 0.9098 | 11.4454 | 11.4454
4740 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | SAVALANGA_66 | 1310302908020101 | F07-KANAVEVEERABHADRESHWRA | AGRI | DLMS Meter | 0.9343 | 0.83842 | 0 | 0.9343 | 10.2623 | 10.2623
4741 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | SAVALANGA_66 | 1310302908020302 | F08-KYATHINAKOPPA | AGRI | DLMS Meter | 0.8202 | 0.7305 | 0 | 0.8202 | 10.9365 | 10.9365
4742 | CTAZ | DAVANAGERE | HARIHARA | NYAMATHI | SAVALANGA_66 | 1310302908020303 | F09-JAYANAGARA | AGRI | DLMS Meter | 0.7954 | 0.69185 | 0 | 0.7954 | 13.0192 | 13.0192
4743 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010301 | F02-D-BLOCK-CSS | DOMESTIC | DLMS Meter | 0.66504 | 0.62043 | 0 | 0.66504 | 6.7078 | 8.8409
4744 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010302 | F03-PRW | DOMESTIC | DLMS Meter | 2.1067 | 2.0763 | 0 | 2.1067 | 1.4437 | 1.4437
4745 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010303 | F04-CR-BLOCK | DOMESTIC | DLMS Meter | 3.5109 | 1.8633 | 1.5563 | 1.9546 | 4.6741 | 4.6741
4746 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010304 | F05-SAN-&-HERBERT,-ITPL-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.9243 | 1.4779 | 2.3539 | 1.5705 | 5.8962 | 13.5571
4747 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010305 | F06-F-TIKMANI-STEELS,-ITPL-ROAD | URBAN MIXED LOAD | DLMS Meter | 5.037 | 4.5762 | 0.35562 | 4.6814 | 2.248 | 2.248
4748 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010101 | F07-F-A-BLOCK-CSS | DOMESTIC | DLMS Meter | 1.2574 | 1.2228 | 0 | 1.2574 | 2.7568 | 4.7587
4749 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010102 | F08-C-BLOCK-CSS | DOMESTIC | DLMS Meter | 0.57777 | 0.43293 | 0.11489 | 0.46288 | 6.4701 | 9.3433
4750 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010103 | F09-F-BLOCK-CSS | DOMESTIC | DLMS Meter | 1.1581 | 1.104 | 0 | 1.1581 | 4.6635 | 5.7444
4751 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010104 | F10-MLCP-BLOCK | COMMERCIAL | DLMS Meter | 2.9406 | 2.898 | 0 | 2.9406 | 1.4487 | 1.4487
4752 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010105 | F11-KTPO,-EPIP-L/O | URBAN MIXED LOAD | DLMS Meter | 7.2071 | 7.0817 | 0 | 7.2071 | 1.7388 | 1.7388
4753 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010106 | F12-GR-TECH-PARK,-ITPL-ROAD | URBAN MIXED LOAD | DLMS Meter | 1.1452 | 1.1048 | 0 | 1.1452 | 3.5265 | 7.2396
4754 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010107 | F13-MAGNA-WAREHOUSE,-EPIP-L/O | URBAN MIXED LOAD | DLMS Meter | 5.5979 | 2.1457 | 3.3613 | 2.2366 | 4.0635 | 14.0307
4755 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010108 | F14-SYMPHONY,-EPIP-L/O | URBAN MIXED LOAD | DLMS Meter | 3.8937 | 3.5795 | 0.25 | 3.6437 | 1.7616 | 8.5841
4756 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010110 | F16-TOWERC | DOMESTIC | DLMS Meter | 2.6838 | 2.6446 | 0 | 2.6838 | 1.4589 | 1.4589
4757 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904020301 | F17-TOTAL ENVIRNAMENT | URBAN MIXED LOAD | DLMS Meter | 4.7091 | 3.1312 | 1.4406 | 3.2685 | 4.2018 | 7.5074
4758 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010113 | F18-SHERATON-GRAND-HOTEL | COMMERCIAL | DLMS Meter | 1.9035 | 1.8787 | 0 | 1.9035 | 1.3008 | 27.9935
4759 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010115 | F19-BRIGADE LAKEFRONT | DOMESTIC | DLMS Meter | 1.1575 | 1.1136 | 0 | 1.1575 | 3.7973 | 5.0672
4760 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | #N/A | F20-FORUM MALL | #N/A | DLMS Meter | 3.3049 | 3.2597 | 0 | 3.3049 | 1.3672 | 1.3672
4761 | BMANZ | EAST | WHITEFIELD | E4 | SHANTHINIKETHAN_66 | 1130202904010114 | F21-PRESTIGE LAKEVIEW | DOMESTIC | DLMS Meter | 0.44471 | 0.39479 | 0.02 | 0.42471 | 7.0452 | 7.0452
4762 | BMANZ | EAST | WHITEFIELD | E4 | SHANTHINIKETHAN_66 | 1130202904020306 | F22-PRESTIGE WHITE_MIDOUS | DOMESTIC | DLMS Meter | 1.0006 | 0.85229 | 0.095 | 0.90559 | 5.8862 | 7.0395
4763 | BMANZ | EAST | WHITEFIELD | E12 | SHANTHINIKETHAN_66 | 1130202904010116 | F23-VASWANI APPARTMENTS | DOMESTIC | DLMS Meter | 0.15359 | 0 | 0 | 0.15359 | 0 | #DIV/0!
4764 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904010101 | F01-GYAREHALLI | AGRI | DLMS Meter | 0.84066 | 0.74291 | 0 | 0.84066 | 11.6273 | 11.6273
4765 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904010102 | F02-SIDARAMANAGARA | AGRI | DLMS Meter | 0.88444 | 0.79622 | 0 | 0.88444 | 9.9743 | 9.9743
4766 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904010103 | F03-HESARAHALLI | AGRI | DLMS Meter | 0.79926 | 0.70605 | 0 | 0.79926 | 11.6625 | 11.6625
4767 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904010104 | F04-SHETTIKERE | AGRI | DLMS Meter | 0.76462 | 0.68773 | 0 | 0.76462 | 10.0565 | 10.0565
4768 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904010106 | F06-AGASARAHALLI-NJY | NJY | DLMS Meter | 0.34056 | 0.30799 | 0 | 0.34056 | 9.5628 | 31.7831
4769 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904020301 | F07-SASALU | AGRI | DLMS Meter | 0.4482 | 0.31343 | 0.1 | 0.3482 | 9.9859 | 9.9859
4770 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904020302 | F08-ARALIKERE | AGRI | DLMS Meter | 1.0165 | 0.91504 | 0 | 1.0165 | 9.9817 | 9.9817
4771 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904020303 | F09-BENAKANAKATTE | AGRI | DLMS Meter | 0.87768 | 0.7898 | 0 | 0.87768 | 10.0123 | 10.0123
4772 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904020304 | F10-AJJENAHALLI | AGRI | DLMS Meter | 0.70484 | 0.60276 | 0.035 | 0.66984 | 10.0137 | 10.0137
4773 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904010108 | F11-NAVILE | AGRI | DLMS Meter | 1.1723 | 1.0247 | 0 | 1.1723 | 12.5859 | 12.5859
4774 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904010107 | F12-RAJJAYANAPALLYA | AGRI | DLMS Meter | 0.41726 | 0.37545 | 0 | 0.41726 | 10.0204 | 10.0204
4775 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904010111 | F13-DUGADIHALLI-NJY | NJY | DLMS Meter | 0.167 | 0.15443 | 0 | 0.167 | 7.5293 | 57.164
4776 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904020305 | F14-GOPALANAHALLI-NJY | NJY | DLMS Meter | 0.34673 | 0.31204 | 0.002 | 0.34473 | 9.483 | 51.2928
4777 | BRAZ | RAMANAGAR | MAGADI | KUDUR | SHIVANASANDRA_66 | 1210103904010102 | F01-JANIGERE | AGRI | DLMS Meter | 1.111 | 0.97933 | 0 | 1.111 | 11.8511 | 11.8511
4778 | BRAZ | RAMANAGAR | MAGADI | KUDUR | SHIVANASANDRA_66 | 1210103904010103 | F02-KALARI | AGRI | DLMS Meter | 0.607 | 0.54629 | 0 | 0.607 | 10.0018 | 10.0018
4779 | BRAZ | RAMANAGAR | MAGADI | KUDUR | SHIVANASANDRA_66 | 1210103904010104 | F03-KODIPALYA | NJY | DLMS Meter | 0.3398 | 0.092155 | 0.237 | 0.1028 | 10.3549 | 38.9874
4780 | BRAZ | RAMANAGAR | MAGADI | KUDUR | SHIVANASANDRA_66 | 1210103904010101 | F04-THALEKERE | NJY | DLMS Meter | 1.0177 | 0.42013 | 0.551 | 0.4667 | 9.9784 | 41.0248
4781 | BRAZ | RAMANAGAR | MAGADI | KUDUR | SHIVANASANDRA_66 | 1210103904010105 | F06-CHIKMUDIGERE | AGRI | DLMS Meter | 0.9862 | 0.86641 | 0 | 0.9862 | 12.1465 | 12.1465
4782 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | SHIVANHALLI_66 | 1220103905010101 | F01-ANKANAHALLI | AGRI | DLMS Meter | 0.88087 | 0.79256 | 0 | 0.88087 | 10.0253 | 10.0253
4783 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | SHIVANHALLI_66 | 1220103905010102 | F02-KADANKUPPE | AGRI | DLMS Meter | 0.71218 | 0.64066 | 0 | 0.71218 | 10.0427 | 10.0427
4784 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | SHIVANHALLI_66 | 1220103905010103 | F03-BANNIKUPPE | AGRI | DLMS Meter | 1.194 | 1.0745 | 0 | 1.194 | 10.0061 | 10.0061
4785 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | SHIVANHALLI_66 | 1220103905010104 | F04-DODDANAHALLI | AGRI | DLMS Meter | 0.9902 | 0.89124 | 0 | 0.9902 | 9.9941 | 9.9941
4786 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | SHIVANHALLI_66 | 1220103905010106 | F05-SHIVANAHALLI NJY | NJY | DLMS Meter | 0.6471 | 0.46825 | 0.1298 | 0.5173 | 9.4823 | 40.5878
4787 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | SHIVANHALLI_66 | 1220103905020301 | F06-KAVANAPURA NJY | NJY | DLMS Meter | 0.2462 | 0.17872 | 0.0498 | 0.1964 | 9.0031 | 57.7701
4788 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | SHIVANHALLI_66 | 1220103905020302 | F07-LAKKOJANAHALLI NJY | NJY | DLMS Meter | 0.1814 | 0.1245 | 0.0446 | 0.1368 | 8.989 | 31.4122
4789 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | SHIVANHALLI_66 | 1220103905010107 | F08-BASAVESHWARA NJY | NJY | DLMS Meter | 0.14062 | 0.064498 | 0.07 | 0.07062 | 8.6689 | 33.3081
4790 | BRAZ | RAMANAGAR | RAMANAGAR | RAMANAGARA RURAL | SHIVANHALLI_66 | 1220103905020303 | F09-KAVERIDODDI | AGRI | DLMS Meter | 0.4916 | 0.39941 | 0.0478 | 0.4438 | 10.002 | 10.002
4791 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | SHIVANI_66 | 1310106907010101 | F03-CHIRANAHALLI | AGRI | DLMS Meter | 0.16097 | 0.027398 | 0.13054 | 0.030433 | 9.9727 | 9.9727
4792 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | SHIVANI_66 | 1310106907010102 | F12-DANDURU NJY | NJY | DLMS Meter | 0.23391 | 0.004326 | 0.22922 | 0.004686 | 7.6825 | 44.8547
4793 | BMASZ | WEST | RAJAJINAGAR | N8 | SHRIGANDHADKAVAL_66 | 1140104901010101 | F02-SUNKADAKATTE_INDL_AREA | URBAN MIXED LOAD | DLMS Meter | 3.1705 | 2.7584 | 0.26656 | 2.9039 | 5.0118 | 10.0288
4794 | BMASZ | WEST | RAJAJINAGAR | N6 | SHRIGANDHADKAVAL_66 | 1140104901010103 | F03-SHIVA FARM | URBAN MIXED LOAD | DLMS Meter | 1.6741 | 1.1868 | 0.42111 | 1.253 | 5.2782 | 10.2254
4795 | BMASZ | WEST | RAJAJINAGAR | N8 | SHRIGANDHADKAVAL_66 | 1140104901010102 | F04-MALLATHALLI_NGEF_LAYOUT | DOMESTIC | DLMS Meter | 2.4703 | 2.2434 | 0.092069 | 2.3782 | 5.6718 | 15.952
4796 | BMASZ | WEST | RAJAJINAGAR | N6 | SHRIGANDHADKAVAL_66 | 1140104901010104 | F06-NILIGIRI THOPU | URBAN MIXED LOAD | DLMS Meter | 4.184 | 3.7913 | 0.17655 | 4.0074 | 5.3938 | 8.9695
4797 | BMASZ | WEST | RAJAJINAGAR | N6 | SHRIGANDHADKAVAL_66 | 1140104901020104 | F07-HEGGANAHALLI | URBAN MIXED LOAD | DLMS Meter | 5.5205 | 5.2184 | 0 | 5.5205 | 5.4731 | 8.8027
4798 | BMASZ | WEST | RAJAJINAGAR | N6 | SHRIGANDHADKAVAL_66 | 1140104901020105 | F08-SHIVA TEMPLE KAMAKSHIPAYA | URBAN MIXED LOAD | DLMS Meter | 2.1891 | 0.89901 | 1.2411 | 0.94803 | 5.1705 | 13.8713
4799 | BMASZ | WEST | RAJAJINAGAR | N10 | SHRIGANDHADKAVAL_66 | #N/A | F09-PATTEGARPALYA | #N/A | DLMS Meter | 0.84838 | 0.74995 | 0.072334 | 0.77604 | 3.3619 | 23.9159
4800 | BMASZ | WEST | RAJAJINAGAR | N8 | SHRIGANDHADKAVAL_66 | 1140104901020101 | F10-ANNAPORNESHWARINAGAR | DOMESTIC | DLMS Meter | 3.8198 | 2.5574 | 1.0888 | 2.731 | 6.3582 | 13.659
4801 | BMASZ | WEST | RAJAJINAGAR | N8 | SHRIGANDHADKAVAL_66 | 1140104901020102 | F11-KOTTIGEPALYA_INDL_AREA | URBAN MIXED LOAD | DLMS Meter | 2.9663 | 2.7423 | 0.065494 | 2.9008 | 5.4649 | 12.9349
4802 | BMASZ | WEST | RAJAJINAGAR | N8 | SHRIGANDHADKAVAL_66 | 1140104901020103 | F12-KENGUNTE | DOMESTIC | DLMS Meter | 1.4473 | 1.4473 | 0 | 1.4473 | 0 | 12.3864
4803 | BMASZ | WEST | RAJAJINAGAR | N10 | SHRIGANDHADKAVAL_66 | 1140104901010105 | F13-SATHVA DEVELOPERS | DOMESTIC | DLMS Meter | 0.39036 | 0.37773 | 0 | 0.39036 | 3.2355 | 3.2355
4804 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | SHYAGALE_66 | 1310103906010101 | F01-KANDAGAL | AGRI | DLMS Meter | 1.0042 | 0.89126 | 0 | 1.0042 | 11.2465 | 11.2465
4805 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | SHYAGALE_66 | 1310103906010102 | F02-KODIHALLI | AGRI | DLMS Meter | 0.69612 | 0.62638 | 0 | 0.69612 | 10.0178 | 10.0178
4806 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | SHYAGALE_66 | 1310103906010103 | F03-GONIWADA | AGRI | DLMS Meter | 0.4633 | 0.38791 | 0.032 | 0.4313 | 10.0607 | 10.0607
4807 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | SHYAGALE_66 | 1310103906010104 | F04-NJ SHYAGALE | NJY | DLMS Meter | 0.84682 | 0.64799 | 0.1025 | 0.74432 | 12.9414 | 52.8766
4808 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901010101 | F01-K.T.HALLI | AGRI | DLMS Meter | 0.19043 | 0.1714 | 0 | 0.19043 | 9.9961 | 16.5981
4809 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901010102 | F02-DEVALAKERE | AGRI | DLMS Meter | 0.18647 | 0.16907 | 0 | 0.18647 | 9.3348 | 15.3933
4810 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901010103 | F04-VADANAKALLU | AGRI | DLMS Meter | 0.17761 | 0.1599 | 0 | 0.17761 | 9.9749 | 16.8551
4811 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901010105 | F05-A.H.PALYA | AGRI | DLMS Meter | 0.065782 | 0.059243 | 0 | 0.065782 | 9.9404 | 12.9083
4812 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901020101 | F06-KOTAGUDDA | AGRI | DLMS Meter | 1.2582 | 1.1389 | 0 | 1.2582 | 9.479 | 9.479
4813 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901020301 | F07--MARIDASANAHALLY | AGRI | DLMS Meter | 1.9178 | 1.7285 | 0 | 1.9178 | 9.87 | 9.87
4814 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901020102 | F08-BUDIDETA | AGRI | DLMS Meter | 0.96963 | 0.87825 | 0 | 0.96963 | 9.4238 | 9.4238
4815 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901010501 | F09-NJY BELLIBATLU | NJY | DLMS Meter | 0.6632 | 0.32265 | 0.305 | 0.3582 | 9.9238 | 80.3537
4816 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901010502 | F10-NJY B.HOSAHALLI | NJY | DLMS Meter | 0.305 | 0.27568 | 0 | 0.305 | 9.6141 | 38.6189
4817 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901010503 | F11-NJY YETTINAHALLI | NJY | DLMS Meter | 0.351 | 0.31589 | 0 | 0.351 | 10.0037 | 54.7067
4818 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | SHYLAPURA_66 | 1320306901010504 | F12-NJY GUJJUNODU | NJY | DLMS Meter | 1.0006 | 0.88916 | 0 | 1.0006 | 11.1371 | 72.4159
4819 | BRAZ | KOLAR | Chinthamani | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010101 | F01-LOCAL | URBAN MIXED LOAD | DLMS Meter | 2.838 | 2.5416 | 0 | 2.838 | 10.4441 | 26.5896
4820 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010102 | F02-IDLLODU | AGRI | DLMS Meter | 1.2178 | 0.84088 | 0.2835 | 0.93434 | 10.0022 | 10.0022
4821 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010103 | F03-ABLOODU | AGRI | DLMS Meter | 1.2953 | 1.024 | 0.15218 | 1.1431 | 10.4224 | 10.4224
4822 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010302 | F04-CHIKKABALLAPURA | AGRI | DLMS Meter | 0.90088 | 0.81062 | 0 | 0.90088 | 10.0191 | 10.0191
4823 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010104 | F05-ANOOR | AGRI | DLMS Meter | 1.5433 | 1.3841 | 0 | 1.5433 | 10.3134 | 10.3134
4824 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010105 | F06-JANGAMAKOTE | AGRI | DLMS Meter | 1.4288 | 1.282 | 0 | 1.4288 | 10.2754 | 10.2754
4825 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902020101 | F07-THIPPENAHALLI | AGRI | DLMS Meter | 0.99036 | 0.87843 | 0 | 0.99036 | 11.3017 | 11.3017
4826 | BRAZ | KOLAR | Chinthamani | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010303 | F08-MINI-VIDHANA-SOUDHA | GOVERNMENT OFFICES | DLMS Meter | 4.1405 | 3.643 | 0 | 4.1405 | 12.0143 | 19.2857
4827 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010106 | F10-HANUMANTH-PURA | NJY | DLMS Meter | 1.4369 | 1.3047 | 0 | 1.4369 | 9.199 | 40.9991
4828 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010107 | F11-LAKKAHALLI | AGRI | DLMS Meter | 1.2263 | 0.78492 | 0.35424 | 0.87204 | 9.9904 | 9.9904
4829 | BRAZ | KOLAR | Chinthamani | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010301 | F12-ASHOKA-ROAD | URBAN MIXED LOAD | DLMS Meter | 1.9151 | 1.6855 | 0 | 1.9151 | 11.9897 | 22.5691
4830 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010110 | F13-NJY HANDIGANALA | NJY | DLMS Meter | 1.174 | 0.72957 | 0.37132 | 0.80268 | 9.1072 | 10.2625
4831 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010111 | F14-NJY THUMMANAHALLI | NJY | DLMS Meter | 0.778 | 0.70488 | 0 | 0.778 | 9.3982 | 58.8918
4832 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010112 | F15-GUDIHALLI | AGRI | DLMS Meter | 1.0098 | 0.90882 | 0 | 1.0098 | 9.9996 | 9.9996
4833 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | SIDLAGHATTA_66 | 1230403902010113 | F16-BYRANAIKANAHALLI | AGRI | DLMS Meter | 0.56168 | 0.48108 | 0.023823 | 0.53786 | 10.5562 | 10.5562
4834 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | SIRA 220/66/11KV | 1320303905010102 | F01-KADAJJANAPALYA | AGRI | DLMS Meter | 0.5946 | 0.52237 | 0 | 0.5946 | 12.1477 | 12.1477
4835 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | SIRA 220/66/11KV | 1320303905010101 | F02-PANJIGANAHALLI | NJY | DLMS Meter | 0.7092 | 0.63687 | 0 | 0.7092 | 10.199 | 30.1974
4836 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | SIRA 220/66/11KV | 1320303905010103 | F04-KAGGALADU | AGRI | DLMS Meter | 0.0482 | 0.04351 | 0 | 0.0482 | 9.7303 | 9.7303
4837 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903010101 | F01-KAMATH-NJY | NJY | DLMS Meter | 0.40572 | 0.36906 | 0 | 0.40572 | 9.0363 | 36.3245
4838 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903010102 | F02-YELIYURU | AGRI | DLMS Meter | 1.0507 | 0.94583 | 0 | 1.0507 | 9.9806 | 9.9806
4839 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903010103 | F03-MEKERAHALLI | AGRI | DLMS Meter | 1.9778 | 1.721 | 0 | 1.9778 | 12.9844 | 12.9844
4840 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903010104 | F04-SIRASKG | URBAN MIXED LOAD | DLMS Meter | 2.2667 | 2.1167 | 0 | 2.2667 | 6.6203 | 14.6353
4841 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903010105 | F05-DEVARAHALLI | AGRI | DLMS Meter | 0.59494 | 0.5354 | 0 | 0.59494 | 10.0081 | 10.0081
4842 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903010301 | F06-MADALUR | AGRI | DLMS Meter | 1.2476 | 1.1225 | 0 | 1.2476 | 10.0245 | 10.0245
4843 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903010302 | F07-CHIKKERE | AGRI | DLMS Meter | 1.2299 | 1.1068 | 0 | 1.2299 | 10.008 | 10.008
4844 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903010303 | F08-SIRALODPURA | URBAN MIXED LOAD | DLMS Meter | 3.2151 | 2.9042 | 0 | 3.2151 | 9.6705 | 26.2109
4845 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903010304 | F09-SIRANH | URBAN MIXED LOAD | DLMS Meter | 2.5881 | 2.3625 | 0 | 2.5881 | 8.716 | 27.9895
4846 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903020501 | F11-MANANGI | AGRI | DLMS Meter | 1.0627 | 0.9351 | 0 | 1.0627 | 12.006 | 12.006
4847 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903020502 | F12-BENCHE NJY | NJY | DLMS Meter | 0.34048 | 0.29928 | 0 | 0.34048 | 12.1016 | 48.0266
4848 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903020503 | F13-BUTHAKATANAHALLI | AGRI | DLMS Meter | 1.345 | 1.2105 | 0 | 1.345 | 9.9955 | 9.9955
4849 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903020504 | F14-GM_HALLI | AGRI | DLMS Meter | 1.223 | 1.1007 | 0 | 1.223 | 9.998 | 9.998
4850 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903020505 | F15-BANDKUNTE | AGRI | DLMS Meter | 1.2711 | 1.144 | 0 | 1.2711 | 10.0025 | 10.0025
4851 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903020506 | F16-SIRAJYOTHINAGARA | URBAN MIXED LOAD | DLMS Meter | 1.2808 | 1.1982 | 0 | 1.2808 | 6.4429 | 21.9085
4852 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903020508 | F17-THOGARAGUNTE NJY | NJY | DLMS Meter | 0.9166 | 0.8186 | 0.0115 | 0.9051 | 9.5571 | 65.1448
4853 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902010101 | F01-KONANUR | NJY | DLMS Meter | 0.7935 | 0.33736 | 0.40521 | 0.38829 | 13.1162 | 23.9806
4854 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902010102 | F02-HALAUDARA | AGRI | DLMS Meter | 1.6446 | 1.4628 | 0 | 1.6446 | 11.056 | 11.056
4855 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902010103 | F03-OBALAPURA | AGRI | DLMS Meter | 0.71142 | 0.57543 | 0.063589 | 0.64783 | 11.1753 | 11.1753
4856 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902010104 | F04-ALAGWADI | AGRI | DLMS Meter | 0.82209 | 0.74003 | 0 | 0.82209 | 9.9823 | 9.9823
4857 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902020301 | F05-PALAKIHALLY | NJY | DLMS Meter | 0.73932 | 0.37995 | 0.30117 | 0.43815 | 13.2838 | 29.4586
4858 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902020302 | F06-MADAKARIPURA | AGRI | DLMS Meter | 0.73877 | 0.60267 | 0.075262 | 0.66351 | 9.1696 | 9.1696
4859 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902020303 | F07-SIDDAPURA | AGRI | DLMS Meter | 0.76562 | 0.68118 | 0 | 0.76562 | 11.0291 | 11.0291
4860 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902020304 | F08-SIRIGERE | NJY | DLMS Meter | 0.34476 | 0.25852 | 0.049499 | 0.29526 | 12.4439 | 20.0892
4861 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902020305 | F09-MEL(BBH) | INDUSTRIAL | DLMS Meter | 0.36562 | 0.36057 | 0 | 0.36562 | 1.3809 | 3.0659
4862 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902020306 | F10-CHIKKENAHALLI | AGRI | DLMS Meter | 1.2834 | 0.97952 | 0.17125 | 1.1122 | 11.9252 | 11.9252
4863 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902010501 | F11-ALAGHATTA | AGRI | DLMS Meter | 0.81542 | 0.53316 | 0.20185 | 0.61357 | 13.1051 | 13.1051
4864 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | SIRIGERE_66 | 1310202902010502 | F12-CHEELANGI | AGRI | DLMS Meter | 1.3078 | 1.1906 | 0 | 1.3078 | 8.9587 | 8.9587
4865 | BMASZ | WEST | RAJAJINAGAR | N8 | SIRMV_LAYOUT_66 | 1140301903010101 | F01-FGOVT.PRESS-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 5.6056 | 3.2737 | 2.1115 | 3.4941 | 6.3068 | 9.9215
4866 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010102 | F02-MARUTHI-NAGARA | URBAN MIXED LOAD | DLMS Meter | 2.7561 | 2.4641 | 0.1013 | 2.6548 | 7.1834 | 28.9334
4867 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010113 | F03-IDLE2 | IDLE | DLMS Meter | 2.5041 | 2.2642 | 0.075236 | 2.4289 | 6.7818 | 13.6315
4868 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010103 | F04-DODDABASTHI | URBAN MIXED LOAD | DLMS Meter | 2.2431 | 2.1118 | 0 | 2.2431 | 5.857 | 14.5081
4869 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010104 | F05-SONNENAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.703 | 3.3894 | 0.06753 | 3.6355 | 6.7691 | 14.8391
4870 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010105 | F06-FTH-BLOCK | URBAN MIXED LOAD | DLMS Meter | 2.7137 | 2.5363 | 0 | 2.7137 | 6.5375 | 15.1682
4871 | BMASZ | WEST | KENGERI | K1 | SIRMV_LAYOUT_66 | 1140301903010112 | F07-IDLE5 | IDLE | DLMS Meter | 1.8697 | 1.6447 | 0.16222 | 1.7075 | 3.6735 | 19.0134
4872 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010109 | F08-RAILWAYLAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.8992 | 1.7888 | 0 | 1.8992 | 5.813 | 18.3297
4873 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010107 | F10-S.M.V.7TH-BLACK | URBAN MIXED LOAD | DLMS Meter | 4.5026 | 4.1311 | 0.04 | 4.4626 | 7.4284 | 21.7144
4874 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010108 | F11-S.M.V.5TH-BLACK | URBAN MIXED LOAD | DLMS Meter | 4.7614 | 4.0424 | 0.4545 | 4.3069 | 6.1419 | 16.7088
4875 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010110 | F12-S.M.V.LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.5406 | 2.3808 | 0 | 2.5406 | 6.2901 | 22.8639
4876 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010111 | F13-S.M.V.6TH-BLACK | URBAN MIXED LOAD | DLMS Meter | 3.4319 | 2.6115 | 0.59612 | 2.8358 | 7.9101 | 19.527
4877 | BMASZ | WEST | KENGERI | K4 | SIRMV_LAYOUT_66 | 1140301903010301 | F15-KHB PLATINUM | DOMESTIC | DLMS Meter | 2.0183 | 1.3107 | 0.60387 | 1.4144 | 7.3342 | 14.1844
4878 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SMMANGALA_66 | 1230102907010101 | F01-THOTLY | AGRI | DLMS Meter | 1.1862 | 1.0584 | 0 | 1.1862 | 10.7714 | 10.7714
4879 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SMMANGALA_66 | 1230102907010102 | F02-SHETTIKUNTE | AGRI | DLMS Meter | 0.6058 | 0.36523 | 0.2 | 0.4058 | 9.998 | 10.1659
4880 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SMMANGALA_66 | 1230102907010103 | F03-ALERI | AGRI | DLMS Meter | 0.695 | 0.62831 | 0 | 0.695 | 9.5963 | 10.3882
4881 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SMMANGALA_66 | 1230102907010104 | F04-MADDERI | AGRI | DLMS Meter | 1.202 | 0.84877 | 0.25 | 0.952 | 10.843 | 10.843
4882 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SMMANGALA_66 | 1230102907020301 | F05-BALAGERE | AGRI | DLMS Meter | 1.1798 | 1.0676 | 0 | 1.1798 | 9.5073 | 26.0638
4883 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SMMANGALA_66 | 1230102907020302 | F07-CHINTANAHALLI | AGRI | DLMS Meter | 0.7046 | 0.40306 | 0.26 | 0.4446 | 9.3432 | 11.5465
4884 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SMMANGALA_66 | 1230102907010107 | F08-M N HALLI | AGRI | DLMS Meter | 0.0924 | 0.081941 | 0 | 0.0924 | 11.3193 | 12.9573
4885 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SMMANGALA_66 | 1230102907020303 | F09-SEEKAL | AGRI | DLMS Meter | 0.5784 | 0.52074 | 0 | 0.5784 | 9.9684 | 9.9684
4886 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SMMANGALA_66 | 1230102907010301 | F11-NJYMADANAHLLI | NJY | DLMS Meter | 0.9501 | 0.84864 | 0 | 0.9501 | 10.6789 | 73.9005
4887 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SMMANGALA_66 | 1230102907010105 | F12-NJYKAKINATTA | NJY | DLMS Meter | 1.095 | 0.97177 | 0 | 1.095 | 11.2509 | 71.4387
4888 | BMANZ | EAST | VIDHANASOUDHA | W3 | SOBHA _INDRAPRASTHA_66 | 1130101902010101 | F02-SOBHA INDRAPRASTHA 1 | DOMESTIC | DLMS Meter | 0.17215 | 0.1287 | 0.025 | 0.14715 | 12.5352 | 18.7663
4889 | BMANZ | EAST | VIDHANASOUDHA | W3 | SOBHA _INDRAPRASTHA_66 | 1130101902010102 | F03-SOBHA GLOBAL MALL 1 | COMMERCIAL | DLMS Meter | 3.9002 | 3.8522 | 0 | 3.9002 | 1.2311 | 1.2311
4890 | BMANZ | NORTH | MALLESHWARA | C1 | SOBHA _INDRAPRASTHA_66 | 1130101902010103 | F05-ROBERTSONBLOCK | URBAN MIXED LOAD | DLMS Meter | 1.4908 | 1.1684 | 0.215 | 1.2758 | 8.419 | 12.0089
4891 | BMANZ | NORTH | MALLESHWARA | C1 | SOBHA _INDRAPRASTHA_66 | 1130101902010104 | F06-BRAHMAPURAM | URBAN MIXED LOAD | DLMS Meter | 0.65773 | 0.63732 | 0 | 0.65773 | 3.1028 | 3.1028
4892 | BMANZ | EAST | VIDHANASOUDHA | W3 | SOBHA _INDRAPRASTHA_66 | 1130101902020101 | F08-SOBHA INDRAPRASTHA 2 | DOMESTIC | DLMS Meter | 0.34562 | 0.24262 | 0.0869 | 0.25872 | 6.2232 | 6.2232
4893 | BMANZ | EAST | VIDHANASOUDHA | W3 | SOBHA _INDRAPRASTHA_66 | 1130101902020102 | F09-SOBHA GLOBAL MALL 2 | COMMERCIAL | DLMS Meter | 0.44998 | 0 | 0.44998 | 0 | 0 | #DIV/0!
4894 | BMANZ | NORTH | MALLESHWARA | C1 | SOBHA _INDRAPRASTHA_66 | 1130101902020103 | F12-SRIRAMPURA POLICE STATION | URBAN MIXED LOAD | DLMS Meter | 1.3754 | 1.3301 | 0 | 1.3754 | 3.2948 | 3.2948
4895 | BMANZ | EAST | SHIVAJINAGAR | E9 | SOBHA_CITY_66 | 1130305904010101 | F02-SOBHA_MYKONOS_BLOCK3_4 | DOMESTIC | DLMS Meter | 0.61053 | 0.60284 | 0 | 0.61053 | 1.2586 | 1.2586
4896 | BMANZ | EAST | SHIVAJINAGAR | E9 | SOBHA_CITY_66 | 1130305904010102 | F04-SOBHA_MYKONOS_BLOCK_2 | DOMESTIC | DLMS Meter | 3.6755 | 3.5424 | 0 | 3.6755 | 3.6215 | 3.6215
4897 | BMANZ | EAST | SHIVAJINAGAR | E9 | SOBHA_CITY_66 | 1130305904010104 | F05-MANIPAL | URBAN MIXED LOAD | DLMS Meter | 5.2717 | 5.001 | 0 | 5.2717 | 5.136 | 5.6333
4898 | BMANZ | EAST | SHIVAJINAGAR | E9 | SOBHA_CITY_66 | 1130305904010103 | F06-CLUBHOUSE_BLOCK_12 | DOMESTIC | DLMS Meter | 0.27514 | 0.26465 | 0 | 0.27514 | 3.8102 | 3.8102
4899 | BMANZ | EAST | SHIVAJINAGAR | E9 | SOBHA_CITY_66 | 1130305904020101 | F07-SOBHA_SANTORINI_BLOCK_9_10 | DOMESTIC | DLMS Meter | 5.7764 | 4.9721 | 0.38956 | 5.3868 | 7.699 | 13.0383
4900 | BMANZ | EAST | SHIVAJINAGAR | E9 | SOBHA_CITY_66 | 1130305904020102 | F08-SOBHA_CASA_SERENITA_BLOCK_13 | DOMESTIC | DLMS Meter | 0.45322 | 0.43929 | 0 | 0.45322 | 3.0721 | 4.9175
4901 | BMANZ | EAST | SHIVAJINAGAR | E9 | SOBHA_CITY_66 | 1130305904020103 | F09-SOBHA_CASA_PARADISO_BLOCK_17 | DOMESTIC | DLMS Meter | 0.55914 | 0.52315 | 0 | 0.55914 | 6.4372 | 6.4372
4902 | BMANZ | EAST | SHIVAJINAGAR | E9 | SOBHA_CITY_66 | 1130305904020106 | F12 BELLAHALLI | URBAN MIXED LOAD | DLMS Meter | 0.19561 | 0 | 0.19561 | -3.802e-13 | 0 | #DIV/0!
4903 | BMASZ | SOUTH | HSR | S12 | SOBHA_FORESTVIEW_66 | 1110304904010201 | F01-BLOCK 01 & 02 | DOMESTIC | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4904 | BMASZ | SOUTH | HSR | S12 | SOBHA_FORESTVIEW_66 | 1110304904010202 | F02-BLOCK 03 & 04 | DOMESTIC | DLMS Meter | 0.59177 | 0.51756 | 0 | 0.59177 | 12.5412 | 22.8398
4905 | BMASZ | SOUTH | HSR | S12 | SOBHA_FORESTVIEW_66 | 1110304904010203 | F03-BLOCK 05 & 06 | DOMESTIC | DLMS Meter | 0.42199 | 0.368 | 0 | 0.42199 | 12.7941 | 21.1294
4906 | BMASZ | SOUTH | HSR | S12 | SOBHA_FORESTVIEW_66 | 1110304904010204 | F04-BLOCK 07 & 08 | DOMESTIC | DLMS Meter | 1.3828 | 1.2113 | 0.012 | 1.3708 | 11.6364 | 21.4127
4907 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902010101 | F01-RMZ-ECO-WORLD | URBAN MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4908 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902010103 | F02--RMZ-ECO-WORLD | INDUSTRIAL | DLMS Meter | 0.67082 | 0 | 0.49107 | 0.17975 | 0 | #DIV/0!
4909 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902020101 | F03-KAIKONDRAHALLI | DOMESTIC | DLMS Meter | 6.758 | 6.4748 | 0 | 6.758 | 4.1901 | 6.9968
4910 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902020102 | F04-CESSNA-GARDEN-B | URBAN MIXED LOAD | DLMS Meter | 0.52497 | 0.43175 | 0.075 | 0.44997 | 4.0497 | 4.0497
4911 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902020103 | F05-IBLUR | URBAN MIXED LOAD | DLMS Meter | 2.7879 | 0.81192 | 1.93 | 0.85792 | 5.3626 | 6.5002
4912 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902020104 | F06-FAKME | URBAN MIXED LOAD | DLMS Meter | 5.4569 | 3.3684 | 1.89 | 3.5669 | 5.5648 | 12.042
4913 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902020105 | F07-FGREEN-GLEN-LAYOUT | DOMESTIC | DLMS Meter | 4.0482 | 3.7599 | 0.06 | 3.9882 | 5.7222 | 5.7222
4914 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902010106 | F08-IDLE 5 | URBAN MIXED LOAD | DLMS Meter | 4.4929 | 1.7888 | 2.6354 | 1.8574 | 3.6936 | 8.4127
4915 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902020303 | F11-SHOBHA-APPT | DOMESTIC | DLMS Meter | 1.4797 | 1.3956 | 0 | 1.4797 | 5.687 | 5.7885
4916 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902020304 | F12-SALARPURIA-SOFT-ZONE | URBAN MIXED LOAD | DLMS Meter | 4.926 | 4.3988 | 0.25 | 4.676 | 5.9281 | 5.9281
4917 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902020305 | F13-TAKSHASHILA-(AKME) | DOMESTIC | DLMS Meter | 3.3784 | 3.169 | 0 | 3.3784 | 6.1975 | 12.4025
4918 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902010102 | F17-OZONE-EVERGREEN | DOMESTIC | DLMS Meter | 6.1301 | 2.5346 | 3.478 | 2.6521 | 4.4328 | 9.1815
4919 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902010201 | F18-SENORITA | DOMESTIC | DLMS Meter | 5.2522 | 2.8916 | 2.175 | 3.0772 | 6.0319 | 6.8371
4920 | BMASZ | SOUTH | HSR | S11 | SOBHAAPPARTMENT_66 | 1110303902010202 | F19-EMBASSY PRESTINE APT | DOMESTIC | DLMS Meter | 1.4416 | 0.14564 | 1.292 | 0.14963 | 2.6671 | 3.0067
4921 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | SOKKE_66 | 1310105902010101 | F01-HOSKERE | AGRI | DLMS Meter | 0.843 | 0.72788 | 0 | 0.843 | 13.6562 | 13.6562
4922 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | SOKKE_66 | 1310105902010102 | F02-CHIKKAUJJINI | NJY | DLMS Meter | 1.0159 | 0.49542 | 0.45632 | 0.5596 | 11.4694 | 35.1098
4923 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | SOKKE_66 | 1310105902010103 | F03-GOURIPURA | AGRI | DLMS Meter | 1.1464 | 1.0036 | 0 | 1.1464 | 12.4577 | 12.4577
4924 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | SOKKE_66 | 1310105902010104 | F04-GADIMAKUNTE | AGRI | DLMS Meter | 0.64612 | 0.56785 | 0 | 0.64612 | 12.1135 | 12.1135
4925 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | SOKKE_66 | 1310105902010105 | F05-MAGADI | NJY | DLMS Meter | 0.98948 | 0.53154 | 0.3803 | 0.60918 | 12.7453 | 47.4082
4926 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | SOKKE_66 | 1310105902010106 | F06-MALIMACHIKERE | AGRI | DLMS Meter | 0.82596 | 0.72161 | 0 | 0.82596 | 12.6333 | 12.6333
4927 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | SOKKE_66 | 1310105902020301 | F08-GOWDAGONDANAHALLY | AGRI | DLMS Meter | 0.88 | 0.77016 | 0 | 0.88 | 12.4813 | 12.4812
4928 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | SOKKE_66 | 1310105902020302 | F09-KYASENAHALLY | AGRI | DLMS Meter | 0.7498 | 0.64969 | 0 | 0.7498 | 13.3516 | 13.3516
4929 | CTAZ | DAVANAGERE | DAVANAGERE | JAGALURU | SOKKE_66 | 1310105902020303 | F10-HIREBANNIHATTY | AGRI | DLMS Meter | 0.9288 | 0.80414 | 0 | 0.9288 | 13.4219 | 13.4219
4930 | BMANZ | NORTH | JALAHALLI | N9 | SOLADEVANAHALLY_66 | 1120102905020301 | F02-HESARAGHATTA | URBAN MIXED LOAD | DLMS Meter | 3.7026 | 3.2893 | 0.022965 | 3.6796 | 10.6072 | 52.8265
4931 | BMANZ | NORTH | JALAHALLI | N9 | SOLADEVANAHALLY_66 | 1120102905020302 | F03-SHIVAKOTE | URBAN MIXED LOAD | DLMS Meter | 2.5184 | 2.3208 | 0.036029 | 2.4824 | 6.5434 | 31.2082
4932 | BMANZ | NORTH | JALAHALLI | N9 | SOLADEVANAHALLY_66 | 1120102905010101 | F04-HESARAGHATTA EXPRESS | URBAN MIXED LOAD | DLMS Meter | 3.4989 | 2.8333 | 0.3816 | 3.1173 | 9.1111 | 31.3646
4933 | BMANZ | NORTH | JALAHALLI | N9 | SOLADEVANAHALLY_66 | 1120102905010102 | F05-CHIKKABANAVAR | URBAN MIXED LOAD | DLMS Meter | 2.1713 | 1.9981 | 0 | 2.1713 | 7.9747 | 7.9747
4934 | BMANZ | NORTH | JALAHALLI | N9 | SOLADEVANAHALLY_66 | 1120102905010103 | F06-BAGALAGUNTE | URBAN MIXED LOAD | DLMS Meter | 2.166 | 2.0185 | 0 | 2.166 | 6.808 | 6.808
4935 | BMANZ | NORTH | JALAHALLI | N9 | SOLADEVANAHALLY_66 | 1120102905020303 | F07-SILVEPURA | URBAN MIXED LOAD | DLMS Meter | 3.1612 | 2.7187 | 0.095 | 3.0662 | 11.4504 | 28.121
4936 | BMANZ | NORTH | JALAHALLI | N9 | SOLADEVANAHALLY_66 | 1120102905010104 | F08-SASUVEGHATTA | URBAN MIXED LOAD | DLMS Meter | 2.7599 | 1.7348 | 0.87167 | 1.8882 | 8.1255 | 36.2282
4937 | BMANZ | NORTH | JALAHALLI | N9 | SOLADEVANAHALLY_66 | 1120102905010105 | F09-BWSSB | URBAN MIXED LOAD | DLMS Meter | 4.5735 | 4.1286 | 0.24 | 4.3335 | 4.7274 | 6.0346
4938 | BMANZ | NORTH | JALAHALLI | N9 | SOLADEVANAHALLY_66 | 1120102905020305 | F11-SOLDEVANAHALLI EXPRESS | URBAN MIXED LOAD | DLMS Meter | 2.3543 | 2.0849 | 0.1166 | 2.2377 | 6.8279 | 6.8279
4939 | CTAZ | TUMKUR | TUMKUR | NITTUR | SOMALAPURA110/11KV | 1320107904010101 | F01-H NAGENAHALLY | AGRI | DLMS Meter | 1.2764 | 0.52815 | 0.685 | 0.59138 | 10.6926 | 10.6926
4940 | CTAZ | TUMKUR | TUMKUR | NITTUR | SOMALAPURA110/11KV | 1320107904010102 | F02-MN-KOTE | AGRI | DLMS Meter | 1.0757 | 0.20961 | 0.842 | 0.23374 | 10.3247 | 10.3247
4941 | CTAZ | TUMKUR | TUMKUR | NITTUR | SOMALAPURA110/11KV | 1320107904010105 | F03-GOLLAHALLY | AGRI | DLMS Meter | 0.968 | 0.69955 | 0.177 | 0.791 | 11.5608 | 11.5608
4942 | CTAZ | TUMKUR | TUMKUR | NITTUR | SOMALAPURA110/11KV | 1320107904010103 | F04-MATHIKERE | AGRI | DLMS Meter | 0.50238 | 0.015416 | 0.4849 | 0.01748 | 11.8078 | 12.8061
4943 | CTAZ | TUMKUR | TUMKUR | NITTUR | SOMALAPURA110/11KV | 1320107904010104 | F05-UDDEHOSAKERE | AGRI | DLMS Meter | 0.9927 | 0.70076 | 0.205 | 0.7877 | 11.0367 | 11.0367
4944 | CTAZ | TUMKUR | TUMKUR | NITTUR | SOMALAPURA110/11KV | 1320107904010106 | F06-SOMALAPURA | NJY | DLMS Meter | 0.3933 | 0.21206 | 0.153 | 0.2403 | 11.7524 | 56.385
4945 | CTAZ | TUMKUR | TUMKUR | NITTUR | SOMALAPURA110/11KV | 1320107904010107 | F07-BAGUR | NJY | DLMS Meter | 0.4352 | 0.38207 | 0 | 0.4352 | 12.2076 | 43.8574
4946 | CTAZ | TUMKUR | TUMKUR | NITTUR | SOMALAPURA110/11KV | 1320107904010108 | F08-SANKAPURA | NJY | DLMS Meter | 0.3009 | 0.27335 | 0 | 0.3009 | 9.1555 | 51.367
4947 | BMASZ | WEST | KENGERI | K3 | SOMANAHALLI_220 | 1140302901010101 | F01-HAROHALLI | DOMESTIC | DLMS Meter | 2.9988 | 2.7283 | 0.0075 | 2.9913 | 8.7937 | 17.4046
4948 | BMASZ | WEST | KENGERI | K3 | SOMANAHALLI_220 | 1140302901020302 | F03-VEDA-VIGNANA | URBAN MIXED LOAD | DLMS Meter | 3.3243 | 3.0328 | 0 | 3.3243 | 8.7673 | 14.5698
4949 | BMASZ | WEST | KENGERI | K3 | SOMANAHALLI_220 | 1140302901020303 | F04-HLTC | URBAN MIXED LOAD | DLMS Meter | 1.78 | 1.5539 | 0.072101 | 1.7079 | 9.0159 | 14.7283
4950 | BMASZ | WEST | KENGERI | K3 | SOMANAHALLI_220 | 1140302901020304 | F07-FAVA-SARALA | INDUSTRIAL | DLMS Meter | 0.099733 | 0.099732 | 0 | 0.099733 | 0 | 0.0010071
4951 | BMASZ | WEST | KENGERI | K3 | SOMANAHALLI_220 | 1140302901010103 | F08-SOMANAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.5621 | 2.3193 | 0 | 2.5621 | 9.476 | 14.9906
4952 | BMASZ | WEST | KENGERI | K3 | SOMANAHALLI_220 | 1140302901020305 | F09-BOLARE | URBAN MIXED LOAD | DLMS Meter | 2.0991 | 1.8717 | 0.0218 | 2.0773 | 9.8976 | 13.6802
4953 | BMASZ | WEST | KENGERI | K3 | SOMANAHALLI_220 | 1140302901010106 | F11-CONCORDE1 | DOMESTIC | DLMS Meter | 0.55226 | 0.51413 | 0.0035 | 0.54876 | 6.3119 | 9.3509
4954 | BMASZ | WEST | KENGERI | K3 | SOMANAHALLI_220 | 1140302901020306 | F12-CONCORDE2 | DOMESTIC | DLMS Meter | 0.14289 | 0.13385 | 0 | 0.14289 | 6.3246 | 9.6652
4955 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SOMAYAJANAHALLI_66 | 1230103904020101 | F01-SMHODALI | AGRI | DLMS Meter | 1.0457 | 0.47489 | 0.51804 | 0.52766 | 10.0008 | 10.0008
4956 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SOMAYAJANAHALLI_66 | 1230103904010101 | F02-MUDDEPALLI | AGRI | DLMS Meter | 0.6287 | 0.56574 | 0 | 0.6287 | 10.015 | 10.015
4957 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SOMAYAJANAHALLI_66 | 1230103904020102 | F03-SMADAVICHAMKUR | AGRI | DLMS Meter | 1.1082 | 0.99748 | 0 | 1.1082 | 9.9944 | 9.9944
4958 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SOMAYAJANAHALLI_66 | 1230103904020103 | F04-SMMURARJI-HOSTEL | COMMERCIAL | DLMS Meter | 0.0082 | 0.004285 | 0.00348 | 0.00472 | 9.2161 | 9.2161
4959 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SOMAYAJANAHALLI_66 | 1230103904020104 | F05-RAJAGUNDLAHALLI | NJY | DLMS Meter | 0.8566 | 0.77949 | 0 | 0.8566 | 9.0022 | 79.8193
4960 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SOMAYAJANAHALLI_66 | 1230103904010106 | F06-DIMBALA | AGRI | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4961 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SOMAYAJANAHALLI_66 | 1230103904010301 | F07-SMFGOLLAHALLI | AGRI | DLMS Meter | 0.66996 | 0.60292 | 0 | 0.66996 | 10.0072 | 10.0072
4962 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SOMAYAJANAHALLI_66 | 1230103904010302 | F08-SMSOMAYAJALAHALLI | AGRI | DLMS Meter | 1.3252 | 1.1927 | 0 | 1.3252 | 9.999 | 10.3189
4963 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SOMAYAJANAHALLI_66 | 1230103904010105 | F09-GOPALAPURA NJY | NJY | DLMS Meter | 0.95588 | 0.86981 | 0 | 0.95588 | 9.0042 | 65.6824
4964 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SOMAYAJANAHALLI_66 | 1230103904010104 | F10-DEVALAPALLI | AGRI | DLMS Meter | 1.4739 | 0.46622 | 0.95588 | 0.51804 | 10.0023 | 10.0023
4965 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | SOMENAHALLI_66 | 1230304905010205 | F01-BATHLAHALLI NJY | NJY | DLMS Meter | 1.0224 | 0.86773 | 0.035143 | 0.98728 | 12.1085 | 26.107
4966 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | SOMENAHALLI_66 | 1230304905010203 | F03-KAMBALAHALLI | AGRI | DLMS Meter | 1.2028 | 1.0826 | 0 | 1.2028 | 9.9962 | 9.9962
4967 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | SOMENAHALLI_66 | 1230304905010204 | F04-CHIKKANENCHERLU NJY | NJY | DLMS Meter | 1.2411 | 1.1101 | 0.013 | 1.2281 | 9.6095 | 58.3861
4968 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | SOMENAHALLI_66 | 1230304905010206 | F06-THUMAKUNTE | AGRI | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
4969 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | SOMENAHALLI_66 | 1230304905010207 | F07-GBD INDUSTRIAL | INDUSTRIAL | DLMS Meter | 1.215 | 1.0809 | 0.027 | 1.188 | 9.0158 | 16.0729
4970 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902010101 | F02-DBPALLI | AGRI | DLMS Meter | 1.3926 | 1.2533 | 0 | 1.3926 | 10.0001 | 10.0001
4971 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902010102 | F03-OLD-CHELUR | AGRI | DLMS Meter | 0.51602 | 0.46444 | 0 | 0.51602 | 9.9948 | 9.9948
4972 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902010103 | F04-THIMMASANDRA-NEW | AGRI | DLMS Meter | 1.0047 | 0.90427 | 0 | 1.0047 | 9.9997 | 9.9997
4973 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902010107 | F05-BYREPALLI | AGRI | DLMS Meter | 0.46976 | 0.39465 | 0.031 | 0.43876 | 10.0531 | 10.0531
4974 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902020301 | F06-CHELUR-EXPRESS | AGRI | DLMS Meter | 1.2173 | 1.0956 | 0 | 1.2173 | 10.0022 | 10.0022
4975 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902020302 | F07-THIMMASANDRA-OLD | AGRI | DLMS Meter | 0.78538 | 0.70669 | 0 | 0.78538 | 10.0187 | 10.0187
4976 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902020303 | F08-OLD-BILLUR | AGRI | DLMS Meter | 1.1879 | 0.80814 | 0.29 | 0.89792 | 9.9982 | 9.9982
4977 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902020304 | F09-NEW-BILLUR | AGRI | DLMS Meter | 1.3938 | 1.2547 | 0 | 1.3938 | 9.9812 | 9.9812
4978 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902010104 | F10-PEDDUR | NJY | DLMS Meter | 0.8863 | 0.7739 | 0 | 0.8863 | 12.6816 | 75.6408
4979 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902010105 | F11-NAGARLU | NJY | DLMS Meter | 0.6094 | 0.54227 | 0 | 0.6094 | 11.0164 | 79.4588
4980 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | SOMNATHPURA_66 | 1230305902010106 | F12-PALYAKERE | NJY | DLMS Meter | 1.0523 | 0.90522 | 0.01 | 1.0423 | 13.1533 | 85.662
4981 | BMASZ | SOUTH | HSR | S10 | SOUDELA_HIRANANDANI_66 | 1110302902020102 | F01-VISHWA PRIYA LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.7247 | 2.799 | 0.81691 | 2.9078 | 3.7434 | 11.3912
4982 | BMASZ | SOUTH | HSR | S10 | SOUDELA_HIRANANDANI_66 | 1110302902020103 | F02-BEGUR KOPPA ROAD | URBAN MIXED LOAD | DLMS Meter | 3.5778 | 3.1805 | 0.28074 | 3.2971 | 3.5349 | 8.8239
4983 | BMASZ | SOUTH | HSR | S19 | SOUDELA_HIRANANDANI_66 | 1110302902020104 | F05-DEVARACHIKKANAHALLI | URBAN MIXED LOAD | DLMS Meter | 4.416 | 3.5779 | 0.5426 | 3.8734 | 7.6292 | 7.6292
4984 | BMASZ | SOUTH | HSR | S10 | SOUDELA_HIRANANDANI_66 | 1110302902020101 | F06-AKSHAY NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.8865 | 3.7642 | 0 | 3.8865 | 3.1473 | 9.9297
4985 | BMASZ | SOUTH | HSR | S10 | SOUDELA_HIRANANDANI_66 | 1110302902010106 | F07-PRESTIGE SONG OF SOUTH | DOMESTIC | DLMS Meter | 2.349 | 1.4511 | 0.8265 | 1.5225 | 4.6908 | 6.5186
4986 | BMASZ | SOUTH | HSR | S19 | SOUDELA_HIRANANDANI_66 | 1110302902010105 | F08-TEJASWINI NAGAR | URBAN MIXED LOAD | DLMS Meter | 6.3546 | 3.9471 | 2.1708 | 4.1838 | 5.6578 | 7.1832
4987 | BMASZ | SOUTH | HSR | S10 | SOUDELA_HIRANANDANI_66 | 1110302902010101 | F09-LAKE WERNDOW | DOMESTIC | DLMS Meter | 2.1102 | 1.8402 | 0.22025 | 1.8899 | 2.6311 | 4.9245
4988 | BMASZ | SOUTH | HSR | S10 | SOUDELA_HIRANANDANI_66 | 1110302902010102 | F10-HILL CRESTA | DOMESTIC | DLMS Meter | 0.39103 | 0.371 | 0.00908 | 0.38195 | 2.8677 | 3.0677
4989 | BMASZ | SOUTH | HSR | S10 | SOUDELA_HIRANANDANI_66 | 1110302902010103 | F11-CLUB MEADOWS | DOMESTIC | DLMS Meter | 0.22001 | 0.20694 | 0.0035 | 0.21651 | 4.4242 | 6.7041
4990 | BMASZ | SOUTH | HSR | S12 | SOUTHCITY_66 | 1110304903010105 | F02-B1B8 | DOMESTIC | DLMS Meter | 2.5584 | 2.2993 | 0 | 2.5584 | 10.1264 | 13.235
4991 | BMASZ | SOUTH | HSR | S12 | SOUTHCITY_66 | 1110304903010101 | F03-BG-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.2534 | 2.929 | 0 | 3.2534 | 9.9688 | 13.2152
4992 | BMASZ | SOUTH | HSR | S12 | SOUTHCITY_66 | 1110304903010102 | F04-LAKSHMI-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 5.6606 | 5.0487 | 0 | 5.6606 | 10.8095 | 10.8095
4993 | BMASZ | SOUTH | HSR | S12 | SOUTHCITY_66 | 1110304903010103 | F05-SOUTH-CITY-A-TO-A-&-C-TO-C-BLOCKS | DOMESTIC | DLMS Meter | 1.7461 | 1.5686 | 0 | 1.7461 | 10.1667 | 10.1667
4994 | BMASZ | SOUTH | HSR | S10 | SOUTHCITY_66 | 1110304903010301 | F06-FKAMMANAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.7728 | 3.3171 | 0.27952 | 3.4933 | 5.0432 | 14.1719
4995 | BMASZ | SOUTH | HSR | S19 | SOUTHCITY_66 | 1110304903020301 | F07-FSHANTHI-NIKETAN | URBAN MIXED LOAD | DLMS Meter | 3.4883 | 2.9893 | 0.137 | 3.3513 | 10.8018 | 11.5124
4996 | BMASZ | SOUTH | HSR | S19 | SOUTHCITY_66 | 1110304903020101 | F08-DODDAMMA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.9883 | 2.7423 | 0.987 | 3.0013 | 8.6293 | 8.6293
4997 | BMASZ | SOUTH | HSR | S12 | SOUTHCITY_66 | 1110304903020102 | F09-B-K-CIRCLE | URBAN MIXED LOAD | DLMS Meter | 4.816 | 4.3741 | 0 | 4.816 | 9.1764 | 15.0624
4998 | BMASZ | SOUTH | JAYANAGAR | S14 | SOUTHCITY_66 | 1110304903010302 | F10-PANDURANGA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.352 | 1.4849 | 1.8099 | 1.5421 | 3.7134 | 6.2186
4999 | BMASZ | SOUTH | HSR | S12 | SOUTHCITY_66 | 1110304903020302 | F11-BWSSB | URBAN MIXED LOAD | DLMS Meter | 3.4197 | 3.0775 | 0 | 3.4197 | 10.0079 | 10.0079
5000 | BMASZ | SOUTH | JAYANAGAR | S14 | SOUTHCITY_66 | 1110304903010303 | F12-MOTAPPA-COMPOUND | URBAN MIXED LOAD | DLMS Meter | 2.5216 | 2.3561 | 0 | 2.5216 | 6.5649 | 8.7005
5001 | BMASZ | SOUTH | HSR | S19 | SOUTHCITY_66 | 1110304903010107 | F13-MAHINDRA HOMES | DOMESTIC | DLMS Meter | 1.7236 | 1.1704 | 0.441 | 1.2826 | 8.7481 | 8.7481
5002 | BMASZ | SOUTH | JAYANAGAR | S14 | SOUTHCITY_66 | 1110304903020304 | F14-GOOD HOMES | DOMESTIC | DLMS Meter | 0.4787 | 0.31858 | 0.145 | 0.3337 | 4.5312 | 5.157
5003 | BRAZ | RAMANAGAR | MAGADI | KUDUR | SRIGIRIPURA_66 | 1210103905010103 | F01-MARASANDRA | AGRI | DLMS Meter | 0.9658 | 0.82979 | 0.015 | 0.9508 | 12.7276 | 12.7276
5004 | BRAZ | RAMANAGAR | MAGADI | KUDUR | SRIGIRIPURA_66 | 1210103905010101 | F02-VEERASAGARA | NJY | DLMS Meter | 0.4267 | 0.35824 | 0.031 | 0.3957 | 9.4678 | 27.1728
5005 | BRAZ | RAMANAGAR | MAGADI | KUDUR | SRIGIRIPURA_66 | 1210103905010102 | F03-HOSAHALLI | AGRI | DLMS Meter | 0.6954 | 0.5679 | 0.05 | 0.6454 | 12.0085 | 12.0085
5006 | BRAZ | RAMANAGAR | MAGADI | KUDUR | SRIGIRIPURA_66 | 1210103905010104 | F04-BETTAHALLI | AGRI | DLMS Meter | 0.6206 | 0.54023 | 0.01 | 0.6106 | 11.5247 | 11.5247
5007 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020101 | F01-ARIKUNTE | AGRI | DLMS Meter | 55.1249 | 0.72573 | 54.3184 | 0.80648 | 10.0126 | 10.0126
5008 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020102 | F02-ALAVATA | AGRI | DLMS Meter | 1.1297 | 0.72867 | 0.32 | 0.80968 | 10.0047 | 10.0047
5009 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020103 | F03-NARAMAKALAHALLI | AGRI | DLMS Meter | 1.1592 | 1.0434 | 0 | 1.1592 | 9.9871 | 9.9871
5010 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020104 | F04-HOGALKERE | AGRI | DLMS Meter | 1.4694 | 1.3227 | 0 | 1.4694 | 9.9858 | 9.9858
5011 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020105 | F05-SRINIVASAPURA-LOCAL | URBAN MIXED LOAD | DLMS Meter | 4.0188 | 3.6513 | 0 | 4.0188 | 9.144 | 33.6169
5012 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020308 | F06-PALYA | AGRI | DLMS Meter | 22.7928 | 0.86067 | 21.8368 | 0.956 | 9.972 | 9.972
5013 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020302 | F07-YALAVAKUNTE | AGRI | DLMS Meter | 1.4464 | 1.3018 | 0 | 1.4464 | 9.9947 | 9.9947
5014 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020303 | F08-KOTAPALLI | AGRI | DLMS Meter | 0.6764 | 0.60872 | 0 | 0.6764 | 10.0052 | 10.0052
5015 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020304 | F09-THADIGOL | AGRI | DLMS Meter | 0.4352 | 0.39174 | 0 | 0.4352 | 9.9871 | 10.8616
5016 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020305 | F10-WATER-WORKS | RURAL MIXED LOAD | DLMS Meter | 1.7401 | 1.5707 | 0 | 1.7401 | 9.7323 | 37.5788
5017 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902010102 | F12-NAMBIHALLI | NJY | DLMS Meter | 2.8605 | 2.3889 | 0.228 | 2.6325 | 9.254 | 80.6718
5018 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020306 | F13-KIRUVAR | NJY | DLMS Meter | 0.7333 | 0.66865 | 0 | 0.7333 | 8.8157 | 86.6385
5019 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902020307 | F14-YACHANAHALLI NJY | NJY | DLMS Meter | 1.0561 | 0.96046 | 0 | 1.0561 | 9.0579 | 55.3327
5020 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902010301 | F15-RONUR NJY | NJY | DLMS Meter | 0.81054 | 0.74158 | 0 | 0.81054 | 8.5082 | 79.8807
5021 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | SRINIVASAPURA_66 | 1230103902010103 | F16-APMC | NJY | DLMS Meter | 0.52928 | 0.3877 | 0.1 | 0.42928 | 9.6851 | 10.1364
5022 | BMANZ | NORTH | PEENYA | N7 | SRS_PEENYA_220 | 1120102901010101 | F01-YESHAWANTAPURA-INDUSTRIAL | URBAN MIXED LOAD | DLMS Meter | 5.0568 | 4.6742 | 0 | 5.0568 | 7.5661 | 9.6417
5023 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901010102 | F02-PEENYA-ST-STAGE | URBAN MIXED LOAD | DLMS Meter | 3.5741 | 3.3474 | 0.07 | 3.5041 | 4.4724 | 5.9413
5024 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901030502 | F03-J.K-GARMENTS | URBAN MIXED LOAD | DLMS Meter | 1.7042 | 1.5641 | 0.09 | 1.6142 | 3.1046 | 6.6519
5025 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901040701 | F04-GRUHALAKSHMI-APARTMENT | URBAN MIXED LOAD | DLMS Meter | 6.0411 | 3.4697 | 2.447 | 3.5941 | 3.4615 | 8.0467
5026 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901020301 | F05-JINDAL | URBAN MIXED LOAD | DLMS Meter | 4.8017 | 4.611 | 0.0085 | 4.7932 | 3.8011 | 3.8011
5027 | BMANZ | NORTH | PEENYA | N7 | SRS_PEENYA_220 | 1120102901020302 | F06-FYESHWANTAPUR-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 1.1805 | 1.0778 | 0 | 1.1805 | 8.6957 | 17.8523
5028 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901030503 | F07-WELCAST-STEEL | INDUSTRIAL | DLMS Meter | 2.4745 | 2.4348 | 0 | 2.4745 | 1.6062 | 1.6062
5029 | BMANZ | NORTH | PEENYA | N4 | SRS_PEENYA_220 | 1120102901020303 | F08-PART-LOAD-OF-PEENYA | URBAN MIXED LOAD | DLMS Meter | 3.2452 | 2.8802 | 0.31474 | 2.9304 | 1.7141 | 8.3808
5030 | BMANZ | NORTH | PEENYA | N4 | SRS_PEENYA_220 | 1120102901030504 | F09-3RD-STAGE.-PEENYA&LAGGERE | INDUSTRIAL | DLMS Meter | 3.6764 | 3.4808 | 0.022 | 3.6544 | 4.749 | 14.3774
5031 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901020304 | F10-TVS-CROSS | INDUSTRIAL | DLMS Meter | 3.056 | 3.0425 | 0 | 3.056 | 0.44065 | 0.44065
5032 | BMANZ | NORTH | PEENYA | N4 | SRS_PEENYA_220 | 1120102901040702 | F11-PEENYA-RD-STAGE | INDUSTRIAL | DLMS Meter | 5.5029 | 5.0999 | 0.20064 | 5.3023 | 3.8165 | 5.3737
5033 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901010103 | F12-ISRO | DEFENSE ESTABLISHMENT | DLMS Meter | 1.2402 | 1.0703 | 0.1657 | 1.0745 | 0.39023 | 0.39023
5034 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901030101 | F13-J.P-EXPORTS | URBAN MIXED LOAD | DLMS Meter | 2.488 | 2.4217 | 0 | 2.488 | 2.6628 | 10.618
5035 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901030301 | F14-PEENYA-4TH-CROSS | INDUSTRIAL | DLMS Meter | 4.146 | 3.9908 | 0.087 | 4.059 | 1.6811 | 1.6811
5036 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901030102 | F15-WELCAST-STEEL | INDUSTRIAL | DLMS Meter | 4.0942 | 4.0436 | 0 | 4.0942 | 1.2345 | 2.9671
5037 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901040703 | F16-DYNAMATIC | URBAN MIXED LOAD | DLMS Meter | 5.3249 | 5.1515 | 0 | 5.3249 | 3.2562 | 5.8058
5038 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901030505 | F17-RELIANCE | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5039 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901040704 | F18-ISRO | DEFENSE ESTABLISHMENT | DLMS Meter | 0.75825 | 0.75363 | 0 | 0.75825 | 0.60972 | 0.60972
5040 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901040705 | F19-NARAYANAPURA | URBAN MIXED LOAD | DLMS Meter | 3.6868 | 3.573 | 0 | 3.6868 | 3.0869 | 3.0869
5041 | BMANZ | NORTH | PEENYA | N4 | SRS_PEENYA_220 | 1120102901040706 | F20-RAJGOPAL-NAGAR | URBAN MIXED LOAD | DLMS Meter | 6.3943 | 5.6952 | 0.50022 | 5.8941 | 3.3751 | 6.7524
5042 | BMANZ | NORTH | PEENYA | N4 | SRS_PEENYA_220 | 1120102901040707 | F21-VIDHANASOUDHA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 5.4013 | 5.0657 | 0.02616 | 5.3751 | 5.7555 | 12.6232
5043 | BMANZ | NORTH | PEENYA | N7 | SRS_PEENYA_220 | 1120102901030501 | F22-ESIC-HOSPITAL | HOSPITAL | DLMS Meter | 0.55386 | 0.53017 | 0 | 0.55386 | 4.2756 | 7.1886
5044 | BMANZ | NORTH | PEENYA | N4 | SRS_PEENYA_220 | 1120102901010104 | F23-LAGGERE | URBAN MIXED LOAD | DLMS Meter | 4.2244 | 4.0688 | 0 | 4.2244 | 3.6827 | 6.3587
5045 | BMANZ | NORTH | PEENYA | N4 | SRS_PEENYA_220 | 1120102901030506 | F24-HITCO | INDUSTRIAL | DLMS Meter | 4.2554 | 4.1687 | 0.052 | 4.2034 | 0.82528 | 1.7696
5046 | BMANZ | NORTH | PEENYA | N4 | SRS_PEENYA_220 | 1120102901020305 | F25-GENERAL-METALS | INDUSTRIAL | DLMS Meter | 4.1063 | 3.6603 | 0.33549 | 3.7708 | 2.93 | 4.1663
5047 | BMANZ | NORTH | PEENYA | N5 | SRS_PEENYA_220 | 1120102901030103 | F26-VAISHNAVI MALL | URBAN MIXED LOAD | DLMS Meter | 0.9699 | 0.93928 | 0 | 0.9699 | 3.1567 | 3.1567
5048 | BMANZ | NORTH | PEENYA | N4 | SRS_PEENYA_220 | 1120102901030507 | F27-HEGGANAHALLI | INDUSTRIAL | DLMS Meter | 4.1238 | 3.8404 | 0 | 4.1238 | 6.8722 | 11.7005
5049 | BMANZ | NORTH | PEENYA | N4 | SRS_PEENYA_220 | 1120102901010108 | F30-KEMPEGOWDA NAGARA | URBAN MIXED LOAD | DLMS Meter | 3.7947 | 3.5496 | 0.026614 | 3.7681 | 5.8007 | 11.0678
5050 | BMANZ | NORTH | PEENYA | N7 | SRS_PEENYA_220 | 1120102901040708 | F31-GORGUNTE_PALYA | URBAN MIXED LOAD | DLMS Meter | 3.2503 | 3.0576 | 0 | 3.2503 | 5.9301 | 27.3515
5051 | BMASZ | SOUTH | KORAMANGALA | S16 | STJOHNSWOOD_66 | 1110202902020102 | F02-MEJESTIC-APPARTMENTS | URBAN MIXED LOAD | DLMS Meter | 3.9332 | 3.6019 | 0 | 3.9332 | 8.422 | 15.1217
5052 | BMASZ | SOUTH | KORAMANGALA | S16 | STJOHNSWOOD_66 | 1110202902020105 | F06-CASHLER-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 2.6379 | 2.4085 | 0 | 2.6379 | 8.6976 | 17.5403
5053 | BMASZ | SOUTH | KORAMANGALA | S16 | STJOHNSWOOD_66 | 1110202902020301 | F07-ST-JOHNS-HOSTLE-RMU | URBAN MIXED LOAD | DLMS Meter | 2.4486 | 1.9591 | 0.35 | 2.0986 | 6.644 | 28.486
5054 | BMASZ | SOUTH | KORAMANGALA | S16 | STJOHNSWOOD_66 | 1110202902020302 | F08-TAVAREKERE | URBAN MIXED LOAD | DLMS Meter | 4.376 | 3.9716 | 0.012 | 4.364 | 8.9916 | 16.5513
5055 | BMASZ | SOUTH | KORAMANGALA | S16 | STJOHNSWOOD_66 | 1110202902020303 | F09-ACCENTURE | URBAN MIXED LOAD | DLMS Meter | 4.3904 | 4.4091 | 0 | 4.3904 | -0.42565 | -0.42565
5056 | BMASZ | SOUTH | KORAMANGALA | S16 | STJOHNSWOOD_66 | 1110202902020304 | F10-ST-JOHNS-WOOD-APPARTMENTS | URBAN MIXED LOAD | DLMS Meter | 1.0758 | 0.88096 | 0.1425 | 0.93328 | 5.6061 | 8.2503
5057 | BMASZ | SOUTH | KORAMANGALA | S16 | STJOHNSWOOD_66 | 1110202902020305 | F11-ORACLE | URBAN MIXED LOAD | DLMS Meter | 1.485 | 1.3742 | 0.015 | 1.47 | 6.5146 | 7.467
5058 | BMASZ | SOUTH | KORAMANGALA | S16 | STJOHNSWOOD_66 | 1110202902020306 | F12-KENDRIYA-SADANA | URBAN MIXED LOAD | DLMS Meter | 4.1297 | 3.8473 | 0 | 4.1297 | 6.84 | 12.0292
5059 | BMASZ | SOUTH | JAYANAGAR | S18 | SUBRAMANYAPURA_66 | 1110103901010101 | F01-RURAL | URBAN MIXED LOAD | DLMS Meter | 2.1101 | 1.9853 | 0 | 2.1101 | 5.9127 | 10.5288
5060 | BMASZ | SOUTH | JAYANAGAR | S18 | SUBRAMANYAPURA_66 | 1110103901020101 | F02-KRISHANA MILL | INDUSTRIAL | DLMS Meter | 4.0566 | 4.0393 | 0 | 4.0566 | 0.4262 | 1.9799
5061 | BMASZ | SOUTH | JAYANAGAR | S5 | SUBRAMANYAPURA_66 | 1110103901010102 | F04-METRO | URBAN MIXED LOAD | DLMS Meter | 1.5258 | 1.4485 | 0 | 1.5258 | 5.0657 | 5.0657
5062 | BMASZ | SOUTH | JAYANAGAR | S18 | SUBRAMANYAPURA_66 | 1110103901010103 | F05-BHARATH LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0.87937 | 0.82085 | 0 | 0.87937 | 6.6541 | 17.9356
5063 | BMASZ | SOUTH | JAYANAGAR | S5 | SUBRAMANYAPURA_66 | 1110103901010104 | F06-REMCO | URBAN MIXED LOAD | DLMS Meter | 2.9911 | 2.8169 | 0 | 2.9911 | 5.8258 | 15.1205
5064 | BMASZ | SOUTH | JAYANAGAR | S5 | SUBRAMANYAPURA_66 | 1110103901020301 | F09-JAYANAGAR | URBAN MIXED LOAD | DLMS Meter | 2.7707 | 2.6055 | 0 | 2.7707 | 5.9623 | 13.5085
5065 | BMASZ | SOUTH | JAYANAGAR | S18 | SUBRAMANYAPURA_66 | 1110103901010107 | F10-GUBBALALA | URBAN MIXED LOAD | DLMS Meter | 2.8778 | 2.7389 | 0 | 2.8778 | 4.8266 | 12.1837
5066 | BMASZ | SOUTH | JAYANAGAR | S18 | SUBRAMANYAPURA_66 | 1110103901010108 | F11-UTTHRAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.9771 | 3.6178 | 0.05 | 3.9271 | 7.8766 | 13.0455
5067 | BMASZ | SOUTH | JAYANAGAR | S5 | SUBRAMANYAPURA_66 | 1110103901020302 | F12-BALAJI-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 0.71649 | 0.67093 | 0 | 0.71649 | 6.3581 | 14.5591
5068 | BMASZ | SOUTH | JAYANAGAR | S5 | SUBRAMANYAPURA_66 | 1110103901020303 | F13-ADARSHA-1 | URBAN MIXED LOAD | DLMS Meter | 0.74548 | 0.52799 | 0.1826 | 0.56288 | 6.1979 | 6.1979
5069 | BMASZ | SOUTH | JAYANAGAR | S5 | SUBRAMANYAPURA_66 | 1110103901020304 | F14-ADARASH-II | URBAN MIXED LOAD | DLMS Meter | 1.8501 | 1.5268 | 0.229 | 1.6211 | 5.8158 | 15.8108
5070 | BMASZ | SOUTH | JAYANAGAR | S18 | SUBRAMANYAPURA_66 | 1110103901020305 | F15-MANTRI | DOMESTIC | DLMS Meter | 2.9165 | 2.7204 | 0.01 | 2.9065 | 6.4037 | 11.5221
5071 | BMASZ | SOUTH | JAYANAGAR | S5 | SUBRAMANYAPURA_66 | 1110103901020306 | F16-MANTRI-2 | DOMESTIC | DLMS Meter | 1.0274 | 0.95519 | 0 | 1.0274 | 7.028 | 14.742
5072 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SUGATUR_66 | 1230102901020101 | F02-KOLAGONJANAHALLY | AGRI | DLMS Meter | 0.632 | 0.57207 | 0 | 0.632 | 9.4828 | 10.0435
5073 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SUGATUR_66 | 1230102901010101 | F03-SUGATUR | AGRI | DLMS Meter | 0.4282 | 0.38308 | 0 | 0.4282 | 10.5369 | 15.2935
5074 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SUGATUR_66 | 1230102901010102 | F04-UPPAKUNTE | AGRI | DLMS Meter | 1.3904 | 1.2268 | 0 | 1.3904 | 11.7683 | 11.7683
5075 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SUGATUR_66 | 1230102901020301 | F06-JANAGHATTA | AGRI | DLMS Meter | 1.0478 | 0.93494 | 0 | 1.0478 | 10.7714 | 10.7714
5076 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SUGATUR_66 | 1230102901010103 | F07-GOWDAHALLI | AGRI | DLMS Meter | 0.4846 | 0.43829 | 0 | 0.4846 | 9.5559 | 12.4935
5077 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SUGATUR_66 | 1230102901010104 | F08-SUGUTUR-EXPRESS | INDUSTRIAL | DLMS Meter | 0.10444 | 0.10458 | 0 | 0.10444 | -0.12926 | -0.12926
5078 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | SUGATUR_66 | 1230102901020302 | F09-NJYKALLUR | NJY | DLMS Meter | 1.1386 | 1.0206 | 0 | 1.1386 | 10.3674 | 66.6674
5079 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | SULIBELE_66 | 1210203901010101 | F01-KAMMASANDRA | AGRI | DLMS Meter | 1.0329 | 0.92985 | 0 | 1.0329 | 9.9781 | 9.9781
5080 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | SULIBELE_66 | 1210203901010102 | F02-SULIBELE | URBAN MIXED LOAD | DLMS Meter | 3.0276 | 2.5183 | 0.42865 | 2.599 | 3.1054 | 45.7797
5081 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | SULIBELE_66 | 1210203901010103 | F03-ANKONAHALLI | AGRI | DLMS Meter | 1.8441 | 1.6598 | 0 | 1.8441 | 9.9913 | 9.9913
5082 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | SULIBELE_66 | 1210203901020301 | F04-ATTIBELE | NJY | DLMS Meter | 1.3504 | 1.1652 | 0 | 1.3504 | 13.7155 | 65.1048
5083 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | SULIBELE_66 | 1210203901020302 | F05-BENDIGANAHALLI | AGRI | DLMS Meter | 1.2847 | 1.1563 | 0 | 1.2847 | 9.9918 | 9.9918
5084 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | SULIBELE_66 | 1210203901020303 | F06-DODDARALAGERE | AGRI | DLMS Meter | 1.1095 | 0.99883 | 0 | 1.1095 | 9.9765 | 9.9765
5085 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | SULIBELE_66 | 1210203901020304 | F07-BETTAHALLI | AGRI | DLMS Meter | 0.94856 | 0.85385 | 0 | 0.94856 | 9.9849 | 9.9907
5086 | BRAZ | BANGALORE RURAL | HOSAKOTE | NANDAGUDI | SULIBELE_66 | 1210203901010105 | F08-BHAVAPURA | NJY | DLMS Meter | 1.6842 | 1.4927 | 0 | 1.6842 | 11.3663 | 61.6767
5087 | BMASZ | SOUTH | KORAMANGALA | S7 | SUPREME BUILD CAP | #N/A | F08 | #N/A | DLMS Meter | 1.2828 | 1.1027 | 0.10962 | 1.1732 | 6.0049 | 13.0024
5088 | BMASZ | SOUTH | KORAMANGALA | S7 | SUPREMEBUILDCAP_66 | 1110203909010201 | F02-DEVARABISANAHALLI NEW | DOMESTIC | DLMS Meter | 1.5633 | 1.3384 | 0.17 | 1.3933 | 3.941 | 10.3734
5089 | BMASZ | SOUTH | KORAMANGALA | S7 | SUPREMEBUILDCAP_66 | 1110203909010202 | F03-ADARSH | COMMERCIAL | DLMS Meter | 2.5637 | 2.5778 | 0 | 2.5637 | -0.5492 | -0.5492
5090 | BMASZ | SOUTH | KORAMANGALA | S7 | SUPREMEBUILDCAP_66 | 1110203909020101 | F06-SAI SHRUTHI | DOMESTIC | DLMS Meter | 0.53621 | 0.53609 | 0 | 0.53621 | 0.023531 | 2.398
5091 | BMASZ | SOUTH | HSR | S11 | SUPREMEBUILDCAP_66 | 1110203909010203 | F07-STERLING ASCENTIA | DOMESTIC | DLMS Meter | 1.8504 | 0.15417 | 1.692 | 0.1584 | 2.6715 | 4.8925
5092 | BMASZ | SOUTH | KORAMANGALA | S7 | SUPREMEBUILDCAP_66 | 1110203909020102 | F09-SAMVI JV HOTEL | COMMERCIAL | DLMS Meter | 0.90647 | 0.91387 | 0 | 0.90647 | -0.81671 | -0.81671
5093 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | SURYANAGAR_66 | 1220203903010106 | F01-SURYA 2ND PHASE RAJAPURA | DOMESTIC | DLMS Meter | 0.2512 | 0.21333 | 0.024 | 0.2272 | 6.1065 | 13.5657
5094 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | SURYANAGAR_66 | 1220203903010101 | F02-NAGANAYAKANHALLI | URBAN MIXED LOAD | DLMS Meter | 0.7392 | 0.56913 | 0.122 | 0.6172 | 7.7882 | 8.4106
5095 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | SURYANAGAR_66 | 1220203903010107 | F03-JR GREEN PARK | DOMESTIC | DLMS Meter | 5.0244 | 3.7455 | 0.94 | 4.0844 | 8.2963 | 9.9245
5096 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | SURYANAGAR_66 | 1220203903010104 | F04-DIVISION-OFFICE-ROAD | URBAN MIXED LOAD | DLMS Meter | 1.1924 | 0.9114 | 0.229 | 0.9634 | 5.3977 | 8.8071
5097 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | SURYANAGAR_66 | 1220203903010103 | F05-SURYA-NAGAR | DOMESTIC | DLMS Meter | 0.8698 | 0.70349 | 0.112 | 0.7578 | 7.1673 | 11.1569
5098 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | SURYANAGAR_66 | 1220203903010108 | F07-NAGANAYAKANAHALLI | AGRI | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5099 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904010101 | F02-INDUS-FILA | RURAL MIXED LOAD | DLMS Meter | 2.2792 | 0.69498 | 1.5032 | 0.776 | 10.4412 | 10.4412
5100 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904010102 | F03-PEPSI | INDUSTRIAL | DLMS Meter | 4.376 | 4.3594 | 0 | 4.376 | 0.37843 | 0.37843
5101 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904010104 | F04-KEMWELL | RURAL MIXED LOAD | DLMS Meter | 7.7319 | 7.2683 | 0 | 7.7319 | 5.9966 | 7.3085
5102 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904010103 | F05-ACE-DESINGER | INDUSTRIAL | DLMS Meter | 2.6851 | 2.6097 | 0 | 2.6851 | 2.8073 | 2.8073
5103 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904020301 | F06-KIRLOSKAR | RURAL MIXED LOAD | DLMS Meter | 3.3015 | 2.9007 | 0.09 | 3.2115 | 9.6793 | 10.2764
5104 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904020302 | F07-HASURUVALLI-AGRI | AGRI | DLMS Meter | 1.6415 | 1.4771 | 0 | 1.6415 | 10.0168 | 10.0168
5105 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904020303 | F08-FILAMENT | RURAL MIXED LOAD | DLMS Meter | 2.8576 | 1.6022 | 1.05 | 1.8076 | 11.3658 | 12.2832
5106 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904020304 | F09-BARDI | AGRI | DLMS Meter | 1.1988 | 0.50826 | 0.635 | 0.56384 | 9.8569 | 9.8569
5107 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904020305 | F10-GEDDALAHALLI | AGRI | DLMS Meter | 0.47684 | 0.4293 | 0 | 0.47684 | 9.9692 | 9.9692
5108 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904010301 | F11-WINTRAC | INDUSTRIAL | DLMS Meter | 1.8117 | 1.81 | 0 | 1.8117 | 0.096317 | 0.096317
5109 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904020306 | F12-HASIRUVALLI-NJY | NJY | DLMS Meter | 1.2096 | 0.78355 | 0.3462 | 0.86342 | 9.2506 | 12.4248
5110 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904020307 | F13-RHCS | RURAL MIXED LOAD | DLMS Meter | 1.7986 | 1.684 | 0 | 1.7986 | 6.3711 | 7.0985
5111 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | T_BEGUR_66 | 1210104904010106 | F14-UNIVERSAL AIR | INDUSTRIAL | DLMS Meter | 4.8146 | 4.7783 | 0 | 4.8146 | 0.75344 | 0.75344
5112 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | TADIGOL_CROSS _66 | 1230103907010101 | F02-KAMATHAMAPALLI | AGRI | DLMS Meter | 0.5594 | 0.5035 | 0 | 0.5594 | 9.9928 | 9.9928
5113 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | TADIGOL_CROSS _66 | 1230103907010102 | F03-SHEEGALAPALYA | AGRI | DLMS Meter | 0.8578 | 0.22378 | 0.6092 | 0.2486 | 9.9831 | 9.9831
5114 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | TADIGOL_CROSS _66 | 1230103907010103 | F04-REDDIMPALLI NJY | NJY | DLMS Meter | 0.3104 | 0.28275 | 0 | 0.3104 | 8.9069 | 81.8356
5115 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | TADIGOL_CROSS _66 | 1230103907010104 | F05-K KURAPALLI | AGRI | DLMS Meter | 0.9976 | 0.89797 | 0 | 0.9976 | 9.9871 | 9.9871
5116 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | TADIGOL_CROSS _66 | 1230103907020105 | F07-KUSANDRA | AGRI | DLMS Meter | 1.086 | 0.9776 | 0 | 1.086 | 9.9817 | 9.9817
5117 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | TADIGOL_CROSS _66 | 1230103907020101 | F08-KAPALLI NJY | NJY | DLMS Meter | 0.5927 | 0.54258 | 0 | 0.5927 | 8.4566 | 74.6756
5118 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | TADIGOL_CROSS _66 | 1230103907020102 | F09-KONDAMARI | AGRI | DLMS Meter | 0.8132 | 0.44391 | 0.32 | 0.4932 | 9.9935 | 9.9935
5119 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | TADIGOL_CROSS _66 | 1230103907020103 | F10-DODDAPALLI NJY | NJY | DLMS Meter | 1.0622 | 0.96657 | 0 | 1.0622 | 9.0027 | 83.2806
5120 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | TADIGOL_CROSS _66 | 1230103907020104 | F11-LOCHERUVAPALLI | AGRI | DLMS Meter | 0.67 | 0.60295 | 0 | 0.67 | 10.0072 | 10.0072
5121 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901010101 | F01-KYALANUR | NJY | DLMS Meter | 0.23894 | 0.21104 | 0 | 0.23894 | 11.6753 | 60.3985
5122 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901010102 | F02-KAIWARA | AGRI | DLMS Meter | 1.58 | 1.422 | 0 | 1.58 | 10.0008 | 10.0008
5123 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901010103 | F03-KEMPADENAHALLI | AGRI | DLMS Meter | 1.2956 | 1.0492 | 0.13 | 1.1656 | 9.9884 | 9.9884
5124 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901010104 | F04-PERAMACHANAHALLI | AGRI | DLMS Meter | 1.6008 | 1.3195 | 0.135 | 1.4658 | 9.985 | 9.985
5125 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901020301 | F05-HIREKATTIGENAHALLI | AGRI | DLMS Meter | 1.2007 | 1.0805 | 0 | 1.2007 | 10.0137 | 10.0137
5126 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901020302 | F06-AMMANALLUR | AGRI | DLMS Meter | 1.3269 | 1.1644 | 0 | 1.3269 | 12.2465 | 12.2465
5127 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901020303 | F07-VAIJAKUR | AGRI | DLMS Meter | 1.2844 | 0.76892 | 0.43 | 0.85436 | 10.0008 | 10.0008
5128 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901010105 | F08-ATTUR | AGRI | DLMS Meter | 1.3554 | 1.2195 | 0 | 1.3554 | 10.0286 | 10.0286
5129 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901010106 | F09-ALMBAGIRI-(NJY) | NJY | DLMS Meter | 0.84738 | 0.7287 | 0 | 0.84738 | 14.0053 | 73.0958
5130 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901010107 | F10-AKKIMANGALA-(NJY) | NJY | DLMS Meter | 1.4871 | 1.3064 | 0 | 1.4871 | 12.1489 | 64.2919
5131 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901020304 | F11-YNA-(NJY) | NJY | DLMS Meter | 2.2633 | 1.9618 | 0.000309 | 2.263 | 13.3129 | 72.4767
5132 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901020306 | F12-MYLAPURA | AGRI | DLMS Meter | 1.1991 | 1.0791 | 0 | 1.1991 | 10.0112 | 10.0112
5133 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901020305 | F13-TG-NJY-KRISHNAPURA | NJY | DLMS Meter | 0.32248 | 0.28952 | 0 | 0.32248 | 10.2221 | 78.2566
5134 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901010108 | F15-CHENNAKESHAVAPURA. | NJY | DLMS Meter | 1.2938 | 1.1179 | 0 | 1.2938 | 13.5976 | 68.0155
5135 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | TALAGAWARA_66 | 1230402901010109 | F16-BEEDAGANAHALLI | AGRI | DLMS Meter | 1.0324 | 0.92913 | 0 | 1.0324 | 10.0033 | 10.0033
5136 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | TALAGUNDA_66 | 1230102909020101 | F06-DHANAMATNAHALLI | AGRI | DLMS Meter | 1.0868 | 0.97764 | 0 | 1.0868 | 10.0438 | 12.6309
5137 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | TALAGUNDA_66 | 1230102909020102 | F07-BUSSANAHALLI | AGRI | DLMS Meter | 0.8282 | 0.7454 | 0 | 0.8282 | 9.997 | 9.997
5138 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | TALAGUNDA_66 | 1230102909020103 | F08-NAGANALA | NJY | DLMS Meter | 1.1466 | 1.0259 | 0 | 1.1466 | 10.5268 | 73.7454
5139 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901010101 | F01-HONNENAHALLI | AGRI | DLMS Meter | 1.4062 | 1.0139 | 0.275 | 1.1312 | 10.3666 | 10.3666
5140 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901010103 | F03-GADDEKANNUR | AGRI | DLMS Meter | 1.1916 | 1.0726 | 0 | 1.1916 | 9.9815 | 10.3267
5141 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901010104 | F04-KODIRAMASANDRA | AGRI | DLMS Meter | 1.8574 | 0.80116 | 0.9671 | 0.89026 | 10.0086 | 33.3139
5142 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901010105 | F05-STEEL-ALLOYS | INDUSTRIAL | DLMS Meter | 1.5513 | 1.5753 | 0 | 1.5513 | -1.5445 | -1.5445
5143 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901020301 | F06-KMF-DIARY | NJY | DLMS Meter | 3.1083 | 2.806 | 0 | 3.1083 | 9.7253 | 10.667
5144 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901020302 | F07-ABBANI | AGRI | DLMS Meter | 1.3566 | 1.2003 | 0 | 1.3566 | 11.5272 | 11.5272
5145 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901020303 | F08-KEMBODI | AGRI | DLMS Meter | 1.2738 | 1.1252 | 0 | 1.2738 | 11.664 | 11.664
5146 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901020304 | F09-KODIKANNUR | AGRI | DLMS Meter | 1.1032 | 0.7991 | 0.215 | 0.88822 | 10.034 | 12.7835
5147 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901020305 | F10-MEDICAL-COLLEGE | URBAN MIXED LOAD | DLMS Meter | 3.2707 | 2.9703 | 0 | 3.2707 | 9.1864 | 11.1804
5148 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901020306 | F11-KAMADENAHALLI | NJY | DLMS Meter | 1.2086 | 0.74075 | 0.395 | 0.81356 | 8.9496 | 51.2701
5149 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901020307 | F12-PATNA NJY | NJY | DLMS Meter | 1.4513 | 0.73083 | 0.626 | 0.82532 | 11.4489 | 60.5763
5150 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901020101 | F13-SHILINGIRI | NJY | DLMS Meter | 0.5418 | 0.14866 | 0.378 | 0.1638 | 9.2415 | 35.189
5151 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901020308 | F14- SRIYA FARM | INDUSTRIAL | DLMS Meter | 0.328 | 0.30916 | 0 | 0.328 | 5.7439 | 5.7439
5152 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | TAVAREKERE(C)_66 | 1310106904010101 | F01-TAVAREKERENJY | NJY | DLMS Meter | 0.4102 | 0.30642 | 0.06875 | 0.34145 | 10.2598 | 35.2938
5153 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | TAVAREKERE(C)_66 | 1310106904010102 | F02-DURVIGERE | AGRI | DLMS Meter | 1.0441 | 0.93923 | 0 | 1.0441 | 10.045 | 10.045
5154 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | TAVAREKERE(C)_66 | 1310106904010103 | F03-MUGALIHALLI IP | AGRI | DLMS Meter | 0.8664 | 0.66872 | 0.122 | 0.7444 | 10.1664 | 10.1664
5155 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | TAVAREKERE(C)_66 | 1310106904010104 | F04-NELLIHANKLU | AGRI | DLMS Meter | 1.3286 | 1.0958 | 0.11 | 1.2186 | 10.0764 | 10.0764
5156 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | TAVAREKERE(C)_66 | 1310106904020301 | F06-MASANIKERENJY | NJY | DLMS Meter | 0.45148 | 0.27844 | 0.143 | 0.30848 | 9.7394 | 28.539
5157 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | TAVAREKERE(C)_66 | 1310106904020302 | F07-GANGEGONDANAHALLI | AGRI | DLMS Meter | 1.6073 | 1.4293 | 0.018 | 1.5893 | 10.0632 | 10.0632
5158 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | TAVAREKERE(C)_66 | 1310106904020303 | F08-JAIPURA | AGRI | DLMS Meter | 0.98692 | 0.74646 | 0.156 | 0.83092 | 10.1646 | 10.1646
5159 | CTAZ | DAVANAGERE | DAVANAGERE | CHANNAGIRI | TAVAREKERE(C)_66 | 1310106904010105 | F09-KAGGI NJY | NJY | DLMS Meter | 0.42554 | 0.30365 | 0.089 | 0.33654 | 9.7728 | 59.3117
5160 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | TAVAREKERE(H)_66 | 1320303904010101 | F01-MG-HATTI | AGRI | DLMS Meter | 2.0135 | 1.7785 | 0 | 2.0135 | 11.6693 | 11.6693
5161 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | TAVAREKERE(H)_66 | 1320303904010102 | F02-MELLEKOTE | AGRI | DLMS Meter | 1.1146 | 0.97992 | 0 | 1.1146 | 12.0833 | 12.0833
5162 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | TAVAREKERE(H)_66 | 1320303904010105 | F03-DANDIKERE | AGRI | DLMS Meter | 1.2618 | 1.0895 | 0 | 1.2618 | 13.6595 | 13.6595
5163 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | TAVAREKERE(H)_66 | 1320303904010103 | F04-MOSARAKUNTE | AGRI | DLMS Meter | 1.2595 | 1.1127 | 0 | 1.2595 | 11.6509 | 11.6509
5164 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | TAVAREKERE(H)_66 | 1320303904020301 | F05-LAKHSMISAGARA | AGRI | DLMS Meter | 1.3616 | 1.2077 | 0 | 1.3616 | 11.303 | 11.303
5165 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | TAVAREKERE(H)_66 | 1320303904020302 | F06-TAVAREKERE | NJY | DLMS Meter | 0.3587 | 0.31171 | 0.015 | 0.3437 | 9.3064 | 36.5638
5166 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | TAVAREKERE(H)_66 | 1320303904010104 | F07-GANADAHUNASE | AGRI | DLMS Meter | 0.97512 | 0.82094 | 0.055455 | 0.91966 | 10.7351 | 10.7351
5167 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | TAVAREKERE(H)_66 | 1320303904020303 | F08-G-RANGANAHALLI | AGRI | DLMS Meter | 1.1146 | 1.0033 | 0 | 1.1146 | 9.978 | 9.978
5168 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | TAVAREKERE(H)_66 | 1320303904010106 | F09-GANDHINAGARA | NJY | DLMS Meter | 0.2627 | 0.23333 | 0 | 0.2627 | 11.1816 | 29.8239
5169 | CTAZ | TUMKUR | MADHUGIRI | SIRA RURAL | TAVAREKERE(H)_66 | 1320303904020304 | F10-SOREKUNTE NJY | NJY | DLMS Meter | 0.2774 | 0.24328 | 0 | 0.2774 | 12.2999 | 57.2531
5170 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902010101 | F01-TAVAREKERE-TOWN | URBAN MIXED LOAD | DLMS Meter | 3.4564 | 2.9762 | 0.3 | 3.1564 | 5.708 | 10.2007
5171 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902010102 | F02-METEPALYA | URBAN MIXED LOAD | DLMS Meter | 1.5803 | 0.82958 | 0.661 | 0.91928 | 9.7579 | 10.7763
5172 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902010103 | F03-JATTIPALYA | URBAN MIXED LOAD | DLMS Meter | 5.312 | 5.0342 | 0 | 5.312 | 5.2294 | 6.9342
5173 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902020301 | F05-DODDALADAMARA | URBAN MIXED LOAD | DLMS Meter | 0.8607 | 0.81455 | 0 | 0.8607 | 5.3621 | 5.3621
5174 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902020302 | F06-STONE-CRUSHER | INDUSTRIAL | DLMS Meter | 1.5187 | 1.3084 | 0.11 | 1.4087 | 7.1201 | 7.1201
5175 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902020303 | F07-CHANNENAHALLI IND | INDUSTRIAL | DLMS Meter | 3.7382 | 3.4927 | 0 | 3.7382 | 6.5653 | 7.9592
5176 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902020304 | F08-KADABAGERE | URBAN MIXED LOAD | DLMS Meter | 1.4179 | 0.96162 | 0.39 | 1.0279 | 6.4514 | 6.8009
5177 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902010301 | F09-TAVAREKERE-ISRO | GOVERNMENT OFFICES | DLMS Meter | 1.7155 | 1.7048 | 0 | 1.7155 | 0.62082 | 0.62306
5178 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902010302 | F10-KITTANAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.5848 | 1.9173 | 0.5192 | 2.0656 | 7.1765 | 7.1765
5179 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TAVAREKERE_66 | 1210105902010105 | F11-MADAPATNA STONE CRUSHER | INDUSTRIAL | DLMS Meter | 1.3041 | 1.2592 | 0 | 1.3041 | 3.4438 | 4.1998
5180 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902010101 | F01-KEMPANAHALLI | AGRI | DLMS Meter | 0.99408 | 0.76425 | 0.145 | 0.84908 | 9.9906 | 9.9906
5181 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902010102 | F02-K.G.HALLI | AGRI | DLMS Meter | 1.103 | 0.6433 | 0.388 | 0.715 | 10.0274 | 10.0274
5182 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902010103 | F03-TEKAL | AGRI | DLMS Meter | 1.1441 | 0.91699 | 0.125 | 1.0191 | 10.0166 | 10.0166
5183 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902010104 | F04-HULADENAHALLI | NJY | DLMS Meter | 2.0435 | 1.5675 | 0.32 | 1.7235 | 9.0506 | 73.0566
5184 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902010105 | F05-IND.EXPRESS | NJY | DLMS Meter | 1.5006 | 1.3695 | 0 | 1.5006 | 8.7341 | 74.9692
5185 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902020301 | F06-NELLAHALLI | AGRI | DLMS Meter | 1.5204 | 1.2335 | 0.15 | 1.3704 | 9.9901 | 9.9901
5186 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902020302 | F07-HUNSEKOTE | INDUSTRIAL | DLMS Meter | 0.3658 | 0.33843 | 0 | 0.3658 | 7.4814 | 29.9073
5187 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902020303 | F08-KOMMANAHALLI | AGRI | DLMS Meter | 1.3967 | 1.1346 | 0.136 | 1.2607 | 10.0028 | 10.0028
5188 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902020304 | F09-SHETTAHALLI | AGRI | DLMS Meter | 1.5798 | 1.4218 | 0 | 1.5798 | 10.0005 | 10.0005
5189 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902020305 | F10-BANAHALLI | NJY | DLMS Meter | 2.1888 | 2.0279 | 0 | 2.1888 | 7.3526 | 51.0607
5190 | BRAZ | KOLAR | KGF | MALUR | TEKAL_66 | 1230204902020306 | F11-NOOTUVE | INDUSTRIAL | DLMS Meter | 2.2883 | 2.1534 | 0 | 2.2883 | 5.8962 | 9.0862
5191 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905010101 | F01-BENDIGERI | AGRI | DLMS Meter | 1.0874 | 0.97826 | 0 | 1.0874 | 10.0333 | 10.0333
5192 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HARAPPANAHALLI_66 | 1310303907010102 | F02-ANANTANAHALLI-NJY | NJY | DLMS Meter | 0.81434 | 0.70957 | 0.037 | 0.77734 | 8.7182 | 25.6669
5193 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905020301 | F04-GUNDAGATTI | AGRI | DLMS Meter | 0.8187 | 0.73647 | 0 | 0.8187 | 10.0441 | 10.0441
5194 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905010104 | F06-RAGIMASALWADA | AGRI | DLMS Meter | 1.3337 | 1.2367 | 0 | 1.3337 | 7.2696 | 7.2696
5195 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905020304 | F07-CHIRASTAHALLI | NJY | DLMS Meter | 0.46292 | 0.27164 | 0.1588 | 0.30412 | 10.679 | 39.7215
5196 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905020303 | F08-KADATHI | AGRI | DLMS Meter | 0.7083 | 0.64961 | 0 | 0.7083 | 8.2862 | 8.2862
5197 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905030301 | F09-SHANKRAHALLI | AGRI | DLMS Meter | 0.86486 | 0.77838 | 0 | 0.86486 | 9.999 | 9.999
5198 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905030302 | F10-NAGALAPURA | NJY | DLMS Meter | 0.75558 | 0.45004 | 0.2525 | 0.50308 | 10.5425 | 53.5434
5199 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905030303 | F11-SINGRIHALLI | AGRI | DLMS Meter | 1.2008 | 1.0223 | 0.065 | 1.1358 | 9.9953 | 9.9953
5200 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905030304 | F12-TELIGITOWN | NJY | DLMS Meter | 0.46624 | 0.37284 | 0.0453 | 0.42094 | 11.4274 | 40.9105
5201 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905030502 | F13-THALAVAGALU NJY | NJY | DLMS Meter | 0.7054 | 0.51877 | 0.125 | 0.5804 | 10.618 | 38.047
5202 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905030501 | F14-VATLAHALLI NJY | NJY | DLMS Meter | 0.4354 | 0.25535 | 0.1525 | 0.2829 | 9.7395 | 55.7196
5203 | BMASZ | WEST | RAJAJINAGAR | N1 | TELECOMLAYOUT_66 | 1130101901020101 | F02-TELECOM | URBAN MIXED LOAD | DLMS Meter | 1.9779 | 1.6405 | 0.2627 | 1.7152 | 4.3585 | 14.8525
5204 | BMANZ | EAST | VIDHANASOUDHA | W3 | TELECOMLAYOUT_66 | 1130101901020102 | F03-TELECOM-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 5.4396 | 4.2138 | 0.766 | 4.6736 | 9.8388 | 22.637
5205 | BMANZ | EAST | VIDHANASOUDHA | W3 | TELECOMLAYOUT_66 | 1130101901020103 | F04-HOSAHALLI-MAIN-ROAD | URBAN MIXED LOAD | DLMS Meter | 5.9424 | 4.2125 | 1.0775 | 4.8649 | 13.4116 | 17.321
5206 | BMANZ | EAST | VIDHANASOUDHA | W3 | TELECOMLAYOUT_66 | 1130101901010301 | F05-CEMETORY-RMU | URBAN MIXED LOAD | DLMS Meter | 5.2608 | 3.7722 | 0.935 | 4.3258 | 12.7979 | 20.047
5207 | BMASZ | WEST | RAJAJINAGAR | N2 | TELECOMLAYOUT_66 | 1130101901020301 | F06-F-AYURVEDIC-COLLEGE | URBAN MIXED LOAD | DLMS Meter | 2.9192 | 2.6426 | 0.10891 | 2.8103 | 5.9662 | 10.0173
5208 | BMASZ | WEST | RAJAJINAGAR | N2 | TELECOMLAYOUT_66 | 1130101901010302 | F07-F-BDA-COMPLEX | URBAN MIXED LOAD | DLMS Meter | 3.3965 | 3.0972 | 0.044376 | 3.3522 | 7.6051 | 9.9553
5209 | BMASZ | WEST | RAJAJINAGAR | N1 | TELECOMLAYOUT_66 | 1130101901020104 | F08-GUBBANA-ESTATE | URBAN MIXED LOAD | DLMS Meter | 3.5395 | 2.559 | 0.83804 | 2.7015 | 5.2752 | 15.7115
5210 | BMANZ | EAST | VIDHANASOUDHA | W3 | TELECOMLAYOUT_66 | 1130101901010303 | F09-RAILWAY-PARALLEL-(RAILWAY-COLONY) | URBAN MIXED LOAD | DLMS Meter | 3.355 | 2.1077 | 1.0195 | 2.3356 | 9.7544 | 24.0855
5211 | BMASZ | WEST | RAJAJINAGAR | N1 | TELECOMLAYOUT_66 | 1130101901010304 | F13-CHOLURPALYA | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5212 | BMANZ | EAST | VIDHANASOUDHA | W3 | TELECOMLAYOUT_66 | 1130101901020308 | F15-PARK WEST | DOMESTIC | DLMS Meter | 0.81961 | 0.74018 | 0 | 0.81961 | 9.6916 | 13.8203
5213 | BMANZ | EAST | VIDHANASOUDHA | W3 | TELECOMLAYOUT_66 | 1130101901020309 | F16-PRESTIGE WOODS | DOMESTIC | DLMS Meter | 1.2974 | 0.55197 | 0.6882 | 0.60918 | 9.3904 | 13.9158
5214 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TGHALLI_66 | 1210105901010101 | F01-TGGANGAPPANAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.5461 | 1.4673 | 0 | 1.5461 | 5.0956 | 5.0956
5215 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TGHALLI_66 | 1210105901010102 | F02-BACHENAHATTY NJY | NJY | DLMS Meter | 0.48822 | 0.31 | 0.149 | 0.33922 | 8.6139 | 33.1327
5216 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TGHALLI_66 | 1210105901010103 | F03-MOTAGANAHALLI | URBAN MIXED LOAD | DLMS Meter | 0.82328 | 0.74933 | 0 | 0.82328 | 8.9822 | 21.3513
5217 | BRAZ | RAMANAGAR | MAGADI | TAVAREKERE | TGHALLI_66 | 1210105901010104 | F04-VARDHENAHALLI | AGRI | DLMS Meter | 0.9184 | 0.8268 | 0 | 0.9184 | 9.9743 | 9.9743
5218 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THALKERE_110 | 1320202903010101 | F01-MANGIKUPPE | AGRI | DLMS Meter | 0.496 | 0.44626 | 0 | 0.496 | 10.029 | 10.029
5219 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THALKERE_110 | 1320202903010102 | F02-TALKERE | AGRI | DLMS Meter | 0.96532 | 0.86127 | 0 | 0.96532 | 10.7784 | 10.7784
5220 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THALKERE_110 | 1320202903010103 | F03-DODDAGORAGATTA | AGRI | DLMS Meter | 1.1029 | 0.99264 | 0 | 1.1029 | 9.9944 | 9.9944
5221 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THALKERE_110 | 1320202903010104 | F04-DONKIHALLI | AGRI | DLMS Meter | 0.66074 | 0.58463 | 0 | 0.66074 | 11.5194 | 11.5194
5222 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THALKERE_110 | 1320202903010106 | F06-D KALKERE-NJY | NJY | DLMS Meter | 0.40944 | 0.36487 | 0 | 0.40944 | 10.8854 | 35.0672
5223 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THALKERE_110 | 1320202903020303 | F09-PUTTAMADHIHALLI | AGRI | DLMS Meter | 0.7444 | 0.66996 | 0 | 0.7444 | 10.0001 | 10.0001
5224 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THALKERE_110 | 1320202903020301 | F10-LALANAKATTE | AGRI | DLMS Meter | 0.8018 | 0.7218 | 0 | 0.8018 | 9.9778 | 9.9778
5225 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THALKERE_110 | 1320202903020302 | F11-PURA | AGRI | DLMS Meter | 0.7544 | 0.67897 | 0 | 0.7544 | 9.9991 | 9.9991
5226 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THALKERE_110 | 1320202903020304 | F12-ANNEMALE | AGRI | DLMS Meter | 0.7432 | 0.66905 | 0 | 0.7432 | 9.9773 | 9.9773
5227 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | THALLAK_66 | 1310403905020301 | F01-DEVARAHALLI | AGRI | DLMS Meter | 0.00502 | 0.004454 | 0 | 0.00502 | 11.2749 | 11.2749
5228 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | THALLAK_66 | 1310403905020302 | F02-NKHATTI | AGRI | DLMS Meter | 0.68544 | 0.61669 | 0 | 0.68544 | 10.0305 | 10.3571
5229 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | THALLAK_66 | 1310403905020303 | F03-BRHALLI | AGRI | DLMS Meter | 1.358 | 1.2222 | 0 | 1.358 | 10.0008 | 10.7628
5230 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | THALLAK_66 | 1310403905010101 | F04-VALSE | AGRI | DLMS Meter | 1.2749 | 1.1469 | 0 | 1.2749 | 10.0402 | 10.8453
5231 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | THALLAK_66 | 1310403905010102 | F05-HIREHALLI | AGRI | DLMS Meter | 0.9006 | 0.8106 | 0 | 0.9006 | 9.9937 | 9.9937
5232 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | THALLAK_66 | 1310403905010103 | F06-CHIKKAMMANAHALLI | AGRI | DLMS Meter | 0.9844 | 0.87137 | 0 | 0.9844 | 11.4822 | 13.0982
5233 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | THALLAK_66 | 1310403905020304 | F07-THALLAK | NJY | DLMS Meter | 0.52432 | 0.47559 | 0 | 0.52432 | 9.2934 | 43.3827
5234 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | THALLAK_66 | 1310403905010104 | F10-BUKKALARAHALLI | AGRI | DLMS Meter | 1.3043 | 1.1523 | 0 | 1.3043 | 11.6539 | 11.6539
5235 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | THALLAK_66 | 1310403905020305 | F11-RUDRAMMANNAHALLY | NJY | DLMS Meter | 1.0023 | 0.90777 | 0 | 1.0023 | 9.4311 | 53.0594
5236 | CTAZ | DAVANAGERE | HIRIYURU | TALAKU | THALLAK_66 | 1310403905010107 | F12-BANJIGERE | NJY | DLMS Meter | 0.45604 | 0.39694 | 0 | 0.45604 | 12.959 | 56.8892
5237 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904010102 | F02-AREMALLENAHALLI | AGRI | DLMS Meter | 0.62644 | 0.56366 | 0 | 0.62644 | 10.0225 | 10.0225
5238 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904010103 | F03-CHANDRAPURA | AGRI | DLMS Meter | 0.65264 | 0.58749 | 0 | 0.65264 | 9.9821 | 9.9821
5239 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904010104 | F04-HULIKAL | AGRI | DLMS Meter | 0.81628 | 0.73478 | 0 | 0.81628 | 9.9838 | 9.9838
5240 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904010105 | F05-THANDAGA | AGRI | DLMS Meter | 0.68216 | 0.60365 | 0 | 0.68216 | 11.5092 | 11.5092
5241 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904010106 | F06-DODDAGHATTA | AGRI | DLMS Meter | 0.62626 | 0.56365 | 0 | 0.62626 | 9.9981 | 9.9981
5242 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904010107 | F07-SOMENAHALLI NJY | NJY | DLMS Meter | 0.2932 | 0.24928 | 0.005 | 0.2882 | 13.5054 | 45.0309
5243 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904010108 | F08-BYADARAKODIGEHALLI NJY | NJY | DLMS Meter | 0.1601 | 0.13214 | 0.007 | 0.1531 | 13.6878 | 41.0001
5244 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904020301 | F09-RANGANATHA PURA | AGRI | DLMS Meter | 0.1972 | 0.17752 | 0 | 0.1972 | 9.9787 | 9.9787
5245 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904020302 | F10-KALKERE | AGRI | DLMS Meter | 0.302 | 0.27172 | 0 | 0.302 | 10.0248 | 10.0248
5246 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904020303 | F11-VITTALADEVARAHALLI | AGRI | DLMS Meter | 0.78762 | 0.60147 | 0.116 | 0.67162 | 10.4444 | 10.4444
5247 | BRAZ | KOLAR | KGF | MULABAGILU | THAYLUR_66 | 1230202907010101 | F01-MOTHAKAPALLI | AGRI | DLMS Meter | 1.2031 | 1.0827 | 0 | 1.2031 | 10.0031 | 10.0031
5248 | BRAZ | KOLAR | KGF | MULABAGILU | THAYLUR_66 | 1230202907020301 | F02-DOOLAPALLI | AGRI | DLMS Meter | 1.4474 | 1.3026 | 0 | 1.4474 | 10.0048 | 10.0048
5249 | BRAZ | KOLAR | KGF | MULABAGILU | THAYLUR_66 | 1230202907020302 | F03-HONAGANAHALLI | AGRI | DLMS Meter | 1.1278 | 1.015 | 0 | 1.1278 | 9.9994 | 9.9994
5250 | BRAZ | KOLAR | KGF | MULABAGILU | THAYLUR_66 | 1230202907010102 | F04-MELTHAYLUR | AGRI | DLMS Meter | 1.1921 | 1.0728 | 0 | 1.1921 | 10.0069 | 10.0069
5251 | BRAZ | KOLAR | KGF | MULABAGILU | THAYLUR_66 | 1230202907010103 | F05-MADIVALA-NJY | NJY | DLMS Meter | 1.1161 | 0.99862 | 0.011 | 1.1051 | 9.6324 | 74.7408
5252 | BRAZ | KOLAR | KGF | MULABAGILU | THAYLUR_66 | 1230202907020303 | F06-THIRUMANAHALLI | AGRI | DLMS Meter | 1.2619 | 0.94484 | 0.212 | 1.0499 | 10.007 | 10.007
5253 | BRAZ | KOLAR | KGF | MULABAGILU | THAYLUR_66 | 1230202907020304 | F07-BYRASANDRA | AGRI | DLMS Meter | 0.6869 | 0.61797 | 0 | 0.6869 | 10.0345 | 10.0345
5254 | BRAZ | KOLAR | KGF | MULABAGILU | THAYLUR_66 | 1230202907020305 | F08-THIMMARAVATHANAHALLI | AGRI | DLMS Meter | 1.3657 | 1.229 | 0 | 1.3657 | 10.0037 | 10.0037
5255 | BRAZ | KOLAR | KGF | MULABAGILU | THAYLUR_66 | 1230202907010104 | F09-KEELAGALI-NJY | NJY | DLMS Meter | 1.0668 | 0.96372 | 0 | 1.0668 | 9.6609 | 67.809
5256 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | THERIYUR_66 | 1320304904010101 | F01-PARTHIHALLI | AGRI | DLMS Meter | 0.6128 | 0.55164 | 0 | 0.6128 | 9.9806 | 9.9806
5257 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | THERIYUR_66 | 1320304904010102 | F02-GUNDAGAL | AGRI | DLMS Meter | 0.542 | 0.48786 | 0 | 0.542 | 9.9887 | 9.9887
5258 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | THERIYUR_66 | 1320304904010103 | F03-MASARAPADI | AGRI | DLMS Meter | 0.62104 | 0.55891 | 0 | 0.62104 | 10.004 | 10.262
5259 | CTAZ | TUMKUR | MADHUGIRI | KODIGENAHALLY | THERIYUR_66 | 1320304904010104 | F04-MUDDENAHALLI | AGRI | DLMS Meter | 0.8546 | 0.76895 | 0 | 0.8546 | 10.022 | 10.022
5260 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | THIMMAMPALLI_66 | 1230305907010101 | F02-THIMMAMPALLY | AGRI | DLMS Meter | 1.4325 | 1.2892 | 0 | 1.4325 | 10.0013 | 10.0013
5261 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | THIMMAMPALLI_66 | 1230305907010102 | F03-GORTHAPALLY | AGRI | DLMS Meter | 1.1838 | 1.0621 | 0 | 1.1838 | 10.2799 | 10.2799
5262 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | THIMMAMPALLI_66 | 1230305907020301 | F04-DEVIKUNTE | AGRI | DLMS Meter | 0.72548 | 0.64846 | 0 | 0.72548 | 10.616 | 10.616
5263 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | THIMMAMPALLI_66 | 1230305907020302 | F05-NAGARLU | NJY | DLMS Meter | 0.47755 | 0.42888 | 0 | 0.47755 | 10.1912 | 73.0901
5264 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | THIMMAMPALLI_66 | 1230305907020303 | F06-VASANTHAPURA | AGRI | DLMS Meter | 0.57496 | 0.51747 | 0 | 0.57496 | 9.9988 | 9.9988
5265 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | THIMMAMPALLI_66 | 1230305907010103 | F07-KOLIMPALLI | AGRI | DLMS Meter | 0.34876 | 0.31391 | 0 | 0.34876 | 9.9934 | 9.9934
5266 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | THIMMAMPALLI_66 | 1230305907010105 | F08-KOTHAKOTE | AGRI | DLMS Meter | 0.67518 | 0.6077 | 0 | 0.67518 | 9.9944 | 9.9944
5267 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | THIMMAMPALLI_66 | 1230305907020304 | F10-PESALAPARTHI | NJY | DLMS Meter | 0.8587 | 0.73408 | 0.028 | 0.8307 | 11.6315 | 71.5444
5268 | BRAZ | KOLAR | CHIKKABALLAPURA | BAGEPALLI | THIMMAMPALLI_66 | 1230305907020305 | F11-MULLANGICHETLAPALLI | NJY | DLMS Meter | 0.5145 | 0.44044 | 0.021 | 0.4935 | 10.7511 | 68.3163
5269 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010101 | F01-BIDRAKATTE | AGRI | DLMS Meter | 1.5464 | 1.3548 | 0 | 1.5464 | 12.3927 | 12.3927
5270 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010104 | F02-SIDDAPANAPALYA IP | AGRI | DLMS Meter | 1.0294 | 0.90929 | 0 | 1.0294 | 11.6699 | 11.6699
5271 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010102 | F03-DOMMANKUPPE | AGRI | DLMS Meter | 0.90558 | 0.79741 | 0 | 0.90558 | 11.9449 | 11.9449
5272 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010301 | F04-MALLAPPANAHALLI NJY | NJY | DLMS Meter | 0.38116 | 0.32981 | 0 | 0.38116 | 13.471 | 54.3744
5273 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010103 | F05-KARADIGERE IP | AGRI | DLMS Meter | 1.5143 | 1.3261 | 0 | 1.5143 | 12.4254 | 12.4254
5274 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010302 | F06-ARIYUR | AGRI | DLMS Meter | 1.232 | 1.1089 | 0 | 1.232 | 9.9931 | 9.9931
5275 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010303 | F07-G-H-RHISALA | AGRI | DLMS Meter | 0.83238 | 0.73647 | 0 | 0.83238 | 11.5229 | 11.5229
5276 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010304 | F08-NAGAVALLI-EXPRESS | RURAL MIXED LOAD | DLMS Meter | 0.60412 | 0.51851 | 0 | 0.60412 | 14.1714 | 20.9259
5277 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010305 | F09-GANGONAHALLY-NJY | NJY | DLMS Meter | 0.3918 | 0.33542 | 0 | 0.3918 | 14.3912 | 49.5332
5278 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010306 | F10-THIMMASANDRA NJY | NJY | DLMS Meter | 0.46195 | 0.39827 | 0 | 0.46195 | 13.7858 | 31.7389
5279 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | THIMMASANDRA_66 | 1320104905010105 | F11-GODREJ | INDUSTRIAL | DLMS Meter | 0.1879 | 0.1837 | 0 | 0.1879 | 2.2352 | 2.2352
5280 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | THIPPURU_66 | 1320401901010104 | F01-SIDDAPURA | AGRI | DLMS Meter | 0.4328 | 0.39569 | 0 | 0.4328 | 8.5737 | 8.5737
5281 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | THIPPURU_66 | 1320401901010101 | F02-SINGONAHALLI | AGRI | DLMS Meter | 0.686 | 0.60328 | 0 | 0.686 | 12.0576 | 12.0576
5282 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | THIPPURU_66 | 1320401901010103 | F03-HPCL | URBAN MIXED LOAD | DLMS Meter | 0.9388 | 0.87282 | 0 | 0.9388 | 7.0285 | 21.0902
5283 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | THIPPURU_66 | 1320401901010102 | F04-KADSHETTIHALLI | AGRI | DLMS Meter | 0.7092 | 0.62168 | 0 | 0.7092 | 12.3408 | 12.3408
5284 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010101 | F01-POTHENAHALLY | AGRI | DLMS Meter | 0.42882 | 0.32093 | 0.072 | 0.35682 | 10.0597 | 10.0597
5285 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010102 | F02-ALIPURA | AGRI | DLMS Meter | 1.3824 | 1.244 | 0 | 1.3824 | 10.0116 | 12.7064
5286 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010103 | F03-MANCHENAHALLY | AGRI | DLMS Meter | 1.9121 | 1.4194 | 0.335 | 1.5771 | 10.0002 | 10.0002
5287 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010104 | F04-ARKUNDA | AGRI | DLMS Meter | 1.3584 | 1.2224 | 0 | 1.3584 | 10.0118 | 10.0118
5288 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010105 | F05-HALEHALLY | AGRI | DLMS Meter | 1.1835 | 1.0661 | 0 | 1.1835 | 9.9206 | 9.9206
5289 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010301 | F06-THONDEBHAVI-LOCAL | AGRI | DLMS Meter | 1.8164 | 1.5267 | 0.12 | 1.6964 | 10.0013 | 10.0013
5290 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010302 | F07-THIPPAGANAHALLY | AGRI | DLMS Meter | 1.1313 | 1.0182 | 0 | 1.1313 | 9.993 | 9.993
5291 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010303 | F08-G.HOSAHALLY | AGRI | DLMS Meter | 1.4966 | 1.14 | 0.23 | 1.2666 | 9.9886 | 9.9886
5292 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010304 | F09-PIONEER | INDUSTRIAL | DLMS Meter | 0.65528 | 0.6489 | 0 | 0.65528 | 0.97306 | 1.4339
5293 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010305 | F10-THARIDAL | AGRI | DLMS Meter | 1.8294 | 1.6463 | 0 | 1.8294 | 10.0095 | 10.0095
5294 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010306 | F11-NJY-BEVINAHALLI | NJY | DLMS Meter | 3.3481 | 2.8875 | 0 | 3.3481 | 13.7578 | 69.2421
5295 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010106 | F12-NJY-RAILWAY-STATION | NJY | DLMS Meter | 1.9554 | 1.6718 | 0 | 1.9554 | 14.5022 | 35.9163
5296 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | THONDEBHAVI_66 | 1230303905010107 | F13-KALLINAYAKANAHALLI--NJY | NJY | DLMS Meter | 0.43506 | 0.39571 | 0 | 0.43506 | 9.0452 | 61.4083
5297 | BRAZ | RAMANAGAR | MAGADI | MAGADI | THOOBINAKERE_220/66/11 | 1210102904010201 | F03-SATHANOORU | AGRI | DLMS Meter | 0.9258 | 0.69802 | 0.15 | 0.7758 | 10.0259 | 10.0259
5298 | BRAZ | RAMANAGAR | MAGADI | MAGADI | THOOBINAKERE_220/66/11 | 1210102904010202 | F04-MATHIKERE | AGRI | DLMS Meter | 0.46232 | 0.41586 | 0 | 0.46232 | 10.0493 | 10.0493
5299 | BRAZ | RAMANAGAR | MAGADI | MAGADI | THOOBINAKERE_220/66/11 | 1210102904010203 | F05-MANGAL | NJY | DLMS Meter | 0.1898 | 0.13312 | 0.043 | 0.1468 | 9.3158 | 38.7796
5300 | BRAZ | RAMANAGAR | MAGADI | MAGADI | THOOBINAKERE_220/66/11 | 1210102904010204 | F06- KEMPASAGARA NJY | NJY | DLMS Meter | 0.352 | 0.23387 | 0.094 | 0.258 | 9.3536 | 36.47
5301 | BRAZ | KOLAR | KGF | MALUR | THORALAKKI_66 | 1230204906010103 | F02-GOLLAHALLI | NJY | DLMS Meter | 1.727 | 1.5824 | 0 | 1.727 | 8.3749 | 9.4506
5302 | BRAZ | KOLAR | KGF | MALUR | THORALAKKI_66 | 1230204906010101 | F04-THORALAKKI NJY | NJY | DLMS Meter | 0.4288 | 0.38153 | 0 | 0.4288 | 11.0229 | 77.0277
5303 | BRAZ | KOLAR | KGF | MALUR | THORALAKKI_66 | 1230204906010104 | F05-DEVARAHALLI | AGRI | DLMS Meter | 0.904 | 0.81348 | 0 | 0.904 | 10.0136 | 10.0136
5304 | BRAZ | KOLAR | KGF | MALUR | THORALAKKI_66 | 1230204906010102 | F06-THURUVALATTI | AGRI | DLMS Meter | 0.8314 | 0.27244 | 0.5285 | 0.3029 | 10.0568 | 11.1074
5305 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901010106 | F01-SURENAHALLI | AGRI | DLMS Meter | 1.1826 | 1.0643 | 0 | 1.1826 | 10.003 | 10.003
5306 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901010102 | F02-KABBIGERE | AGRI | DLMS Meter | 1.1229 | 0.99783 | 0 | 1.1229 | 11.1365 | 11.1468
5307 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901010103 | F03-KODIHALLI | NJY | DLMS Meter | 0.64494 | 0.58427 | 0 | 0.64494 | 9.4075 | 42.8647
5308 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901010104 | F04-DODDERI | AGRI | DLMS Meter | 1.2335 | 1.079 | 0 | 1.2335 | 12.5253 | 12.5253
5309 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901020301 | F05-THOVINKERE-RURAL | AGRI | DLMS Meter | 1.9295 | 1.7367 | 0 | 1.9295 | 9.9921 | 10.0779
5310 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901020302 | F06-THOVINKERE-TOWN | URBAN MIXED LOAD | DLMS Meter | 0.7081 | 0.34638 | 0.341 | 0.3671 | 5.6437 | 33.5014
5311 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901020303 | F07-KESTUR | AGRI | DLMS Meter | 1.1759 | 1.0363 | 0 | 1.1759 | 11.8711 | 11.8711
5312 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901020304 | F08-GOWRAGONDANA-HALLI | AGRI | DLMS Meter | 1.1262 | 0.98571 | 0 | 1.1262 | 12.4733 | 12.4733
5313 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901010105 | F09-SUREKUNTE | AGRI | DLMS Meter | 1.3642 | 1.2014 | 0 | 1.3642 | 11.9348 | 11.9348
5314 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901010101 | F10-SIDDRABETTA | AGRI | DLMS Meter | 1.4047 | 1.243 | 0 | 1.4047 | 11.5109 | 11.5109
5315 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901020305 | F11-SIDDESHWARA | NJY | DLMS Meter | 0.36275 | 0.3276 | 0 | 0.36275 | 9.6909 | 63.4226
5316 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901020306 | F12-DANDIMARAMMA | NJY | DLMS Meter | 0.1219 | 0.11046 | 0 | 0.1219 | 9.3831 | 66.22
5317 | CTAZ | TUMKUR | MADHUGIRI | KORATAGERE | THOVINAKERE_66 | 1320305901010107 | F13-CHOWDESHWARI | NJY | DLMS Meter | 1.3338 | 1.0224 | 0.208 | 1.1258 | 9.1864 | 27.0797
5318 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907010101 | F02-LAKKENAHALLI | AGRI | DLMS Meter | 0.9402 | 0.84606 | 0 | 0.9402 | 10.0127 | 10.0127
5319 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907020101 | F03-BADAKEGUDLU | AGRI | DLMS Meter | 2.0807 | 1.8061 | 0 | 2.0807 | 13.1979 | 13.1979
5320 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907010106 | F04-THIMMANALLI | AGRI | DLMS Meter | 1.0254 | 0.89865 | 0 | 1.0254 | 12.3588 | 12.3588
5321 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907010107 | F05-RAMANAHALLI | AGRI | DLMS Meter | 0.8207 | 0.71942 | 0 | 0.8207 | 12.3403 | 12.3403
5322 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907020301 | F06-GANTENHALLI | AGRI | DLMS Meter | 1.5292 | 1.3579 | 0 | 1.5292 | 11.2009 | 11.376
5323 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907020302 | F07-KUSHALPURA | AGRI | DLMS Meter | 0.81872 | 0.73664 | 0 | 0.81872 | 10.025 | 10.025
5324 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907020303 | F08-KANDIKERE | AGRI | DLMS Meter | 1.2702 | 1.1151 | 0 | 1.2702 | 12.208 | 12.208
5325 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907020103 | F09-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 0.54312 | 0.51978 | 0 | 0.54312 | 4.2968 | 25.5784
5326 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907020304 | F10-AGGIGUDDE | AGRI | DLMS Meter | 0.82124 | 0.72015 | 0 | 0.82124 | 12.3088 | 12.3088
5327 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907010102 | F11-AGRAHARA-NJY | NJY | DLMS Meter | 0.48987 | 0.418 | 0 | 0.48987 | 14.6716 | 59.1298
5328 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907010103 | F12-SIDDANAKATTE-NJY | NJY | DLMS Meter | 0.45449 | 0.38843 | 0 | 0.45449 | 14.5352 | 54.0399
5329 | CTAZ | TUMKUR | TIPTUR | CN HALLY | TIMMANAHALLI_110 | 1320203907020305 | F13-SADARAHALLI NJY | NJY | DLMS Meter | 0.2665 | 0.24093 | 0 | 0.2665 | 9.5932 | 40.7966
5330 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901010102 | F02-ICHANOOR | AGRI | DLMS Meter | 0.9154 | 0.6978 | 0.14 | 0.7754 | 10.0079 | 10.526
5331 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901010103 | F03-RANGAPURA | AGRI | DLMS Meter | 0.9546 | 0.85899 | 0 | 0.9546 | 10.0156 | 10.0156
5332 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901010104 | F04-KEREGODI | RURAL MIXED LOAD | DLMS Meter | 1.1766 | 0.91411 | 0.12 | 1.0566 | 13.4854 | 13.4854
5333 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901010108 | F05-VIDHYA NAGARA | URBAN MIXED LOAD | DLMS Meter | 2.0897 | 1.461 | 0.471 | 1.6187 | 9.7385 | 9.7385
5334 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901020301 | F08-MADENOOR | AGRI | DLMS Meter | 1.052 | 0.84772 | 0.11 | 0.942 | 10.0086 | 10.0086
5335 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901020302 | F09-BUSSTAND | URBAN MIXED LOAD | DLMS Meter | 1.493 | 1.3523 | 0.005 | 1.488 | 9.1218 | 10.1583
5336 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901030502 | F10-BELAGARAHALLI | AGRI | DLMS Meter | 0.69 | 0.57138 | 0.055 | 0.635 | 10.0184 | 10.0184
5337 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901030501 | F11-NELAGONDANAHALLI | NJY | DLMS Meter | 0.4382 | 0.32441 | 0.059 | 0.3792 | 14.448 | 56.6215
5338 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901020305 | F12-SARTHAVALLI | AGRI | DLMS Meter | 0.8124 | 0.73109 | 0 | 0.8124 | 10.0091 | 10.0091
5339 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901030503 | F13-TADASOOR | AGRI | DLMS Meter | 0.862 | 0.77599 | 0 | 0.862 | 9.9775 | 11.5729
5340 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901020303 | F15-NJY-MARANAGERE | NJY | DLMS Meter | 0.0947 | 0.086447 | 0 | 0.0947 | 8.7149 | 43.4702
5341 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901020304 | F16-NJY-SHIVARA | NJY | DLMS Meter | 0.6592 | 0.4585 | 0.129 | 0.5302 | 13.523 | 34.2282
5342 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902010101 | F01-PRAGATHI | INDUSTRIAL | DLMS Meter | 0.36652 | 0.32483 | 0.025 | 0.34152 | 4.8867 | 6.1879
5343 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902010102 | F02-TAPASIPURA | NJY | DLMS Meter | 1.4377 | 1.1966 | 0.05 | 1.3877 | 13.7743 | 54.6492
5344 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902010103 | F03-S-S-GHATI | AGRI | DLMS Meter | 0.89216 | 0.80282 | 0 | 0.89216 | 10.0135 | 10.0135
5345 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902010104 | F04-MELEKOTE | AGRI | DLMS Meter | 1.0515 | 0.9465 | 0 | 1.0515 | 9.9874 | 9.9874
5346 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902020101 | F05-HIREMUDDENAHALLI | AGRI | DLMS Meter | 0.98741 | 0.88844 | 0 | 0.98741 | 10.0237 | 10.0237
5347 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902020102 | F06-MACHAGONDANAHALLI | AGRI | DLMS Meter | 0.99165 | 0.89269 | 0 | 0.99165 | 9.9787 | 9.9787
5348 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902020103 | F07-TUBUGERE | AGRI | DLMS Meter | 1.3826 | 1.2443 | 0 | 1.3826 | 10.0039 | 10.0039
5349 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902020104 | F08-GANTIGANAHALLI | AGRI | DLMS Meter | 0.74554 | 0.67093 | 0 | 0.74554 | 10.0068 | 10.0068
5350 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902020302 | F09-VASUDEVANAHALLI | AGRI | DLMS Meter | 0.99517 | 0.89585 | 0 | 0.99517 | 9.98 | 9.98
5351 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902020301 | F10-KALLUKOTE | NJY | DLMS Meter | 0.89334 | 0.61788 | 0.196 | 0.69734 | 11.3957 | 51.2489
5352 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (R) | TUBUGERE_66 | 1210101902010107 | F11-GUNJUR | NJY | DLMS Meter | 0.6403 | 0.50356 | 0.07 | 0.5703 | 11.7023 | 35.9119
5353 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | TUMKUR_66 | 1320101902010101 | F01-VIJAYANAGAR | URBAN MIXED LOAD | DLMS Meter | 1.6254 | 1.4801 | 0 | 1.6254 | 8.9409 | 27.3246
5354 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | TUMKUR_66 | 1320101902010102 | F02-HOYSALA | URBAN MIXED LOAD | DLMS Meter | 2.9594 | 2.7146 | 0 | 2.9594 | 8.271 | 20.0163
5355 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | TUMKUR_66 | 1320101902010107 | F03-SOMESHWARA | URBAN MIXED LOAD | DLMS Meter | 3.0559 | 2.8616 | 0 | 3.0559 | 6.3554 | 18.8186
5356 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | TUMKUR_66 | 1320101902010103 | F04-TUMKUR 1 | URBAN MIXED LOAD | DLMS Meter | 4.0201 | 3.7609 | 0 | 4.0201 | 6.4481 | 14.1111
5357 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | TUMKUR_66 | 1320101902010104 | F05-TUMKUR 3 | AGRI | DLMS Meter | 1.1337 | 0.82744 | 0.19 | 0.94368 | 12.3174 | 12.3174
5358 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | TUMKUR_66 | 1320101902010105 | F06-TUMKUR 2 DC OFFICE | URBAN MIXED LOAD | DLMS Meter | 1.2985 | 1.2126 | 0 | 1.2985 | 6.618 | 7.0723
5359 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | TUMKUR_66 | 1320101902020301 | F07-BELGUMBA | AGRI | DLMS Meter | 1.4612 | 1.2817 | 0 | 1.4612 | 12.2789 | 12.2789
5360 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | TUMKUR_66 | 1320101902020302 | F09-JYOTHIPURA | NJY | DLMS Meter | 1.3887 | 1.2588 | 0 | 1.3887 | 9.358 | 24.1454
5361 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | TUMKUR_66 | 1320101902020303 | F10-HMT | URBAN MIXED LOAD | DLMS Meter | 3.6753 | 3.1751 | 0.4873 | 3.188 | 0.40255 | 14.5957
5362 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION2 | TUMKUR_66 | 1320101902020304 | F11-SIT | URBAN MIXED LOAD | DLMS Meter | 4.2106 | 3.8744 | 0 | 4.2106 | 7.984 | 17.4418
5363 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | TUMKUR_66 | 1320101902020305 | F12-BELLAVI | URBAN MIXED LOAD | DLMS Meter | 3.6665 | 3.267 | 0.15151 | 3.515 | 7.0561 | 21.5461
5364 | CTAZ | TUMKUR | TUMKUR | TUMKUR URBAN SUB DIVISION1 | TUMKUR_66 | 1320101902020501 | F13-ISRO | INDUSTRIAL | DLMS Meter | 0 | 0.016775 | 0 | 0 | 0 | #DIV/0!
5365 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | TUMMINAKATTE_33 | 1310301908010101 | F02-UKKADAGATRI | AGRI | DLMS Meter | 0.7174 | 0.64555 | 0 | 0.7174 | 10.0146 | 12.0001
5366 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | TURUVANUR_66 | 1310202903010101 | F01-BOMMAKKANAHALLI | AGRI | DLMS Meter | 0.67587 | 0.60811 | 0 | 0.67587 | 10.0249 | 10.0249
5367 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | TURUVANUR_66 | 1310202903010102 | F03-AVALENAHALLI | AGRI | DLMS Meter | 0.65642 | 0.5815 | 0 | 0.65642 | 11.414 | 11.414
5368 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | TURUVANUR_66 | 1310202903010103 | F04-DODDAGHATTA | AGRI | DLMS Meter | 0.79904 | 0.71889 | 0 | 0.79904 | 10.0303 | 10.0303
5369 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | TURUVANUR_66 | 1310202903020301 | F05-TURUVANUR | NJY | DLMS Meter | 0.56924 | 0.45061 | 0.05149 | 0.51775 | 12.9676 | 41.0277
5370 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | TURUVANUR_66 | 1310202903020302 | F06-KARIAMMANAHATTI | AGRI | DLMS Meter | 0.56171 | 0.33652 | 0.19436 | 0.36735 | 8.3936 | 8.3936
5371 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | TURUVANUR_66 | 1310202903020303 | F07-KOTEHATTI | AGRI | DLMS Meter | 0.71917 | 0.64897 | 0 | 0.71917 | 9.7617 | 9.7617
5372 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | TURUVANUR_66 | 1310202903020304 | F08-HUNSEKATIE | AGRI | DLMS Meter | 0.94852 | 0.85889 | 0 | 0.94852 | 9.4491 | 9.4491
5373 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | TURUVANUR_66 | 1310202903020305 | F09-PELARHATTI-NJY | NJY | DLMS Meter | 1.2697 | 1.086 | 0.02062 | 1.2491 | 13.0533 | 46.1398
5374 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010101 | F01-NJY-MALLAGHATTA | NJY | DLMS Meter | 0.48647 | 0.4173 | 0.02 | 0.46647 | 10.54 | 25.5582
5375 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010102 | F02-NJY-CHENDUR | NJY | DLMS Meter | 0.49006 | 0.44483 | 0 | 0.49006 | 9.2299 | 28.6638
5376 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010103 | F03-HEMAVATHI | AGRI | DLMS Meter | 0.94662 | 0.85187 | 0 | 0.94662 | 10.0089 | 10.0089
5377 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010104 | F04-KALLANAKERE | AGRI | DLMS Meter | 1.0416 | 0.92018 | 0 | 1.0416 | 11.6606 | 11.6606
5378 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010110 | F05-LOKAMMANAHALLI | AGRI | DLMS Meter | 1.3473 | 1.2121 | 0 | 1.3473 | 10.0358 | 10.0358
5379 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010105 | F06-GOTTIKERE | AGRI | DLMS Meter | 0.80052 | 0.72057 | 0 | 0.80052 | 9.9869 | 9.9869
5380 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010106 | F07-HULIKERE | AGRI | DLMS Meter | 0.645 | 0.58074 | 0 | 0.645 | 9.9628 | 9.9628
5381 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010301 | F08-ANEKERE | AGRI | DLMS Meter | 0.8687 | 0.78212 | 0 | 0.8687 | 9.9663 | 9.9663
5382 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905020505 | F09-BHADRIKASHRAMA-NJY | NJY | DLMS Meter | 1.4675 | 0.25708 | 1.1726 | 0.29488 | 12.8178 | 34.0518
5383 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010303 | F10-BEVINAHALLI | AGRI | DLMS Meter | 0.79252 | 0.71327 | 0 | 0.79252 | 10.0004 | 10.0004
5384 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905020502 | F12-KONDAJJI | AGRI | DLMS Meter | 0.79642 | 0.71682 | 0 | 0.79642 | 9.9947 | 9.9947
5385 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905020503 | F13-TURUVEKERE | URBAN MIXED LOAD | DLMS Meter | 1.996 | 1.7188 | 0.076 | 1.92 | 10.4766 | 14.9768
5386 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905020504 | F15-GONITUMKUR | AGRI | DLMS Meter | 0.86722 | 0.78072 | 0 | 0.86722 | 9.9745 | 9.9745
5387 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010109 | F16-COURT | URBAN MIXED LOAD | DLMS Meter | 0.77046 | 0.65657 | 0.051 | 0.71946 | 8.7409 | 9.6865
5388 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905010302 | F17-THOREMAVIANAHALLI | AGRI | DLMS Meter | 1.0746 | 0.84038 | 0.1408 | 0.9338 | 10.0042 | 10.0042
5389 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905020507 | F18-MUNIYUR | AGRI | DLMS Meter | 0.727 | 0.6546 | 0 | 0.727 | 9.9582 | 9.9582
5390 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | TURUVEKERE_110 | 1320202905020506 | F19-TAVAREKERE NJY | NJY | DLMS Meter | 0.4757 | 0.21416 | 0.23 | 0.2457 | 12.8374 | 41.5302
5391 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901010101 | F01-BIGBAG | INDUSTRIAL | DLMS Meter | 28.0259 | 26.3577 | 0.165 | 27.8609 | 5.3953 | 5.7694
5392 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901010102 | F02-TRMN | INDUSTRIAL | DLMS Meter | 6.2993 | 6.049 | 0 | 6.2993 | 3.9734 | 3.9734
5393 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901010103 | F03-SATARAC | INDUSTRIAL | DLMS Meter | 5.1288 | 4.9485 | 0 | 5.1288 | 3.5159 | 6.8993
5394 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901010104 | F04-KALLALUGHATTA-AGRI | AGRI | DLMS Meter | 0.8456 | 0.74913 | 0 | 0.8456 | 11.4087 | 11.4297
5395 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901020301 | F05-GUNDENAHALLI-AGRI | AGRI | DLMS Meter | 1.1496 | 1.0081 | 0 | 1.1496 | 12.3104 | 12.3104
5396 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901020302 | F06-KSDL | AGRI | DLMS Meter | 1.306 | 1.1443 | 0 | 1.306 | 12.3797 | 17.8446
5397 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901020303 | F07-BERAGONDANAHALLI-AGRI | AGRI | DLMS Meter | 0.5008 | 0.44123 | 0 | 0.5008 | 11.8956 | 18.7636
5398 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901020304 | F08-THOTANAHALLI | RURAL MIXED LOAD | DLMS Meter | 2.0056 | 1.629 | 0.14 | 1.8656 | 12.6845 | 31.3957
5399 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901010105 | F09-RAMA-HI-POWER | INDUSTRIAL | DLMS Meter | 4.1434 | 3.9849 | 0 | 4.1434 | 3.8248 | 19.9456
5400 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901020101 | F11-KIADB | INDUSTRIAL | DLMS Meter | 5.1596 | 4.9028 | 0 | 5.1596 | 4.9775 | 10.587
5401 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901010107 | F12-BARAGOORU | AGRI | DLMS Meter | 1.0544 | 0.95326 | 0 | 1.0544 | 9.5925 | 11.8901
5402 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901020305 | F13-OBALAPURA | NJY | DLMS Meter | 1.7213 | 0.4516 | 1.212 | 0.5093 | 11.3289 | 25.0112
5403 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | TYAVANAGI_66 | 1310107902010101 | F01-NALKUDURE | AGRI | DLMS Meter | 1.1349 | 1.0213 | 0 | 1.1349 | 10.0091 | 10.0091
5404 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | TYAVANAGI_66 | 1310107902010102 | F02-DODDAGATTA IP | AGRI | DLMS Meter | 0.71266 | 0.64153 | 0 | 0.71266 | 9.9816 | 9.9816
5405 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | TYAVANAGI_66 | 1310107902010103 | F03-KATHALGERE | AGRI | DLMS Meter | 1.0478 | 0.94281 | 0 | 1.0478 | 10.0202 | 10.0202
5406 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | TYAVANAGI_66 | 1310107902010104 | F04-KARIGNUR | AGRI | DLMS Meter | 1.1055 | 0.99484 | 0 | 1.1055 | 10.013 | 10.013
5407 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | TYAVANAGI_66 | 1310107902010105 | F05-BELALAGERE | AGRI | DLMS Meter | 0.6634 | 0.59687 | 0 | 0.6634 | 10.0282 | 10.0282
5408 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | TYAVANAGI_66 | 1310107902010106 | F06-THYAVANAGI | NJY | DLMS Meter | 0.50704 | 0.39801 | 0.065 | 0.44204 | 9.9611 | 37.3334
5409 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | TYAVANAGI_66 | 1310107902010107 | F07-AREHALLI | NJY | DLMS Meter | 0.8361 | 0.62951 | 0.1375 | 0.6986 | 9.8903 | 23.0436
5410 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | TYAVANAGI_66 | 1310107902010108 | F08-NAVALIHAL | NJY | DLMS Meter | 1.0883 | 0.66059 | 0.3445 | 0.74378 | 11.1841 | 37.5639
5411 | CTAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | TYAVANAGI_66 | 1310107902010109 | F09-KABBALA NJY | NJY | DLMS Meter | 0.82669 | 0.60036 | 0.159 | 0.66769 | 10.0833 | 37.346
5412 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908010101 | F01-KARADIDURGA | AGRI | DLMS Meter | 0.86418 | 0.77743 | 0 | 0.86418 | 10.0382 | 10.0382
5413 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908010105 | F02-CHATNIHALLI NJY | NJY | DLMS Meter | 0.57444 | 0.3739 | 0.1515 | 0.42294 | 11.596 | 24.8854
5414 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908020305 | F03-PANIYAPURA INDUSTRIAL | INDUSTRIAL | DLMS Meter | 0.45764 | 0.39395 | 0.031 | 0.42664 | 7.6622 | 19.6591
5415 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908020306 | F04-U BAVINAHALLI | AGRI | DLMS Meter | 0.70112 | 0.55465 | 0.085 | 0.61612 | 9.9773 | 9.9773
5416 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908010102 | F05-CHIKKAMEGALAGERE NJY | NJY | DLMS Meter | 0.9498 | 0.66107 | 0.212 | 0.7378 | 10.3993 | 22.7313
5417 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908010103 | F06-UCHANGIDURGA NJY | NJY | DLMS Meter | 0.41 | 0.33429 | 0.0345 | 0.3755 | 10.9759 | 25.3407
5418 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908020301 | F07-HALLAMMANA THOPU | INDUSTRIAL | DLMS Meter | 0.978 | 0.9316 | 0 | 0.978 | 4.7447 | 15.0343
5419 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908020304 | F08-ANAJGERE | AGRI | DLMS Meter | 1.251 | 0.9192 | 0.23 | 1.021 | 9.9691 | 9.9691
5420 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908020307 | F09-GADIGUDAL NJY | NJY | DLMS Meter | 0.48092 | 0.3343 | 0.1075 | 0.37342 | 10.4752 | 30.9411
5421 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908020302 | F10-MADIHALLI | AGRI | DLMS Meter | 0.83742 | 0.78834 | 0 | 0.83742 | 5.8611 | 5.8611
5422 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | UCHCHANGIDURGA_66 | 1310303908020303 | F11-RAMAGHATTA | AGRI | DLMS Meter | 1.5504 | 1.4299 | 0 | 1.5504 | 7.7758 | 7.7758
5423 | CTAZ | TUMKUR | TUMKUR | GUBBI | UNGRA_110 | 1320106905010104 | F01-C.N PALYA | AGRI | DLMS Meter | 1.4957 | 0.93687 | 0.44564 | 1.0501 | 10.7813 | 10.7813
5424 | CTAZ | TUMKUR | TUMKUR | GUBBI | UNGRA_110 | 1320106905010105 | F02-KENCHANAHALLI | AGRI | DLMS Meter | 0.98834 | 0.88948 | 0 | 0.98834 | 10.0021 | 10.0021
5425 | CTAZ | TUMKUR | TUMKUR | GUBBI | UNGRA_110 | 1320106905010101 | F03-IDAGOOR | AGRI | DLMS Meter | 1.3279 | 1.1952 | 0 | 1.3279 | 9.9926 | 9.9926
5426 | CTAZ | TUMKUR | TUMKUR | GUBBI | UNGRA_110 | 1320106905010102 | F04-ANKALAKOPPA | AGRI | DLMS Meter | 0.90248 | 0.72966 | 0.069874 | 0.83261 | 12.3649 | 12.3649
5427 | CTAZ | TUMKUR | TUMKUR | GUBBI | UNGRA_110 | 1320106905010103 | F05-C S PURA-NJY | NJY | DLMS Meter | 1.3083 | 1.1706 | 0 | 1.3083 | 10.5249 | 63.5104
5428 | CTAZ | TUMKUR | TUMKUR | GUBBI | UNGRA_110 | 1320106905020303 | F06-HEMAVATHI-WATER-SUPPLY | WATER WORKS | DLMS Meter | 0.71431 | 0.62959 | 0 | 0.71431 | 11.8601 | 41.0307
5429 | CTAZ | TUMKUR | TUMKUR | GUBBI | UNGRA_110 | 1320106905010301 | F07-NARANAHALLY | AGRI | DLMS Meter | 1.5149 | 0.62436 | 0.80254 | 0.71232 | 12.3481 | 12.3481
5430 | CTAZ | TUMKUR | TUMKUR | GUBBI | UNGRA_110 | 1320106905020304 | F08-UNGRA | AGRI | DLMS Meter | 1.2833 | 1.1093 | 0 | 1.2833 | 13.5577 | 13.5577
5431 | CTAZ | TUMKUR | TUMKUR | GUBBI | UNGRA_110 | 1320106905020302 | F09-MANIKUPE | AGRI | DLMS Meter | 1.8148 | 1.5034 | 0.069542 | 1.7452 | 13.8549 | 13.8549
5432 | CTAZ | TUMKUR | TUMKUR | GUBBI | UNGRA_110 | 1320106905020301 | F10-GADDEHALLI | AGRI | DLMS Meter | 1.7184 | 1.033 | 0.53364 | 1.1847 | 12.8086 | 13.1467
5433 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | URAGAHALLI_66 | 1220101904010101 | F01-MG PALYA CRUSHER | INDUSTRIAL | DLMS Meter | 1.1732 | 1.1252 | 0 | 1.1732 | 4.0898 | 6.4918
5434 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | URAGAHALLI_66 | 1220101904010103 | F02-RAMANAHALLI | AGRI | DLMS Meter | 0.2916 | 0.27849 | 0 | 0.2916 | 4.4955 | 4.4955
5435 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | URAGAHALLI_66 | 1220101904010102 | F03-NAMDHARI | INDUSTRIAL | DLMS Meter | 1.0258 | 1.0502 | 0 | 1.0258 | -2.3786 | -2.3786
5436 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | URAGAHALLI_66 | 1220101904020101 | F05-ANNAHALLI | AGRI | DLMS Meter | 1.3476 | 1.2391 | 0 | 1.3476 | 8.0516 | 8.0516
5437 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | URAGAHALLI_66 | 1220101904020103 | F07-GOPAHALLI | NJY | DLMS Meter | 0.346 | 0.22822 | 0.099 | 0.247 | 7.6045 | 53.8971
5438 | BRAZ | RAMANAGAR | RAMANAGAR | BIDADI | URAGAHALLI_66 | 1220101904020102 | F08-H M DODDI | NJY | DLMS Meter | 0.5248 | 0.35086 | 0.141 | 0.3838 | 8.5826 | 41.9875
5439 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | URDIGERE_66 | 1320105904010101 | F01-SEETHAKALLU | AGRI | DLMS Meter | 0.7628 | 0.68655 | 0 | 0.7628 | 9.9966 | 9.9966
5440 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | URDIGERE_66 | 1320105904010102 | F02-MYDALA | NJY | DLMS Meter | 0.7334 | 0.55525 | 0.1377 | 0.5957 | 6.7903 | 27.7651
5441 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | URDIGERE_66 | 1320105904010103 | F03-D.DURGA | AGRI | DLMS Meter | 1.072 | 0.79006 | 0.19416 | 0.87784 | 9.9992 | 9.9992
5442 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | URDIGERE_66 | 1320105904010104 | F04-URDIGERE-RURAL | AGRI | DLMS Meter | 0.8436 | 0.62804 | 0.1458 | 0.6978 | 9.9976 | 9.9976
5443 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | URDIGERE_66 | 1320105904020301 | F05-KALENAHALLI | NJY | DLMS Meter | 0.6694 | 0.53572 | 0.0837 | 0.5857 | 8.533 | 41.786
5444 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | URDIGERE_66 | 1320105904020302 | F06-KURUVELU | AGRI | DLMS Meter | 1.0113 | 0.89207 | 0.0203 | 0.99105 | 9.9877 | 9.9877
5445 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | URDIGERE_66 | 1320105904020303 | F07-SATHAGHATTA | NJY | DLMS Meter | 0.8827 | 0.69949 | 0.12355 | 0.75915 | 7.8588 | 38.2744
5446 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | URDIGERE_66 | 1320105904010105 | F08-HALUGONDANAHALLI | AGRI | DLMS Meter | 1.149 | 0.80682 | 0.2523 | 0.8967 | 10.0236 | 10.0236
5447 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | VANDARAGUPPE_66 | 1220106902010101 | F01-KANNAMANGALA | AGRI | DLMS Meter | 0.93271 | 0.74936 | 0.1 | 0.83271 | 10.0093 | 10.0093
5448 | BRAZ | RAMANAGAR | RAMANAGAR | BEVOORU | VANDARAGUPPE_66 | 1220106902010102 | F02-KENGAL NJY | NJY | DLMS Meter | 0.468 | 0.22805 | 0.2175 | 0.2505 | 8.9632 | 17.9067
5449 | BRAZ | RAMANAGAR | RAMANAGAR | CHANNAPATNA URBAN | VANDARAGUPPE_66 | 1220106902010103 | F03-PTS | URBAN MIXED LOAD | DLMS Meter | 0.8716 | 0.77639 | 0.037 | 0.8346 | 6.9751 | 15.899
5450 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | VATADAHOSAHALLI_66 | 1230304902010101 | F02-D.PALYA | AGRI | DLMS Meter | 0.5651 | 0.50848 | 0 | 0.5651 | 10.02 | 10.02
5451 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | VATADAHOSAHALLI_66 | 1230304902010102 | F03-NAKKALAHALLI | AGRI | DLMS Meter | 0.9844 | 0.88596 | 0 | 0.9844 | 9.9999 | 9.9999
5452 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | VATADAHOSAHALLI_66 | 1230304902010103 | F04-VATADAHOSAHALLI | AGRI | DLMS Meter | 0.7732 | 0.66886 | 0.03 | 0.7432 | 10.0031 | 10.1436
5453 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | VATADAHOSAHALLI_66 | 1230304902020301 | F05-LAKKASANDRA | AGRI | DLMS Meter | 0.0102 | 0.009174 | 0 | 0.0102 | 10.0588 | 10.0588
5454 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | VATADAHOSAHALLI_66 | 1230304902020302 | F06-HULIKUNTE | AGRI | DLMS Meter | 0.5272 | 0.4743 | 0 | 0.5272 | 10.0349 | 10.0349
5455 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | VATADAHOSAHALLI_66 | 1230304902020303 | F08-JEELAKUNTE | AGRI | DLMS Meter | 1.1224 | 1.0102 | 0 | 1.1224 | 9.999 | 10.0313
5456 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | VATADAHOSAHALLI_66 | 1230304902010104 | F09-THOKALAHALLI NJY | NJY | DLMS Meter | 1.0436 | 0.91963 | 0.016 | 1.0276 | 10.5071 | 58.0445
5457 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | VATADAHOSAHALLI_66 | 1230304902010105 | F10-NARASAPURA(NJY) | NJY | DLMS Meter | 0.5549 | 0.50342 | 0 | 0.5549 | 9.2766 | 65.5391
5458 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903010101 | F01-IQF | INDUSTRIAL | DLMS Meter | 1.6018 | 1.5649 | 0 | 1.6018 | 2.3019 | 2.3019
5459 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903010102 | F02-TALAGUNDA | AGRI | DLMS Meter | 1.0364 | 0.93275 | 0 | 1.0364 | 10.0014 | 10.0014
5460 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903010103 | F04-SHETTIHALLI | AGRI | DLMS Meter | 1.7508 | 1.5652 | 0 | 1.7508 | 10.5997 | 10.5997
5461 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903010107 | F05-SHIVAM AUTO-TECH | INDUSTRIAL | DLMS Meter | 1.9478 | 1.9063 | 0 | 1.9478 | 2.13 | 2.13
5462 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903020301 | F06-NARASAPURA-INDUSTRIAL | NJY | DLMS Meter | 1.692 | 0.99966 | 0.6 | 1.092 | 8.4564 | 56.1803
5463 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903020302 | F07-KYALANUR-RURAL | AGRI | DLMS Meter | 1.1996 | 1.0724 | 0 | 1.1996 | 10.6005 | 10.6005
5464 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903020303 | F08-VEMAGAL | AGRI | DLMS Meter | 1.7178 | 1.5249 | 0 | 1.7178 | 11.2323 | 11.2323
5465 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903020304 | F10-BELAMARANAHALLI | AGRI | DLMS Meter | 2.3412 | 2.0926 | 0 | 2.3412 | 10.6173 | 10.6173
5466 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903020305 | F11-NJY-KALVAMANJALI | NJY | DLMS Meter | 1.4361 | 0.68605 | 0.66 | 0.7761 | 11.6029 | 76.07
5467 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903020306 | F12-NJY RAJAKALLAHALLI | NJY | DLMS Meter | 0.517 | 0.46289 | 0 | 0.517 | 10.4656 | 76.197
5468 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903020307 | F13-NJY KURABARAHALLI | NJY | DLMS Meter | 2.0017 | 1.7567 | 0 | 2.0017 | 12.2395 | 57.7738
5469 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903020308 | F14-GSK | INDUSTRIAL | DLMS Meter | 1.3668 | 1.4038 | 0 | 1.3668 | -2.7071 | -2.7071
5470 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903020310 | F15-TATA POWER | INDUSTRIAL | DLMS Meter | 0.2632 | 0.2715 | 0 | 0.2632 | -3.1535 | -3.1535
5471 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VEMAGAL_66 | 1230102903020309 | F16-KIADB | INDUSTRIAL | DLMS Meter | 3.16 | 3.0877 | 0 | 3.16 | 2.2884 | 4.9614
5472 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | VENKATAPURA_66 | 1320306904010107 | F09-JAJURAYANAHALLI NJY | NJY | DLMS Meter | 0.1984 | 0.18053 | 0 | 0.1984 | 9.0055 | 40.9066
5473 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | VENKATAPURA_66 | 1320306904020301 | F01-KRISHNAPURA | AGRI | DLMS Meter | 0.69878 | 0.63311 | 0 | 0.69878 | 9.398 | 9.398
5474 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | VENKATAPURA_66 | 1320306904020302 | F02-KANIVENAHALLI | AGRI | DLMS Meter | 0.70916 | 0.64064 | 0 | 0.70916 | 9.6623 | 9.6623
5475 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | VENKATAPURA_66 | 1320306904020303 | F03-MADURAYANAPALYA | AGRI | DLMS Meter | 0.45486 | 0.40929 | 0 | 0.45486 | 10.0187 | 10.0187
5476 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | VENKATAPURA_66 | 1320306904010102 | F04-GUMMAGATTA | AGRI | DLMS Meter | 0.73112 | 0.65793 | 0 | 0.73112 | 10.0107 | 10.0107
5477 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | VENKATAPURA_66 | 1320306904010103 | F05-DOMMATHAMARI | AGRI | DLMS Meter | 0.28468 | 0.25613 | 0 | 0.28468 | 10.0295 | 10.0295
5478 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | VENKATAPURA_66 | 1320306904010104 | F06-GOWDETY | AGRI | DLMS Meter | 0.4648 | 0.41827 | 0 | 0.4648 | 10.0116 | 10.0116
5479 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | VENKATAPURA_66 | 1320306904010101 | F07-VIRUPASAMUDRA | AGRI | DLMS Meter | 0.57182 | 0.51462 | 0 | 0.57182 | 10.003 | 12.0466
5480 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | VENKATAPURA_66 | 1320306904010106 | F08-NJY VENKATAPURA | NJY | DLMS Meter | 1.0682 | 0.94923 | 0 | 1.0682 | 11.1373 | 68.1167
5481 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | VENKATARAYANADODDI_66 | 1220303904010101 | F02-BISALAPPA | NJY | DLMS Meter | 0.94812 | 0.84924 | 0.01 | 0.93812 | 9.474 | 48.8824
5482 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | VENKATARAYANADODDI_66 | 1220303904010102 | F03-ATTIHALLI | AGRI | DLMS Meter | 0.96304 | 0.52897 | 0.375 | 0.58804 | 10.0451 | 10.0451
5483 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | VENKATARAYANADODDI_66 | 1220303904010103 | F04-VADERAHALLI | AGRI | DLMS Meter | 0.79544 | 0.71556 | 0 | 0.79544 | 10.0427 | 10.0427
5484 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | VENKATARAYANADODDI_66 | 1220303904020301 | F05-SOMEDYAPANAHALLI | AGRI | DLMS Meter | 0.86688 | 0.77377 | 0.007 | 0.85988 | 10.0137 | 10.0137
5485 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | VENKATARAYANADODDI_66 | 1220303904020302 | F06-THENGANAYAKANAHALLI | AGRI | DLMS Meter | 0.6835 | 0.55645 | 0.065 | 0.6185 | 10.0325 | 10.0325
5486 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | VENKATARAYANADODDI_66 | 1220303904020303 | F07-UJJANAHALLI | AGRI | DLMS Meter | 1.22 | 1.075 | 0.025 | 1.195 | 10.0403 | 10.0403
5487 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | VENKATARAYANADODDI_66 | 1220303904020304 | F08-MENASIGANAHALLI-NJY | NJY | DLMS Meter | 0.65644 | 0.51281 | 0.101 | 0.55544 | 7.6743 | 50.5375
5488 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | VENKATARAYANADODDI_66 | 1220303904020305 | F09- MURKANI NJY | NJY | DLMS Meter | 0.73456 | 0.31471 | 0.3968 | 0.33776 | 6.8255 | 59.213
5489 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | VENKATARAYANADODDI_66 | 1220303904010105 | F10-BANANTAMARAMMA | AGRI | DLMS Meter | 0.87986 | 0.72072 | 0.0788 | 0.80106 | 10.0297 | 10.0297
5490 | BRAZ | RAMANAGAR | KANAKAPUR | SATHANURU | VENKATARAYANADODDI_66 | 1220303904010106 | F11-APPU EXPRESS | LIFT IRRIGATION | DLMS Meter | 0.28361 | 0.042755 | 0.23891 | 0.044704 | 4.3598 | 4.3598
5491 | BRAZ | RAMANAGAR | MAGADI | MAGADI | VGDODDI_66 | 1210102903010105 | F01-AJJANAHALLI | NJY | DLMS Meter | 0.44742 | 0.25533 | 0.165 | 0.28242 | 9.5924 | 30.7437
5492 | BRAZ | RAMANAGAR | MAGADI | MAGADI | VGDODDI_66 | 1210102903010101 | F02-DABBAGULI | URBAN MIXED LOAD | DLMS Meter | 1.2047 | 0.81142 | 0.295 | 0.9097 | 10.8038 | 32.7822
5493 | BRAZ | RAMANAGAR | MAGADI | MAGADI | VGDODDI_66 | 1210102903010102 | F03-ATHIMEGERE | AGRI | DLMS Meter | 0.3119 | 0.28074 | 0 | 0.3119 | 9.991 | 9.991
5494 | BRAZ | RAMANAGAR | MAGADI | MAGADI | VGDODDI_66 | 1210102903010103 | F04-GAVINAGAMANGALA | AGRI | DLMS Meter | 0.58728 | 0.52845 | 0 | 0.58728 | 10.0179 | 10.0179
5495 | BRAZ | RAMANAGAR | MAGADI | MAGADI | VGDODDI_66 | 1210102903010106 | F05-GERAHALLI | AGRI | DLMS Meter | 0.48954 | 0.13803 | 0.336 | 0.15354 | 10.1036 | 10.1036
5496 | BRAZ | RAMANAGAR | MAGADI | MAGADI | VGDODDI_66 | 1210102903010107 | F06-ATTIMGERE NJY | NJY | DLMS Meter | 0.09968 | 0.068678 | 0.0232 | 0.07648 | 10.2018 | 25.5155
5497 | BMANZ | EAST | VIDHANASOUDHA | W5 | VICTORIAHOSPITAL_66 | 1130103902020101 | F01-MASJID-ROAD | URBAN MIXED LOAD | DLMS Meter | 1.1065 | 1.0441 | 0 | 1.1065 | 5.6339 | 7.4858
5498 | BMASZ | WEST | RR NAGAR | W2 | VICTORIAHOSPITAL_66 | 1130103902020105 | F03-RMU10 | URBAN MIXED LOAD | DLMS Meter | 1.0522 | 1.0054 | 0.005 | 1.0472 | 3.999 | 9.7378
5499 | BMANZ | EAST | VIDHANASOUDHA | W5 | VICTORIAHOSPITAL_66 | 1130103902020102 | F04-VICTORIA-HOSPITAL-LAUNDARY-+STN-AUX | HOSPITAL | DLMS Meter | 2.7143 | 2.6174 | 0.013355 | 2.7009 | 3.0933 | 3.0933
5500 | BMANZ | EAST | VIDHANASOUDHA | W5 | VICTORIAHOSPITAL_66 | 1130103902020103 | F05-A-M-ROAD/RMU-65 | URBAN MIXED LOAD | DLMS Meter | 3.0037 | 2.7916 | 0.033211 | 2.9705 | 6.0204 | 9.4109
5501 | BMASZ | WEST | RR NAGAR | W2 | VICTORIAHOSPITAL_66 | 1130103902020106 | F06-RMU-08 | URBAN MIXED LOAD | DLMS Meter | 2.1348 | 1.8113 | 0.1836 | 1.9512 | 7.1742 | 14.9668
5502 | BMANZ | EAST | VIDHANASOUDHA | W4 | VICTORIAHOSPITAL_66 | 1130103902020104 | F09-SCHOOL-COMPOUND-RMU | URBAN MIXED LOAD | DLMS Meter | 2.1958 | 2.0867 | 0 | 2.1958 | 4.9705 | 6.6143
5503 | BMANZ | EAST | VIDHANASOUDHA | W5 | VICTORIAHOSPITAL_66 | 1130103902010302 | F10-MILLIA-RMU | URBAN MIXED LOAD | DLMS Meter | 1.8758 | 1.7998 | 0 | 1.8758 | 4.0478 | 4.3919
5504 | BMANZ | EAST | VIDHANASOUDHA | W5 | VICTORIAHOSPITAL_66 | 1130103902010304 | F13-S-J-PARK-RMU64A | URBAN MIXED LOAD | DLMS Meter | 1.826 | 1.1665 | 0.57278 | 1.2532 | 6.9191 | 8.0669
5505 | BMASZ | SOUTH | JAYANAGAR | S2 | VICTORIAHOSPITAL_66 | 1130103902010105 | F15-RMU 82 MINERVA CIRCLE | URBAN MIXED LOAD | DLMS Meter | 2.0635 | 1.6445 | 0.35027 | 1.7133 | 4.0119 | 9.1731
5506 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | VIDHURASHWATHA_66 | 1230303901020101 | F01-RAMACHANDRAPURA | AGRI | DLMS Meter | 1.0066 | 0.90581 | 0 | 1.0066 | 10.0107 | 10.0107
5507 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | VIDHURASHWATHA_66 | 1230303901020102 | F02-MELYA | AGRI | DLMS Meter | 1.317 | 1.1852 | 0 | 1.317 | 10.0044 | 10.2951
5508 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | VIDHURASHWATHA_66 | 1230303901010103 | F04-H.NAGASANDRA | AGRI | DLMS Meter | 1.0028 | 0.90258 | 0 | 1.0028 | 9.9902 | 9.9902
5509 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | VIDHURASHWATHA_66 | 1230303901020301 | F05-KUDAMALAKUNTE | INDUSTRIAL | DLMS Meter | 4.5369 | 4.3673 | 0 | 4.5369 | 3.7369 | 3.7369
5510 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | VIDHURASHWATHA_66 | 1230303901020302 | F06-PRECOT | INDUSTRIAL | DLMS Meter | 4.2988 | 4.1209 | 0 | 4.2988 | 4.1386 | 5.6574
5511 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | VIDHURASHWATHA_66 | 1230303901020303 | F08-HUNASENAHALLI | AGRI | DLMS Meter | 0.84672 | 0.76187 | 0 | 0.84672 | 10.0207 | 10.0207
5512 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | VIDHURASHWATHA_66 | 1230303901010107 | F10-A-ONE STEEL1 | INDUSTRIAL | DLMS Meter | 12.396 | 11.8824 | 0 | 12.396 | 4.1433 | 4.1433
5513 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | VIDHURASHWATHA_66 | 1230303901020104 | F11-NJY-JAGAREDDYHALLY | NJY | DLMS Meter | 0.46744 | 0.40306 | 0 | 0.46744 | 13.7735 | 58.6167
5514 | BRAZ | KOLAR | CHIKKABALLAPURA | GOWRIBIDANUR | VIDHURASHWATHA_66 | 1230303901020304 | F12-NJY-VIDHURASWATHA | NJY | DLMS Meter | 1.4955 | 1.2993 | 0 | 1.4955 | 13.1205 | 51.4497
5515 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901010107 | F01-EMBASSY | DOMESTIC | DLMS Meter | 0.79166 | 0.76796 | 0 | 0.79166 | 2.9937 | 3.4352
5516 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901010101 | F03-BAGALURU | DOMESTIC | DLMS Meter | 4.7988 | 3.9627 | 0.3 | 4.4988 | 11.9173 | 11.9173
5517 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901010103 | F04-HOSAHALLI | DOMESTIC | DLMS Meter | 3.8708 | 3.4659 | 0 | 3.8708 | 10.4611 | 17.1064
5518 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901010104 | F05-DWARAKANAGAR | DOMESTIC | DLMS Meter | 3.7005 | 3.0034 | 0.32 | 3.3805 | 11.1533 | 11.1533
5519 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901020101 | F07-LOCAL | DOMESTIC | DLMS Meter | 4.9514 | 4.4707 | 0 | 4.9514 | 9.709 | 10.6189
5520 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901020301 | F08-BETTAHALASUR | DOMESTIC | DLMS Meter | 5.6312 | 5.0185 | 0 | 5.6312 | 10.8798 | 14.3692
5521 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901020102 | F09-M-V-SOLAR | INDUSTRIAL | DLMS Meter | 1.1127 | 1.1165 | 0 | 1.1127 | -0.34195 | -0.34195
5522 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901020302 | F10-THE-RETRET | DOMESTIC | DLMS Meter | 1.2648 | 1.1028 | 0.05 | 1.2148 | 9.2252 | 20.3601
5523 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901020303 | F11-UTHOPIA | DOMESTIC | DLMS Meter | 3.1976 | 2.3494 | 0.505 | 2.6926 | 12.7459 | 13.4787
5524 | BMANZ | NORTH | HEBBAL | C7 | VIDYANAGAR_66 | 1210202901010109 | F12-IAF | DEFENSE ESTABLISHMENT | DLMS Meter | 1.4545 | 1.0075 | 0.3942 | 1.0603 | 4.9735 | 4.9735
5525 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901010105 | F13-AWHO | DOMESTIC | DLMS Meter | 0.31734 | 0.29775 | 0 | 0.31734 | 6.1716 | 8.1623
5526 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | VIDYANAGAR_66 | 1210202901010106 | F14-UTHANAHALLI | DOMESTIC | DLMS Meter | 2.9734 | 2.5059 | 0.1 | 2.8734 | 12.789 | 19.4236
5527 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | VIJAPURA_66 | 1310202906010101 | F01-KALKUNTE | AGRI | DLMS Meter | 0.97688 | 0.89259 | 0 | 0.97688 | 8.6279 | 8.6279
5528 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | VIJAPURA_66 | 1310202906010102 | F02-BALIGHATTE | AGRI | DLMS Meter | 0.9556 | 0.23744 | 0.69571 | 0.25989 | 8.6364 | 8.6364
5529 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | VIJAPURA_66 | 1310202906010103 | F03-LAKSHMISAGARA | AGRI | DLMS Meter | 0.54576 | 0.49112 | 0 | 0.54576 | 10.0123 | 10.0123
5530 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | VIJAPURA_66 | 1310202906010104 | F04-VIJAPURA NJY | NJY | DLMS Meter | 0.2686 | 0.14665 | 0.10058 | 0.16802 | 12.719 | 29.5068
5531 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | VIJAPURA_66 | 1310202906010105 | F05-MARADI ANJANEYA | AGRI | DLMS Meter | 0.99652 | 0.87791 | 0 | 0.99652 | 11.9032 | 11.9032
5532 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA RURAL | VIJAPURA_66 | 1310202906010106 | F06-CHIKKALAGHATTA | AGRI | DLMS Meter | 1.0371 | 0.894 | 0 | 1.0371 | 13.7976 | 13.7976
5533 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904010101 | F01-LOCAL VIJAYAPURA | DOMESTIC | DLMS Meter | 3.4981 | 2.6948 | 0.38534 | 3.1127 | 13.4254 | 13.4254
5534 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904010102 | F02-BIJJAVARA | AGRI | DLMS Meter | 1.3132 | 1.1817 | 0 | 1.3132 | 10.0091 | 10.0091
5535 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904010103 | F03-NARAYANAPURA | AGRI | DLMS Meter | 0.81312 | 0.61937 | 0.10339 | 0.70973 | 12.7321 | 13.8005
5536 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904020301 | F05-DAIRY | URBAN MIXED LOAD | DLMS Meter | 1.4774 | 1.3445 | 0 | 1.4774 | 8.9977 | 8.9977
5537 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904010104 | F06-VARADENAHALLI | AGRI | DLMS Meter | 0.92954 | 0.83615 | 0 | 0.92954 | 10.0471 | 10.0879
5538 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904020302 | F07-DINNUR | AGRI | DLMS Meter | 0.30124 | 0.26229 | 0.009678 | 0.29156 | 10.0404 | 10.0404
5539 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904020303 | F08-BEEDIGANAHALLI | AGRI | DLMS Meter | 1.039 | 0.94309 | 0 | 1.039 | 9.2325 | 9.457
5540 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904010105 | F09-WATER-SUPPLY | WATER WORKS | DLMS Meter | 0.038 | 0.03795 | 0 | 0.038 | 0.13158 | 0.13158
5541 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904020304 | F10-JANGAMAKOTE | URBAN MIXED LOAD | DLMS Meter | 1.1631 | 0.95718 | 0.10639 | 1.0567 | 9.4157 | 9.4157
5542 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904020305 | F11-MUDUGURKI | AGRI | DLMS Meter | 1.2291 | 1.0874 | 0 | 1.2291 | 11.5309 | 17.1148
5543 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904010106 | F12-NJY-SAIBABA | NJY | DLMS Meter | 2.5233 | 2.2077 | 0.13109 | 2.3922 | 7.7114 | 55.187
5544 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904020306 | F13-NJY-PAPANAHALLI | NJY | DLMS Meter | 1.831 | 1.6807 | 0 | 1.831 | 8.2088 | 8.2088
5545 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904010107 | F14-NJY-DHARMAPURA | NJY | DLMS Meter | 0.77858 | 0.71235 | 0.027612 | 0.75097 | 5.1415 | 32.1418
5546 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904020307 | F16-VENKATAGIRI KOTE NJY | NJY | DLMS Meter | 1.4303 | 1.3473 | 0 | 1.4303 | 5.8077 | 36.3634
5547 | BRAZ | BANGALORE RURAL | HOSAKOTE | DEVANAHALLI | VIJAYAPURA_66 | 1210202904020308 | F17-GONURU | AGRI | DLMS Meter | 0.5334 | 0.47985 | 0 | 0.5334 | 10.0403 | 10.0496
5548 | BMASZ | WEST | RAJAJINAGAR | N2 | VIJAYNAGAR_66 | 1140102902020301 | F01-VIJAYANAGAR,-HOSAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.4859 | 2.2493 | 0.094352 | 2.3916 | 5.9513 | 8.9998
5549 | BMASZ | WEST | RAJAJINAGAR | N2 | VIJAYNAGAR_66 | 1140102902020302 | F02-GOVINDARAJANAGAR | URBAN MIXED LOAD | DLMS Meter | 2.1061 | 1.9175 | 0.060357 | 2.0458 | 6.2716 | 10.2003
5550 | BMASZ | WEST | RAJAJINAGAR | N8 | VIJAYNAGAR_66 | 1140102902020303 | F03-FNAGARBHAVI | URBAN MIXED LOAD | DLMS Meter | 5.4811 | 5.2433 | 0 | 5.4811 | 4.339 | 11.7567
5551 | BMASZ | WEST | RAJAJINAGAR | N6 | VIJAYNAGAR_66 | 1140102902020304 | F04-SHIVA-FARM-INDUSTRIAL-AREA | INDUSTRIAL | DLMS Meter | 5.8923 | 5.5269 | 0.091556 | 5.8008 | 4.7218 | 9.4504
5552 | BMASZ | WEST | RAJAJINAGAR | N3 | VIJAYNAGAR_66 | 1140102902020305 | F05-BASAVESHWARA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.1824 | 3.0538 | 0 | 3.1824 | 4.0431 | 8.0619
5553 | BMASZ | WEST | RAJAJINAGAR | N3 | VIJAYNAGAR_66 | 1140102902010101 | F06-F--BEML-LAYOUT-KAMALANAGAR | URBAN MIXED LOAD | DLMS Meter | 3.1207 | 2.9792 | 0 | 3.1207 | 4.5355 | 9.3532
5554 | BMASZ | WEST | RAJAJINAGAR | N6 | VIJAYNAGAR_66 | 1140102902010102 | F07-FKAMAKSHIPALYA-FEEDER | URBAN MIXED LOAD | DLMS Meter | 5.0107 | 4.7767 | 0 | 5.0107 | 4.6694 | 11.1084
5555 | BMASZ | WEST | RAJAJINAGAR | N3 | VIJAYNAGAR_66 | 1140102902010104 | F09-A-D-HALLI | URBAN MIXED LOAD | DLMS Meter | 3.5945 | 3.3329 | 0 | 3.5945 | 7.2757 | 12.9303
5556 | BMASZ | WEST | RAJAJINAGAR | N10 | VIJAYNAGAR_66 | 1140102902020306 | F10-KAMAKSHIPALYA-INDUSTRIAL-ESTATE | INDUSTRIAL | DLMS Meter | 4.0017 | 3.8469 | 0 | 4.0017 | 3.8681 | 6.0474
5557 | BMASZ | WEST | RAJAJINAGAR | N10 | VIJAYNAGAR_66 | 1140102902010105 | F11-SELVEM-INDUSTRIAL-ESTATE | INDUSTRIAL | DLMS Meter | 3.5152 | 3.2959 | 0.057458 | 3.4577 | 4.6806 | 9.1028
5558 | BMASZ | WEST | RAJAJINAGAR | N2 | VIJAYNAGAR_66 | 1140102902010106 | F12-VIJAYANAGAR-ND-STAGE | URBAN MIXED LOAD | DLMS Meter | 2.1816 | 2.0651 | 0 | 2.1816 | 5.3385 | 8.1718
5559 | BMASZ | WEST | RAJAJINAGAR | N3 | VIJAYNAGAR_66 | 1140102902010107 | F13-NGOS-COLONY-KAMALANAGAR | URBAN MIXED LOAD | DLMS Meter | 3.1113 | 2.8935 | 0 | 3.1113 | 7.0024 | 13.4816
5560 | BMASZ | WEST | RAJAJINAGAR | N8 | VIJAYNAGAR_66 | 1140102902020307 | F14-BINNY-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.4351 | 3.2715 | 0 | 3.4351 | 4.7633 | 12.5065
5561 | BMASZ | WEST | RAJAJINAGAR | N10 | VIJAYNAGAR_66 | 1140102902010108 | F15-PETECHANNAPPA-IND.ESTATE | URBAN MIXED LOAD | DLMS Meter | 4.2151 | 4.0633 | 0 | 4.2151 | 3.6002 | 5.37
5562 | BMASZ | WEST | RAJAJINAGAR | N10 | VIJAYNAGAR_66 | 1140102902020308 | F16-KAVERIPURA | URBAN MIXED LOAD | DLMS Meter | 5.5868 | 5.21 | 0.13865 | 5.4482 | 4.3708 | 15.9943
5563 | BMASZ | WEST | RAJAJINAGAR | N6 | VIJAYNAGAR_66 | 1140102902010109 | F17-PREMNAGAR | DOMESTIC | DLMS Meter | 3.1935 | 3.0807 | 0 | 3.1935 | 3.5351 | 5.3708
5564 | BMASZ | SOUTH | KORAMANGALA | S7 | VIKASTECHPARK_220 | 1110203910010102 | F05-CISSCO | INDUSTRIAL | DLMS Meter | 9.4625 | 9.572 | 0 | 9.4625 | -1.1571 | -1.1571
5565 | BMASZ | SOUTH | KORAMANGALA | S7 | VIKASTECHPARK_220 | 1110203910010101 | F07-WELLS FARGO | INDUSTRIAL | DLMS Meter | 2.6805 | 2.725 | 0 | 2.6805 | -1.6593 | -1.6593
5566 | BMASZ | SOUTH | KORAMANGALA | S7 | VIKASTECHPARK_220 | 1110203910020105 | F10-I LIFE APARTMENT | URBAN MIXED LOAD | DLMS Meter | 1.1526 | 0.82494 | 0.295 | 0.85759 | 3.807 | 9.8149
5567 | BMASZ | SOUTH | KORAMANGALA | S7 | VIKASTECHPARK_220 | 1110203910020106 | F11-KB HALLI BRIDGE | URBAN MIXED LOAD | DLMS Meter | 1.9203 | 0.78595 | 1.115 | 0.80534 | 2.4073 | 4.029
5568 | BMASZ | SOUTH | KORAMANGALA | S7 | VIKASTECHPARK_220 | 1110203910020101 | F12-GROUP-1 | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5569 | BMASZ | SOUTH | KORAMANGALA | S7 | VIKASTECHPARK_220 | 1110203910020102 | F13-7B | COMMERCIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5570 | BMASZ | SOUTH | KORAMANGALA | S7 | VIKASTECHPARK_220 | 1110203910020103 | F14-GROUP-2 | COMMERCIAL | DLMS Meter | 0 | 0 | 0.0013873 | -0.0013873 | 0 | #DIV/0!
5571 | BMASZ | SOUTH | KORAMANGALA | S7 | VIKASTECHPARK_220 | 1110203910020104 | F15-GROUP-3 | COMMERCIAL | DLMS Meter | 1.2656 | 0.30653 | 0.955 | 0.31063 | 1.3197 | 2.8048
5572 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | VISHWESHWARAPURA_66 | 1310402909010101 | F01-V V PURA | AGRI | DLMS Meter | 0.9538 | 0.8478 | 0 | 0.9538 | 11.1134 | 11.1134
5573 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | VISHWESHWARAPURA_66 | 1310402909010102 | F02-RANGAVANAHALLY NJY | NJY | DLMS Meter | 0.3868 | 0.33142 | 0.0069 | 0.3799 | 12.7623 | 52.0689
5574 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | VISHWESHWARAPURA_66 | 1310402909010104 | F03-GOWDRAHATTI | AGRI | DLMS Meter | 0.5458 | 0.48878 | 0 | 0.5458 | 10.4472 | 10.4472
5575 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | VISHWESHWARAPURA_66 | 1310402909010103 | F04-CHIKKA ULLARTHI | AGRI | DLMS Meter | 0.1532 | 0.13792 | 0 | 0.1532 | 9.9739 | 9.9739
5576 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VOKKALERI_66 | 1230102905020301 | F01-PARSHAGANAHALLY | AGRI | DLMS Meter | 1.3314 | 1.1987 | 0 | 1.3314 | 9.9698 | 9.9698
5577 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VOKKALERI_66 | 1230102905010101 | F02-KUNTANA-HALLI | AGRI | DLMS Meter | 1.3294 | 0.93544 | 0.29 | 1.0394 | 10.002 | 10.2072
5578 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VOKKALERI_66 | 1230102905020302 | F03-JANGALAHALLI | AGRI | DLMS Meter | 1.998 | 1.4474 | 0.39 | 1.608 | 9.9856 | 9.9856
5579 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VOKKALERI_66 | 1230102905010102 | F04-VOKKALERI | AGRI | DLMS Meter | 2.2624 | 1.474 | 0.62 | 1.6424 | 10.2534 | 10.2534
5580 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VOKKALERI_66 | 1230102905020303 | F05-MANGASANDRA | AGRI | DLMS Meter | 1.0978 | 0.98528 | 0 | 1.0978 | 10.2497 | 10.2497
5581 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VOKKALERI_66 | 1230102905020304 | F06-NARASAPURA | AGRI | DLMS Meter | 1.8904 | 1.6938 | 0 | 1.8904 | 10.4008 | 11.4406
5582 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VOKKALERI_66 | 1230102905020305 | F07-NJY-CHINNAPURA | NJY | DLMS Meter | 1.2727 | 1.1194 | 0 | 1.2727 | 12.0449 | 76.9199
5583 | BRAZ | KOLAR | KOLAR | KOLAR RURAL | VOKKALERI_66 | 1230102905010103 | F08-NJY-GANGAPURA | NJY | DLMS Meter | 1.8516 | 1.3417 | 0.31 | 1.5416 | 12.967 | 63.2711
5584 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | VOLVO_66 | 1210201905020301 | F01-TAVAREKERE | AGRI | DLMS Meter | 1.5928 | 1.4333 | 0 | 1.5928 | 10.0159 | 10.0914
5585 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | VOLVO_66 | 1210201905020302 | F02-MUGABALA | AGRI | DLMS Meter | 0.96368 | 0.86722 | 0 | 0.96368 | 10.0092 | 10.0092
5586 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | VOLVO_66 | 1210201905020303 | F03-YELACHAHALLI | AGRI | DLMS Meter | 1.7761 | 1.5885 | 0 | 1.7761 | 10.5633 | 14.4611
5587 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | VOLVO_66 | 1210201905020304 | F04-MYLAPURA | NJY | DLMS Meter | 2.2554 | 1.3272 | 0.81336 | 1.442 | 7.9639 | 46.717
5588 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | VOLVO_66 | 1210201905020305 | F05-INDUSTRIAL | INDUSTRIAL | DLMS Meter | 0.95496 | 0.58584 | 0.29135 | 0.66361 | 11.7191 | 42.3374
5589 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | VOLVO_66 | 1210201905010101 | F06-GOOGUTTAHALLI | AGRI | DLMS Meter | 1.0404 | 0.93599 | 0 | 1.0404 | 10.039 | 12.267
5590 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | VOLVO_66 | 1210201905010102 | F07-VOLVO | INDUSTRIAL | DLMS Meter | 1.1485 | 1.1444 | 0 | 1.1485 | 0.35743 | 0.35743
5591 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | VOLVO_66 | 1210201905010103 | F08-MEDRICH | INDUSTRIAL | DLMS Meter | 4.5482 | 4.526 | 0 | 4.5482 | 0.48859 | 0.48859
5592 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | VOLVO_66 | 1210201905010301 | F10-GANGAPURA | NJY | DLMS Meter | 1.5129 | 1.4242 | 0 | 1.5129 | 5.8636 | 24.2398
5593 | BMASZ | WEST | RR NAGAR | W6 | VRISHABAVATHY_66 | 1140203901020202 | F02-JOHN-DISTILLERY | URBAN MIXED LOAD | DLMS Meter | 3.6556 | 3.4004 | 0 | 3.6556 | 6.9828 | 11.5436
5594 | BMASZ | WEST | RR NAGAR | W6 | VRISHABAVATHY_66 | 1140203901020203 | F03-THE-CLUB | URBAN MIXED LOAD | DLMS Meter | 1.7961 | 1.6766 | 0 | 1.7961 | 6.6554 | 11.9799
5595 | BMASZ | WEST | RR NAGAR | W6 | VRISHABAVATHY_66 | 1140203901020205 | F05-BWSSB | URBAN MIXED LOAD | DLMS Meter | 4.9375 | 4.6152 | 0 | 4.9375 | 6.5278 | 18.0288
5596 | BMASZ | WEST | RR NAGAR | W6 | VRISHABAVATHY_66 | 1140203901020206 | F08-SPORTS-AUTHORITY-OF-INDIA | URBAN MIXED LOAD | DLMS Meter | 1.7058 | 1.0751 | 0.52722 | 1.1786 | 8.7829 | 8.7829
5597 | BMASZ | WEST | RR NAGAR | W7 | VRISHABAVATHY_66 | 1140203901020101 | F11-MYSORE-ROAD | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5598 | BMASZ | WEST | KENGERI | K1 | VRISHABAVATHY_66 | 1140203901020209 | F12-RV-COLLAGE | URBAN MIXED LOAD | DLMS Meter | 1.7425 | 1.6604 | 0.010124 | 1.7324 | 4.1535 | 4.1535
5599 | BMASZ | WEST | KENGERI | K1 | VRISHABAVATHY_66 | 1140203901010105 | F14-BDA-1 KAILASA | DOMESTIC | DLMS Meter | 1.1033 | 1.0672 | 0 | 1.1033 | 3.2702 | 6.7857
5600 | BMASZ | WEST | KENGERI | K1 | VRISHABAVATHY_66 | 1140203901020303 | F15-BDA-2 GANGA | URBAN MIXED LOAD | DLMS Meter | 5.5466 | 4.2126 | 1.0911 | 4.4555 | 5.4515 | 20.8311
5601 | BMASZ | WEST | RR NAGAR | W6 | VRISHABAVATHY_66 | 1140203901010104 | F16-SALARPURIA DIVINITY | URBAN MIXED LOAD | DLMS Meter | 1.7133 | 0.72114 | 0.92702 | 0.78631 | 8.2871 | 34.8712
5602 | BMASZ | WEST | RR NAGAR | W6 | VRISHABAVATHY_66 | #N/A | F17-BWSSB 2 | #N/A | DLMS Meter | 3.0593 | 3.0086 | 0 | 3.0593 | 1.6568 | 1.6577
5603 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902010101 | F01-GARRISON-ENGG | URBAN MIXED LOAD | DLMS Meter | 2.308 | 1.8007 | 0.365 | 1.943 | 7.326 | 11.111
5604 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902010102 | F02-AYYAPPA-RMU | URBAN MIXED LOAD | DLMS Meter | 1.806 | 1.591 | 0.105 | 1.701 | 6.471 | 19.6577
5605 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902010103 | F03-KSRTC | COMMERCIAL | DLMS Meter | 0.7175 | 0.69029 | 0 | 0.7175 | 3.7927 | 3.7927
5606 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902010104 | F04 -G.L.APARTMENTS | URBAN MIXED LOAD | DLMS Meter | 0.3317 | 0.27314 | 0.052 | 0.2797 | 2.3461 | 2.3825
5607 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902010105 | F05-WELCAST-RMU | INDUSTRIAL | DLMS Meter | 2.3171 | 2.2846 | 0.0072 | 2.3099 | 1.0947 | 9.2435
5608 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902020301 | F07-RAVI-KIRLOSKAR | INDUSTRIAL | DLMS Meter | 0.95745 | 0.81774 | 0.1322 | 0.82525 | 0.91028 | 71.1728
5609 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902020302 | F08-BFW | INDUSTRIAL | DLMS Meter | 2.0499 | 1.8835 | 0.115 | 1.9349 | 2.6574 | 2.6574
5610 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902020303 | F09-TATA-TEA | INDUSTRIAL | DLMS Meter | 1.9193 | 1.8041 | 0.02 | 1.8993 | 5.01 | 25.3379
5611 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902020304 | F10-ITC | INDUSTRIAL | DLMS Meter | 1.4711 | 1.4533 | 0 | 1.4711 | 1.2078 | 1.2078
5612 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902020401 | F11-WELCAST-(ADDITIONAL) | INDUSTRIAL | DLMS Meter | 3.8862 | 3.8552 | 0 | 3.8862 | 0.8 | 0.8
5613 | BMANZ | NORTH | PEENYA | N5 | WELCASTSTEEL_66 | 1120102902010106 | F12-ITC-RMU-(ADDITIONAL) | INDUSTRIAL | DLMS Meter | 2.7954 | 2.7031 | 0.0475 | 2.7479 | 1.6314 | 1.6314
5614 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | WIDIA_66 | 1120102906010301 | F03-BIEC | URBAN MIXED LOAD | DLMS Meter | 0.3294 | 0.29264 | 0.0237 | 0.3057 | 4.2731 | 16.8347
5615 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | WIDIA_66 | 1120102906010304 | F08-ANCHEPALYA | URBAN MIXED LOAD | DLMS Meter | 0.59165 | 0.59065 | 0 | 0.59165 | 0.16986 | 4.8386
5616 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | WIDIA_66 | #N/A | F10-STN AXILLARY | #N/A | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5617 | BRAZ | BANGALORE RURAL | NELAMANGALA | NELAMANGALA | WIDIA_66 | 1120102906010102 | F11-JINDAL | INDUSTRIAL | DLMS Meter | 37.3222 | 6.5511 | 30.662 | 6.6602 | 1.6386 | 1.6386
5618 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | YADAVANI_66 | 1320109906010102 | F02-YADAVANI NJY | NJY | DLMS Meter | 0.69852 | 0.64334 | 0 | 0.69852 | 7.899 | 77.6059
5619 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | YADAVANI_66 | 1320109906010103 | F03-UNGRA | AGRI | DLMS Meter | 0.92356 | 0.83122 | 0 | 0.92356 | 9.9977 | 9.9977
5620 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | YADAVANI_66 | 1320109906010104 | F04-ARJUNAHALLI | AGRI | DLMS Meter | 0.41252 | 0.37131 | 0 | 0.41252 | 9.9898 | 9.9898
5621 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | YADAVANI_66 | 1320109906020301 | F06-PALLERAYANAHALLI | AGRI | DLMS Meter | 0.3844 | 0.33829 | 0 | 0.3844 | 11.9961 | 11.9961
5622 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | YADAVANI_66 | 1320109906020304 | F07-BENAVARA | AGRI | DLMS Meter | 1.038 | 0.93446 | 0 | 1.038 | 9.9748 | 9.9748
5623 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | YADAVANI_66 | 1320109906020302 | F08-ANCHIPURA | AGRI | DLMS Meter | 0.9382 | 0.8571 | 0 | 0.9382 | 8.6439 | 8.6439
5624 | CTAZ | TUMKUR | KUNIGAL | HULIYURDURGA | YADAVANI_66 | 1320109906020303 | F09-KUMBARAPALYA | AGRI | DLMS Meter | 0.8716 | 0.77623 | 0 | 0.8716 | 10.9416 | 10.9416
5625 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901010101 | F01-CHITANAHALLI | AGRI | DLMS Meter | 0.67972 | 0.61182 | 0 | 0.67972 | 9.9894 | 9.9894
5626 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901010102 | F03-KAKKARAGOLLA | AGRI | DLMS Meter | 0.90032 | 0.81032 | 0 | 0.90032 | 9.9969 | 9.9969
5627 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901010103 | F04-AVARAGOLLA | AGRI | DLMS Meter | 0.74284 | 0.60109 | 0.075 | 0.66784 | 9.9948 | 9.9948
5628 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901020301 | F05-DEVARAHATTY | AGRI | DLMS Meter | 0.79188 | 0.71258 | 0 | 0.79188 | 10.0143 | 10.0143
5629 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | YARAGUNTA_66 | 1310103901020302 | F06-SHIVALI | URBAN MIXED LOAD | DLMS Meter | 4.3149 | 3.7569 | 0.16529 | 4.1496 | 9.4634 | 18.4258
5630 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | YARAGUNTA_66 | 1310103901020303 | F08-VIJAYNAGARA | URBAN MIXED LOAD | DLMS Meter | 2.4045 | 2.1548 | 0.051507 | 2.353 | 8.4231 | 15.5771
5631 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | YARAGUNTA_66 | 1310103901010104 | F09-SHANESHWARA | URBAN MIXED LOAD | DLMS Meter | 2.335 | 2.2332 | 0 | 2.335 | 4.3595 | 14.1258
5632 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901020304 | F10-WATERWORKS | WATER WORKS | DLMS Meter | 1.7455 | 1.6928 | 0 | 1.7455 | 3.0214 | 36.4998
5633 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901020501 | F11-BATHI | AGRI | DLMS Meter | 0.56714 | 0.51058 | 0 | 0.56714 | 9.9732 | 9.9732
5634 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901020502 | F12-SATYANARAYANA | AGRI | DLMS Meter | 0.66828 | 0.6013 | 0 | 0.66828 | 10.0235 | 10.0235
5635 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-1 | YARAGUNTA_66 | 1310103901020503 | F13-KARURINDUSTRIAL | INDUSTRIAL | DLMS Meter | 0.84532 | 0.80122 | 0.017 | 0.82832 | 3.2714 | 6.0446
5636 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901010701 | F14-YARAGUNTA | DOMESTIC | DLMS Meter | 0.61068 | 0.52375 | 0.012 | 0.59868 | 12.515 | 17.3949
5637 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | YARAGUNTA_66 | 1310103901010301 | F15-COMMERCIAL | URBAN MIXED LOAD | DLMS Meter | 4.5165 | 2.0976 | 2.2055 | 2.311 | 9.2352 | 16.8149
5638 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUBDIVISION-2 | YARAGUNTA_66 | 1310103901010702 | F16-SJM | URBAN MIXED LOAD | DLMS Meter | 0.517 | 0.51105 | 0 | 0.517 | 1.1503 | 8.4488
5639 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901010703 | F17-AMRUTNAGARA NJY | NJY | DLMS Meter | 1.2152 | 1.0457 | 0 | 1.2152 | 13.9503 | 23.9939
5640 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901020305 | F18-NEELANAHALLI NJY | NJY | DLMS Meter | 1.6573 | 1.3709 | 0.098 | 1.5593 | 12.0862 | 22.4722
5641 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | YARAGUNTA_66 | 1310103901010705 | F20-KODIHALLI | NJY | DLMS Meter | 0.7075 | 0.55292 | 0.074 | 0.6335 | 12.7205 | 46.8054
5642 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | YEDIYUR_66 | 1320109904010101 | F01-SIIDLINGESHWAR | URBAN MIXED LOAD | DLMS Meter | 1.7483 | 1.5814 | 0 | 1.7483 | 9.5439 | 18.9199
5643 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | YEDIYUR_66 | 1320109904010102 | F02-HATTILAKKAMMA | AGRI | DLMS Meter | 0.93074 | 0.82319 | 0 | 0.93074 | 11.5551 | 11.5551
5644 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | YEDIYUR_66 | 1320109904010108 | F03-CHIKKAMADHURE | AGRI | DLMS Meter | 0.06154 | 0.027479 | 0.031 | 0.03054 | 10.0229 | 10.0229
5645 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | YEDIYUR_66 | 1320109904010106 | F04-MANAVALLI | AGRI | DLMS Meter | 0.044934 | 0.040386 | 0 | 0.044934 | 10.122 | 10.122
5646 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | YEDIYUR_66 | 1320109904010107 | F05-KACHONAHALLI | AGRI | DLMS Meter | 0.19566 | 0.17603 | 0 | 0.19566 | 10.0328 | 10.0328
5647 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | YEDIYUR_66 | 1320109904020303 | F06-NAGASANDRA | AGRI | DLMS Meter | 0.69958 | 0.61276 | 0 | 0.69958 | 12.4104 | 12.4104
5648 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | YEDIYUR_66 | 1320109904020304 | F07-CT-PALYA | AGRI | DLMS Meter | 0.8792 | 0.77199 | 0 | 0.8792 | 12.1935 | 12.1935
5649 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | YEDIYUR_66 | 1320109904020305 | F08-TIPPUR | AGRI | DLMS Meter | 0.63092 | 0.55438 | 0 | 0.63092 | 12.1313 | 12.1313
5650 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | YEDIYUR_66 | 1320109904020301 | F09-NJY 1-HEMAVATHI | NJY | DLMS Meter | 1.274 | 1.1678 | 0 | 1.274 | 8.3336 | 30.8109
5651 | CTAZ | TUMKUR | KUNIGAL | YEDIYUR | YEDIYUR_66 | 1320109904020302 | F10-NJY 2-DODDAMADHURE | NJY | DLMS Meter | 0.3469 | 0.30696 | 0 | 0.3469 | 11.5143 | 11.5143
5652 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | YEDUMADU_66 | 1220304904020301 | F02-YADAMADU-NJY-F | NJY | DLMS Meter | 0.3887 | 0.30899 | 0.048 | 0.3407 | 9.3085 | 38.4393
5653 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | YEDUMADU_66 | 1220304904010101 | F03-SONA-INDUTRIAL-F | URBAN MIXED LOAD | DLMS Meter | 1.3528 | 1.1868 | 0.039 | 1.3138 | 9.6694 | 14.2653
5654 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | YEDUMADU_66 | 1220304904010102 | F04-GABBADI-F | AGRI | DLMS Meter | 0.8845 | 0.7963 | 0 | 0.8845 | 9.9716 | 9.9716
5655 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | YEDUMADU_66 | 1220304904020302 | F05-MAIYAS | INDUSTRIAL | DLMS Meter | 0.06739 | 0.0671 | 0 | 0.06739 | 0.43033 | 0.43033
5656 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | YEDUMADU_66 | 1220304904020303 | F06-KADUJAKKASANDRA | AGRI | DLMS Meter | 0.58488 | 0.52643 | 0 | 0.58488 | 9.994 | 9.994
5657 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | YEDUMADU_66 | 1220304904010103 | F07-ARALALUSANDRA | AGRI | DLMS Meter | 0.51102 | 0.46572 | 0 | 0.51102 | 8.864 | 8.864
5658 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | YEDUMADU_66 | 1220304904020304 | F08-BILIGANAKUPPE | NJY | DLMS Meter | 0.40856 | 0.33435 | 0.038 | 0.37056 | 9.7717 | 40.42
5659 | BRAZ | RAMANAGAR | KANAKAPUR | HAROHALLY | YEDUMADU_66 | 1220304904020305 | F09-GOLLAHALLI NJY | NJY | DLMS Meter | 0.6906 | 0.44826 | 0.20215 | 0.48845 | 8.228 | 38.5965
5660 | BMANZ | NORTH | JALAHALLI | C9 | YELAHANKA_66 | 1120303901010101 | F01-,VIDYARANYAPURA | URBAN MIXED LOAD | DLMS Meter | 3.1672 | 2.8067 | 0 | 3.1672 | 11.3809 | 18.9573
5661 | BMANZ | NORTH | JALAHALLI | C9 | YELAHANKA_66 | 1120303901010102 | F02-YELAHANKA-OLD-TOWN | URBAN MIXED LOAD | DLMS Meter | 5.6079 | 3.3287 | 1.9927 | 3.6153 | 7.9273 | 14.4964
5662 | BMANZ | NORTH | HEBBAL | C7 | YELAHANKA_66 | 1120303901020308 | F03-K-M-F | COMMERCIAL | DLMS Meter | 3.6493 | 3.6024 | 0 | 3.6493 | 1.2868 | 1.2868
5663 | BMANZ | NORTH | HEBBAL | C7 | YELAHANKA_66 | 1120303901010103 | F04-YELAHANKA-NEW-TOWN | INDUSTRIAL | DLMS Meter | 1.1888 | 0.89346 | 0.28403 | 0.90474 | 1.2475 | 1.2475
5664 | BMANZ | NORTH | HEBBAL | C7 | YELAHANKA_66 | 1120303901020302 | F06-FMARUTHI-NAGAR | URBAN MIXED LOAD | DLMS Meter | 1.8088 | 0.89872 | 0.86 | 0.94875 | 5.2729 | 6.072
5665 | BMANZ | NORTH | JALAHALLI | C9 | YELAHANKA_66 | #N/A | F07-F,M.S.-PALYA | #N/A | DLMS Meter | 4.2674 | 3.6979 | 0.085 | 4.1824 | 11.584 | 15.216
5666 | BMANZ | NORTH | HEBBAL | C7 | YELAHANKA_66 | 1120303901010104 | F09-,JUDICIAL-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.1712 | 3.6898 | 0.35 | 3.8212 | 3.4377 | 7.7989
5667 | BMANZ | NORTH | HEBBAL | C7 | YELAHANKA_66 | 1120303901010105 | F10-I-A-F | URBAN MIXED LOAD | DLMS Meter | 2.4517 | 2.3434 | 0 | 2.4517 | 4.4164 | 18.2275
5668 | BMANZ | NORTH | HEBBAL | C8 | YELAHANKA_66 | 1120303901020305 | F12-,NCBS | URBAN MIXED LOAD | DLMS Meter | 4.2572 | 4.0765 | 0 | 4.2572 | 4.2445 | 15.3988
5669 | BMANZ | NORTH | JALAHALLI | C9 | YELAHANKA_66 | 1120303901010109 | F13-INDUSTRIAL AREA | INDUSTRIAL | DLMS Meter | 3.0303 | 2.7531 | 0.01 | 3.0203 | 8.848 | 11.1305
5670 | BMANZ | NORTH | HEBBAL | C7 | YELAHANKA_66 | 1120303901010106 | F14-PURVANKARA | DOMESTIC | DLMS Meter | 0.27619 | 0.2637 | 0 | 0.27619 | 4.522 | 6.6931
5671 | BMANZ | NORTH | HEBBAL | C7 | YELAHANKA_66 | 1120303901010107 | F15-PURVANKARA | DOMESTIC | DLMS Meter | 0.40246 | 0.36989 | 0.02 | 0.38246 | 3.2862 | 12.8611
5672 | BMANZ | NORTH | HEBBAL | C7 | YELAHANKA_66 | 1120303901020306 | F16-PURVANKARA | DOMESTIC | DLMS Meter | 0.2916 | 0.28281 | 0 | 0.2916 | 3.0138 | 23.5882
5673 | BMANZ | NORTH | HEBBAL | C7 | YELAHANKA_66 | 1120303901020307 | F17-PURVANKARA | DOMESTIC | DLMS Meter | 0.21644 | 0.19553 | 0.01 | 0.20644 | 5.2887 | 12.2234
5674 | BMANZ | NORTH | HEBBAL | C7 | YELAHANKA_66 | 1120303901020301 | F18-RMZ GALLERIA | DOMESTIC | DLMS Meter | 2.4877 | 1.3026 | 1.1 | 1.3877 | 6.1357 | 6.1357
5675 | BMANZ | NORTH | HEBBAL | C8 | YELAHANKA_66 | 1120303901010117 | F19-RAIN TREE BOLEVARD | DOMESTIC | DLMS Meter | 1.8098 | 0.90489 | 0.82 | 0.98975 | 8.5738 | 9.8774
5676 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901010301 | F01-KOLTHUR-NJY | NJY | DLMS Meter | 0.8848 | 0.80406 | 0 | 0.8848 | 9.1248 | 62.7307
5677 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901010302 | F02-MUTHAKAPALLI | AGRI | DLMS Meter | 1.8717 | 0.84543 | 0.93225 | 0.93945 | 10.0078 | 10.0078
5678 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901010303 | F03-YALDUR-LOCAL | AGRI | DLMS Meter | 0.64 | 0.57629 | 0 | 0.64 | 9.9553 | 9.9553
5679 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901010304 | F04-UPPUKUNTE | AGRI | DLMS Meter | 1.4043 | 0.63258 | 0.7014 | 0.7029 | 10.0037 | 10.0037
5680 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901010305 | F05-HOSAHALLI | AGRI | DLMS Meter | 0.3183 | 0.28635 | 0 | 0.3183 | 10.0377 | 10.0377
5681 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901010306 | F06-HOGALAGERE | AGRI | DLMS Meter | 1.1897 | 1.071 | 0 | 1.1897 | 9.9784 | 9.9784
5682 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901010307 | F07-LAKSHMISAGARA | AGRI | DLMS Meter | 1.3045 | 1.1743 | 0 | 1.3045 | 9.9799 | 9.9799
5683 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901010308 | F08-GAJALAHALLI-NJY | NJY | DLMS Meter | 1.0976 | 0.9951 | 0 | 1.0976 | 9.3399 | 65.4807
5684 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901020301 | F09-THINNALI | NJY | DLMS Meter | 0.96154 | 0.87538 | 0 | 0.96154 | 8.9603 | 60.9364
5685 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901010101 | F10-CHANNAHALLI | AGRI | DLMS Meter | 0.7014 | 0.32709 | 0.338 | 0.3634 | 9.9931 | 9.9931
5686 | BRAZ | KOLAR | KOLAR | SRINIVASAPURA | YELDUR_66 | 1230103901020303 | F11-ATHIKUNTE | AGRI | DLMS Meter | 0.93225 | 0.83904 | 0 | 0.93225 | 9.9985 | 9.9985
5687 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903010101 | F01-NAVODAYA-SCHOOL | GOVERNMENT OFFICES | DLMS Meter | 0.0429 | 0.042804 | 0 | 0.0429 | 0.22378 | 0.22378
5688 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903010102 | F02-NAVODAYA | AGRI | DLMS Meter | 0.8346 | 0.75109 | 0 | 0.8346 | 10.0065 | 10.0065
5689 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903010103 | F03-CHILKALANERUPU | AGRI | DLMS Meter | 1.3112 | 1.18 | 0 | 1.3112 | 10.0107 | 10.0107
5690 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903020301 | F04-THULAVANURU | AGRI | DLMS Meter | 1.2636 | 1.1372 | 0 | 1.2636 | 10.0028 | 10.0028
5691 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903020302 | F05-BURUDAGUNTE | AGRI | DLMS Meter | 0.95346 | 0.81302 | 0.05 | 0.90346 | 10.0103 | 10.0103
5692 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903020303 | F06-NANDANAVANA | AGRI | DLMS Meter | 1.0525 | 0.59628 | 0.39 | 0.66252 | 9.9974 | 9.9974
5693 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903020304 | F07-NADAMPALLI | AGRI | DLMS Meter | 1.1885 | 1.0696 | 0 | 1.1885 | 10.0056 | 10.0056
5694 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903020305 | F08-BTN-NJY | NJY | DLMS Meter | 0.63396 | 0.48151 | 0.087 | 0.54696 | 11.9654 | 76.2277
5695 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903020306 | F09-NJY-YENIGADALE | NJY | DLMS Meter | 0.6234 | 0.55425 | 0 | 0.6234 | 11.0927 | 70.2726
5696 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903020307 | F10-CHOKKANAHALLI | NJY | DLMS Meter | 0.568 | 0.4953 | 0 | 0.568 | 12.7986 | 86.9335
5697 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI RURAL | YENIGADALE_66 | 1230402903010104 | F11-T. DEVAPALLI | AGRI | DLMS Meter | 0.71896 | 0.64696 | 0 | 0.71896 | 10.0149 | 10.0149
5698 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901020101 | F01-SKF | INDUSTRIAL | DLMS Meter | 5.6938 | 5.6625 | 0 | 5.6938 | 0.55007 | 0.55184
5699 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010201 | F02-VIDYANAGARA | URBAN MIXED LOAD | DLMS Meter | 2.5792 | 2.095 | 0.3287 | 2.2505 | 6.9105 | 16.6846
5700 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010101 | F03-TEGUTECH. | URBAN MIXED LOAD | DLMS Meter | 2.3732 | 2.0007 | 0.245 | 2.1282 | 5.9888 | 8.3684
5701 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010102 | F04-KIRLOSKAR. | INDUSTRIAL | DLMS Meter | 3.7008 | 3.5052 | 0 | 3.7008 | 5.2865 | 5.2865
5702 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010103 | F05-YARANDAHALLY. | URBAN MIXED LOAD | DLMS Meter | 5.0226 | 4.8219 | 0 | 5.0226 | 3.9964 | 3.9964
5703 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010104 | F06-KUDUMA. | INDUSTRIAL | DLMS Meter | 4.5044 | 4.3654 | 0 | 4.5044 | 3.0859 | 4.3135
5704 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901020301 | F07-FIEM-AUTO. | INDUSTRIAL | DLMS Meter | 4.409 | 4.3505 | 0 | 4.409 | 1.3275 | 1.3275
5705 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901020302 | F08-BULZAR. | URBAN MIXED LOAD | DLMS Meter | 2.0943 | 1.966 | 0 | 2.0943 | 6.1259 | 6.1259
5706 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010301 | F10-SHETRON | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5707 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901020401 | F11-VICTORY-GLASS. | INDUSTRIAL | DLMS Meter | 6.5616 | 3.504 | 2.86 | 3.7016 | 5.3388 | 5.3388
5708 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901020402 | F12-DEEPAK-FORGE. | INDUSTRIAL | DLMS Meter | 6.6077 | 6.188 | 0 | 6.6077 | 6.3512 | 6.8837
5709 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030501 | F13-TIRUPALYA | URBAN MIXED LOAD | DLMS Meter | 4.4476 | 4.0244 | 0 | 4.4476 | 9.5145 | 9.5145
5710 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030502 | F14-KACHANAYAKANAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.9124 | 1.4613 | 0.315 | 1.5974 | 8.518 | 9.3288
5711 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030503 | F15-MTR. | INDUSTRIAL | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5712 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030504 | F16-CORTO-PRINTS. | INDUSTRIAL | DLMS Meter | 2.9088 | 1.4713 | 1.3336 | 1.5752 | 6.595 | 6.595
5713 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030505 | F17-BIA-ST-PHASE | INDUSTRIAL | DLMS Meter | 2.6016 | 2.5469 | 0 | 2.6016 | 2.1024 | 2.1024
5714 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030506 | F18-BIA-III-STAGE. | INDUSTRIAL | DLMS Meter | 3.0746 | 2.6241 | 0.279 | 2.7956 | 6.1337 | 6.1337
5715 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010202 | F19-BTL-COLLEGE | COMMERCIAL | DLMS Meter | 0.045606 | 0.040076 | 0 | 0.045606 | 12.1256 | 18.4273
5716 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010203 | F20-BIA-KSSIDC-SHEDS | INDUSTRIAL | DLMS Meter | 6.678 | 6.2344 | 0 | 6.678 | 6.6421 | 6.7492
5717 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030507 | F21-R-K-TOWN-SHIP | URBAN MIXED LOAD | DLMS Meter | 0.4924 | 0.42889 | 0.032999 | 0.4594 | 6.6406 | 11.2253
5718 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030508 | F22-CLOUD-NINE-LAYOUT. | URBAN MIXED LOAD | DLMS Meter | 0.8944 | 0.83769 | 0.025 | 0.8694 | 3.6471 | 4.6509
5719 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010204 | F23-MASTENAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.0504 | 1.0755 | 0.875 | 1.1754 | 8.4969 | 21.0267
5720 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901020403 | F24-SIEMENS | INDUSTRIAL | DLMS Meter | 6.0848 | 6.034 | 0 | 6.0848 | 0.83405 | 0.83405
5721 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901020404 | F25-TATA-BP-SOLAR | INDUSTRIAL | DLMS Meter | 2.2268 | 1.8617 | 0.28 | 1.9468 | 4.3699 | 5.4747
5722 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901020405 | F26-NH-HOSPITAL | HOSPITAL | DLMS Meter | 4.363 | 4.2525 | 0 | 4.363 | 2.5335 | 2.5335
5723 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030509 | F27-KIADB | INDUSTRIAL | DLMS Meter | 1.5174 | 1.4512 | 0 | 1.5174 | 4.3604 | 4.3604
5724 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030510 | F28-PPC ROAD | INDUSTRIAL | DLMS Meter | 1.8068 | 1.7557 | 0 | 1.8068 | 2.8269 | 4.3551
5725 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901030511 | F29-MANJUSHREE | INDUSTRIAL | DLMS Meter | 6.672 | 6.6917 | 0 | 6.672 | -0.29579 | -0.29579
5726 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010503 | F30-KSSIDC SHEDS | INDUSTRIAL | DLMS Meter | 2.8276 | 2.679 | 0 | 2.8276 | 5.2567 | 6.0397
5727 | BRAZ | RAMANAGAR | CHANDAPURA | CHANDAPURA | YERANDANAHALLI_220 | 1220203901010502 | F31-AGRI FEEDER | AGRI | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5728 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | YHUNASENAHALLI_66 | 1230403901020101 | F01-CHINTAMANI | AGRI | DLMS Meter | 0.99014 | 0.8914 | 0 | 0.99014 | 9.9725 | 9.9725
5729 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | YHUNASENAHALLI_66 | 1230403901020102 | F02-SEEGEHALLI | AGRI | DLMS Meter | 1.1165 | 1.0006 | 0 | 1.1165 | 10.3822 | 10.3822
5730 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | YHUNASENAHALLI_66 | 1230403901020301 | F03-KUNDALAGURKI | AGRI | DLMS Meter | 1.3935 | 1.144 | 0.11661 | 1.2769 | 10.4034 | 10.5325
5731 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | YHUNASENAHALLI_66 | 1230403901020302 | F04-DEVARAMALLUR | AGRI | DLMS Meter | 1.2347 | 0.80431 | 0.34076 | 0.89392 | 10.0239 | 10.0239
5732 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | YHUNASENAHALLI_66 | 1230403901020303 | F05-GORAMODAGU | NJY | DLMS Meter | 1.1134 | 1.0077 | 0 | 1.1134 | 9.4906 | 73.0423
5733 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | YHUNASENAHALLI_66 | 1230403901020304 | F06-PINDIPAPANAHALLI | AGRI | DLMS Meter | 1.4772 | 1.3207 | 0 | 1.4772 | 10.5938 | 10.6911
5734 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | YHUNASENAHALLI_66 | 1230403901020305 | F07-KANGANAHALLI | AGRI | DLMS Meter | 1.7569 | 1.5814 | 0 | 1.7569 | 9.9922 | 9.9922
5735 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | YHUNASENAHALLI_66 | 1230403901020306 | F08-GOLLAHALLI | NJY | DLMS Meter | 1.0235 | 0.92584 | 0 | 1.0235 | 9.5436 | 72.1467
5736 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | YHUNASENAHALLI_66 | 1230403901010101 | F09-KOTHANUR | AGRI | DLMS Meter | 1.1925 | 0.79009 | 0.31479 | 0.87767 | 9.9784 | 9.9784
5737 | BRAZ | KOLAR | CHINTHAMANI | SHIDLAGATTA URBAN | YHUNASENAHALLI_66 | 1230403901020307 | F10-KADASHENAHALLI-NJY | NJY | DLMS Meter | 0.9441 | 0.82386 | 0 | 0.9441 | 12.7356 | 68.8013
5738 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906010302 | F01-THIPPAGANAHALLY | AGRI | DLMS Meter | 1.4194 | 1.2776 | 0 | 1.4194 | 9.9895 | 12.0575
5739 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906010303 | F02-Y.N.HOSAKOTE | URBAN MIXED LOAD | DLMS Meter | 1.3092 | 1.2612 | 0 | 1.3092 | 3.6625 | 17.7176
5740 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906010301 | F03-G.T.HALLI | AGRI | DLMS Meter | 0.5534 | 0.50052 | 0 | 0.5534 | 9.5551 | 9.5551
5741 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906010101 | F04-JALODU | AGRI | DLMS Meter | 1.1476 | 1.0362 | 0 | 1.1476 | 9.7094 | 9.7094
5742 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906010105 | F06-HANUMANTHANAHALLI | AGRI | DLMS Meter | 1.5174 | 1.3694 | 0 | 1.5174 | 9.7537 | 9.8197
5743 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906020102 | F07--BHEMANAKUNTE | AGRI | DLMS Meter | 0.82642 | 0.74619 | 0 | 0.82642 | 9.7083 | 9.7083
5744 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906020103 | F08-HOSADURGA | AGRI | DLMS Meter | 0.59732 | 0.53967 | 0 | 0.59732 | 9.6514 | 15.3233
5745 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906020104 | F09-DODDAHALLY | AGRI | DLMS Meter | 0.89894 | 0.81014 | 0 | 0.89894 | 9.878 | 12.4503
5746 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906020101 | F10-S.N.HALLI | AGRI | DLMS Meter | 0.64654 | 0.58226 | 0 | 0.64654 | 9.9417 | 11.0424
5747 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906010104 | F11-HOSADURGA NJY | NJY | DLMS Meter | 0.98629 | 0.88794 | 0 | 0.98629 | 9.9714 | 72.1554
5748 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906020301 | F12-NJY-BHEEMANAKUNTE | NJY | DLMS Meter | 0.66311 | 0.60019 | 0 | 0.66311 | 9.4889 | 68.0112
5749 | CTAZ | TUMKUR | MADHUGIRI | PAVAGADA | YNHOSKOTE_66 | 1320306906020302 | F17- H.T STONE CRUSHER | INDUSTRIAL | DLMS Meter | 0.206 | 0.205 | 0 | 0.206 | 0.48301 | 0.48301
5750 | BMASZ | WEST | KENGERI | K3 | SOMANAHALLI_220 | 1140302901020301 | F02-KAGGALIPURA | URBAN MIXED LOAD | DLMS Meter | 1.3159 | 1.2171 | 0 | 1.3159 | 7.508 | 9.9684
5751 | BMASZ | WEST | KENGERI | K3 | SOMANAHALLI_220 | 1140302901010102 | F05-PGCL | DOMESTIC | DLMS Meter | 0.066139 | 0.062018 | 0 | 0.066139 | 6.2323 | 25.6234
5752 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | SOMENAHALLI_66 | 1230304905010202 | F02-SOMENAHALLI | AGRI | DLMS Meter | 0.94944 | 0.83664 | 0.02 | 0.92944 | 9.9844 | 9.9844
5753 | BRAZ | KOLAR | CHIKKABALLAPURA | GUDIBANDE | SOMENAHALLI_66 | 1230304905010201 | F05-DHINNAHALLI | AGRI | DLMS Meter | 1.091 | 0.94558 | 0.04 | 1.051 | 10.0303 | 10.0303
5754 | BMANZ | NORTH | JALAHALLI | C3 & N9 | ABBIGERE_66 | 1120203902010301 | F07-ABBIGERE-VILLAGE | URBAN MIXED LOAD | DLMS Meter | 7.1883 | 3.3534 | 3.5222 | 3.6661 | 8.5278 | 13.1933
5755 | BMASZ | SOUTH | JAYANAGAR | S1 & S2 | ADUGODI_66 | 1110102902010104 | F10-SIDDAIAH-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.7739 | 2.6879 | 0.96196 | 2.812 | 4.4133 | 6.4052
5756 | BMASZ | SOUTH | KORAMANGALA | S4 & S16 | ADUGODI_66 | 1110102902030505 | F15-INDUSTRIAL-KUDREMUKH | INDUSTRIAL | DLMS Meter | 3.2591 | 1.8633 | 1.9028 | 1.3562 | 4.5722 | 6.0127
5757 | BMASZ | SOUTH | KORAMANGALA | S3 & S4 | AMARJYOTHI_66 | 1110201902010101 | F01-EGIPURA | DOMESTIC | DLMS Meter | 2.1276 | 1.5143 | 0.545 | 1.5826 | 4.3134 | 7.7484
5758 | BMASZ | SOUTH | KORAMANGALA | S3 & E6 | AMARJYOTHI_66 | 1110201902020301 | F04-TH-CROSS-RMU | DOMESTIC | DLMS Meter | 4.2597 | 1.2344 | 2.9662 | 1.2936 | 4.5759 | 6.8797
5759 | BMASZ | SOUTH | KORAMANGALA | S3 & E6 | AMARJYOTHI_66 | 1110201902010104 | F09-SHANTHINAGAR-RMU | COMMERCIAL | DLMS Meter | 3.8648 | 2.4359 | 1.3195 | 2.5453 | 4.2987 | 4.349
5760 | BMANZ | EAST | INDIRA NAGAR | E3 & E6 | AMARJYOTHI_66 | 1110201902010301 | F14-ESI-HOSPITAL | DOMESTIC | DLMS Meter | 6.1291 | 3.5709 | 2.3243 | 3.8048 | 6.1455 | 9.2555
5761 | BMASZ | SOUTH | KORAMANGALA | S3 & E6 | AMARJYOTHI_66 | 1110201902020401 | F15-MARUTHI-INFO-TECH | COMMERCIAL | DLMS Meter | 5.6401 | 2.5293 | 3.0027 | 2.6375 | 4.0996 | 5.2096
5762 | BMASZ | SOUTH | KORAMANGALA | S3 & E6 | AMARJYOTHI_66 | 1110201902020402 | F16-CHERRY-HILL | COMMERCIAL | DLMS Meter | 9.6337 | 2.5385 | 6.9595 | 2.6742 | 5.0724 | 6.1106
5763 | BMASZ | SOUTH | KORAMANGALA | S3 & S4 | AMARJYOTHI_66 | 1110201902020403 | F17-NAVEEN-TERRACE | DOMESTIC | DLMS Meter | 5.3461 | 3.0137 | 2.2202 | 3.1259 | 3.5916 | 8.56
5764 | BMASZ | SOUTH | JAYANAGAR | S15 & S18 | AREHALLI_66 | 1110103903010101 | F01-NANDINI-ENCLAVE | URBAN MIXED LOAD | DLMS Meter | 2.5347 | 2.0802 | 0.32132 | 2.2134 | 6.019 | 9.9515
5765 | BMANZ | NORTH | MALLESHWARA | C1 & C2 | ASTATION_66 | 1130102901030501 | F03-OKALIPURAM | URBAN MIXED LOAD | DLMS Meter | 4.0576 | 2.9003 | 0.9336 | 3.124 | 7.1618 | 10.8281
5766 | BMANZ | EAST | VIDHANASOUDHA | W4 & C2 | ASTATION_66 | 1130102901040701 | F04-KUMARA-PARK-WEST | URBAN MIXED LOAD | DLMS Meter | 4.0584 | 3.2582 | 0.69388 | 3.3645 | 3.1584 | 10.1487
5767 | BMANZ | EAST | VIDHANASOUDHA | W4 & W5 | ASTATION_66 | 1130102901030502 | F07-STADIUM | COMMERCIAL | DLMS Meter | 1.5787 | 1.0982 | 0.43536 | 1.1434 | 3.9463 | 11.6415
5768 | BMANZ | EAST | VIDHANASOUDHA | W4 & W5 | ASTATION_66 | 1130102901020302 | F20-CUBBON-PET | URBAN MIXED LOAD | DLMS Meter | 3.0523 | 2.4864 | 0.40368 | 2.6486 | 6.1247 | 8.9548
5769 | BMANZ | EAST | VIDHANASOUDHA | W3 & W4 | ASTATION_66 | 1130102901020305 | F24-RAILWAY-QUARTERS | URBAN MIXED LOAD | DLMS Meter | 2.582 | 2.0194 | 0.4979 | 2.0841 | 3.1045 | 15.6725
5770 | BMASZ | SOUTH | JAYANAGAR | S2 & E3 | AUSTIN_TOWN_66 | 1110201904010103 | F04-TRINITY-CHURCH | URBAN MIXED LOAD | DLMS Meter | 5.92 | 3.6104 | 2.1567 | 3.7632 | 4.0604 | 4.189
5771 | BMASZ | SOUTH | KORAMANGALA | S3 & E3 | AUSTIN_TOWN_66 | 1110201904020304 | F08-LIFE-STYLE | COMMERCIAL | DLMS Meter | 6.7676 | 1.6341 | 5.0513 | 1.7163 | 4.7901 | 4.7901
5772 | BMASZ | SOUTH | KORAMANGALA | S2, S3 & E3 | AUSTIN_TOWN_66 | 1110201904030502 | F11-AUSTIN-TOWN-BWSSB | DOMESTIC | DLMS Meter | 4.1606 | 2.0574 | 2.0048 | 2.1559 | 4.5667 | 6.1259
5773 | BMASZ | SOUTH | KORAMANGALA | S3 & E3 | AUSTIN_TOWN_66 | 1110201904010107 | F19-VICTORIA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.4664 | 1.9539 | 1.415 | 2.0514 | 4.7523 | 7.8734
5774 | BMANZ | EAST | WHITEFIELD | E4 & AVALAHALLI | AWHO | 1310203907010109 | F11-GANESHA TEMPLE | URBAN MIXED LOAD | DLMS Meter | 2.1395 | 1.0967 | 0.99961 | 1.1399 | 3.791 | 3.791
5775 | BMANZ | EAST | WHITEFIELD | E7 & AVALAHALLI | AWHO | 1310203907010110 | F12-SADARAMANGALA | URBAN MIXED LOAD | DLMS Meter | 3.3557 | 1.7933 | 1.4319 | 1.9238 | 6.785 | 11.7346
5776 | BMANZ | EAST | INDIRA NAGAR | E3 & E2 | B_STATION_66 | 1130201902030502 | F20-YMCA-RMU | COMMERCIAL | DLMS Meter | 3.4426 | 2.4303 | 0.94387 | 2.4987 | 2.7401 | 6.2483
5777 | BMANZ | EAST | INDIRA NAGAR | E3 & E2 | B_STATION_66 | 1130201902030503 | F22-MANIPAL-RMU | URBAN MIXED LOAD | DLMS Meter | 3.2163 | 3.0484 | 0.05312 | 3.1632 | 3.6293 | 9.1218
5778 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | BADDIHALLI_66 | 1320105901020303 | F10-CM-EXTENSION | URBAN MIXED LOAD | DLMS Meter | 4.65 | 2.3411 | 2.1075 | 2.5425 | 7.9237 | 25.0143
5779 | BMASZ | WEST | RR NAGAR | W1 & W8 | BANASHANKARI_66 | 1110105902010101 | F01-SRINAGAR | URBAN MIXED LOAD | DLMS Meter | 3.7805 | 2.3115 | 1.3633 | 2.4172 | 4.3735 | 12.0989
5780 | BMASZ | WEST | RR NAGAR | W1 & W8 | BANASHANKARI_66 | 1110105902020402 | F09-THYAGARAJA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.9957 | 2.5296 | 1.2085 | 2.7872 | 9.2423 | 16.5142
5781 | BMASZ | WEST | RR NAGAR | W1, W2 & W8 | BANASHANKARI_66 | 1110105902010301 | F14-BULL TEMPLE ROAD | DOMESTIC | DLMS Meter | 3.5054 | 2.9941 | 0.41204 | 3.0933 | 3.2091 | 9.448
5782 | BMASZ | WEST | RR NAGAR | W7 & S15 | BANASHANKARI_66 | 1110105902020302 | F15-BANGARAPPA NAGARA | URBAN MIXED LOAD | DLMS Meter | 9.7275 | 5.1191 | 4.307 | 5.4205 | 5.5601 | 35.0721
5783 | BMASZ | WEST | RR NAGAR | W1 & W8 | BANASHANKARI_66 | 1110105902030601 | F16-PES-COLLEGE | URBAN MIXED LOAD | DLMS Meter | 2.0616 | 1.8861 | 0.064831 | 1.9967 | 5.5418 | 13.5486
5784 | BMASZ | WEST | RR NAGAR | W1 & W6 | BANASHANKARI_66 | 1110105902030603 | F18-AVALAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.1035 | 2.7829 | 0.20647 | 2.8971 | 3.9417 | 10.7865
5785 | BMASZ | WEST | RR NAGAR | W6 & S15 | BANASHANKARI_66 | 1110105902030604 | F19-VEERABHADRA NAGAR | URBAN MIXED LOAD | DLMS Meter | 3.364 | 2.4566 | 0.80881 | 2.5552 | 3.8586 | 5.9905
5786 | BMASZ | WEST | RR NAGAR | W1 & W8 | BANASHANKARI_66 | 1110105902010105 | F21-MUNESHWARA-BLOCK | URBAN MIXED LOAD | DLMS Meter | 2.3471 | 1.9237 | 0.32622 | 2.0209 | 4.8107 | 15.5055
5787 | BMASZ | WEST | RR NAGAR | W1 & W6 | BANASHANKARI_66 | 1110105902030506 | F25-NTY-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.6268 | 4.0406 | 0.2465 | 4.3803 | 7.7563 | 12.1065
5788 | BMANZ | EAST | SHIVAJINAGAR | E5 & E8 | BANASWADI_66 | 1130304901020104 | F17-ADMC | URBAN MIXED LOAD | DLMS Meter | 4.5702 | 3.674 | 0.5243 | 4.0459 | 9.1918 | 17.4474
5789 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905010102 | F03-MANJUNATHANAGARA | URBAN MIXED LOAD | DLMS Meter | 3.2165 | 1.7118 | 1.86 | 1.3565 | 8.7084 | 8.7084
5790 | CTAZ | TUMKUR | TIPTUR | TIPTUR | BANDIHALLI_110 | 1320201905020305 | F13-GANDHINAGARA | URBAN MIXED LOAD | DLMS Meter | 5.4382 | 2.7142 | 3.3328 | 2.1054 | 8.409 | 28.8559
5791 | BMASZ | SOUTH | HSR | S10 & S12 | BANNERGHATTAROAD_66 | 1220204901010101 | F01-WEAVERS-COLONY | URBAN MIXED LOAD | DLMS Meter | 6.8473 | 3.5901 | 3.0072 | 3.8401 | 6.5112 | 9.9221
5792 | BMASZ | SOUTH | HSR | S10 & JIGANI | BANNERGHATTAROAD_66 | 1220204901010103 | F05-AMC | URBAN MIXED LOAD | DLMS Meter | 6.0574 | 5.2973 | 0.349 | 5.7084 | 7.2013 | 9.9737
5793 | BMASZ | WEST | RAJAJINAGAR | N6 & N4 | BRINDAVANA_66 | 1120101902010102 | F05-DODDANNA-INDL.-ESTATE | URBAN MIXED LOAD | DLMS Meter | 7.7594 | 6.0779 | 1.3538 | 6.4055 | 5.1152 | 7.7168
5794 | BMASZ | WEST | RAJAJINAGAR | N6 & N4 | BRINDAVANA_66 | 1120101902010103 | F06-FHEGGANAHALLI | URBAN MIXED LOAD | DLMS Meter | 9.0285 | 4.8219 | 3.9157 | 5.1129 | 5.6914 | 11.0947
5795 | BMASZ | SOUTH | HSR | S10 & S19 | BTMIVPHASE_66 | 1110302901020307 | F13-VISHWA-PRIYA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.0745 | 2.4395 | 0.49 | 2.5845 | 5.6091 | 11.0241
5796 | BMASZ | WEST | RAJAJINAGAR | N6 & N4 | BYADRAHALLI_66 | 1140303901020303 | F09-SHANKARAPPA-INDUSTRIAL-ESTATE | INDUSTRIAL | DLMS Meter | 5.465 | 5.0496 | 0.14838 | 5.3167 | 5.0241 | 7.4976
5797 | BMASZ | WEST | RAJAJINAGAR | N6 & K2 | BYADRAHALLI_66 | 1140303901020305 | F10-NADAKERAPPA-INDUSTRIAL-AREA | URBAN MIXED LOAD | DLMS Meter | 7.5443 | 4.7767 | 2.4887 | 5.0556 | 5.5163 | 7.1083
5798 | BMASZ | WEST | RAJAJINAGAR | N6 & K2 | BYADRAHALLI_66 | 1140303901020304 | F11-ANJANANAGARA | DOMESTIC | DLMS Meter | 10.0381 | 6.5833 | 3.0455 | 6.9927 | 5.8542 | 13.4993
5799 | BMANZ | EAST | SHIVAJINAGAR | E2 & W4 | C_STATION_66 | 1130302901010101 | F01-VIDHANA-SOUDHA | URBAN MIXED LOAD | DLMS Meter | 5.3044 | 3.188 | 1.9796 | 3.3248 | 4.116 | 4.3023
5800 | BMANZ | EAST | SHIVAJINAGAR | E2 & W4 | C_STATION_66 | 1130302901010103 | F03-MILLERS-ROAD | URBAN MIXED LOAD | DLMS Meter | 5.7154 | 3.5232 | 1.998 | 3.7173 | 5.2237 | 5.2237
5801 | BMANZ | EAST | SHIVAJINAGAR | E2 & W4 | C_STATION_66 | 1130302901010201 | F15-GENEVA-HOUSE | URBAN MIXED LOAD | DLMS Meter | 4.1477 | 3.832 | 0 | 4.1477 | 7.612 | 9.737
5802 | BMANZ | EAST | VIDHANASOUDHA | W4 & C2 | C_STATION_66 | 1130302901010202 | F18-PALACE-GUTTALLI | URBAN MIXED LOAD | DLMS Meter | 4.9406 | 4.3428 | 0.44 | 4.5006 | 3.5044 | 6.8771
5803 | BMANZ | EAST | SHIVAJINAGAR | E1 & E2 | C_STATION_66 | 1130302901010108 | F22-CHANDRAIAH | URBAN MIXED LOAD | DLMS Meter | 3.9621 | 2.3077 | 1.4819 | 2.4802 | 6.9551 | 27.8867
5804 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906020301 | F01-PAVAGADAROAD | URBAN MIXED LOAD | DLMS Meter | 7.824 | 3.4724 | 3.9867 | 3.8373 | 9.5111 | 19.018
5805 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906020101 | F02-BANGALORE ROAD | URBAN MIXED LOAD | DLMS Meter | 6.2408 | 2.7605 | 3.1189 | 3.1219 | 11.5754 | 18.4556
5806 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906010101 | F07-SOMAGUDDIROAD | URBAN MIXED LOAD | DLMS Meter | 1.7256 | 1.6283 | 0 | 1.7256 | 5.6337 | 18.2793
5807 | CTAZ | DAVANAGERE | HIRIYURU | CHALLAKERE | CHALLAKERE_66 | 1310402906010102 | F08-BELLARY ROAD | URBAN MIXED LOAD | DLMS Meter | 5.5137 | 2.3552 | 2.9542 | 2.5595 | 7.9806 | 15.5949
5808 | BMASZ | WEST | RAJAJINAGAR | N2 & N10 | CHANDRA LAYOUT_66 | 1140102901010101 | F02-MUDALAPALYA | URBAN MIXED LOAD | DLMS Meter | 6.2844 | 4.5851 | 1.3539 | 4.9305 | 7.0051 | 13.4011
5809 | BMASZ | WEST | RAJAJINAGAR | N2 & N10 | CHANDRA LAYOUT_66 | 1140102901020302 | F06-F-SKYLINE-APARTMENT | URBAN MIXED LOAD | DLMS Meter | 4.4275 | 3.7697 | 0.4131 | 4.0144 | 6.0949 | 10.581
5810 | BMASZ | WEST | RR NAGAR | W6, N2 & N10 | CHANDRA LAYOUT_66 | 1140102901020304 | F10-BEL-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 4.5147 | 4.0087 | 0.32224 | 4.1925 | 4.384 | 8.2343
5811 | BMASZ | WEST | RAJAJINAGAR | N2 & N10 | CHANDRA LAYOUT_66 | 1140102901010103 | F11-SVG-NAGAR | URBAN MIXED LOAD | DLMS Meter | 4.6843 | 4.0729 | 0.34273 | 4.3415 | 6.1862 | 16.5905
5812 | BRAZ | KOLAR | CHINTHAMANI | CHINTHAMANI URBAN | CHINTAMANI_66 | 1230401901010106 | F12-SMV | URBAN MIXED LOAD | DLMS Meter | 3.0955 | 1.0646 | 2.8861 | 0.20943 | 12.0488 | 44.6636
5813 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010502 | F13-CHANDRAVALLI | DOMESTIC | DLMS Meter | 8.633 | 4.2573 | 3.9858 | 4.6472 | 8.3902 | 13.5914
5814 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | DABUSPET_220 | 1210104902020304 | F10-GOVINAHALLI | AGRI | DLMS Meter | 0.75985 | 0.61001 | 0.085 | 0.67485 | 9.6189 | 20.3094
5815 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE URBAN SUB DIVISION 1 & DAVANAGERE RURAL | DAVANGERE_SRS_220 | 1310101902010106 | F06-NAGNUR | AGRI | DLMS Meter | 1.0578 | 0.95174 | 0 | 1.0578 | 10.0268 | 10.0268
5816 | BMANZ | EAST | INDIRA NAGAR | E3 & W4 | EASTDIVCOMP_220 | 1130201901020301 | F06-FSTAR-INDIA-BUILDING | URBAN MIXED LOAD | DLMS Meter | 1.1598 | 1.0411 | 0.084865 | 1.0749 | 3.1408 | 3.1408
5817 | BMASZ | SOUTH | KORAMANGALA | S7 & E12 | EPIP_66 | 1130202907020303 | F08-RG-HALLI-/-SIDDAPURA-GATE | DOMESTIC | DLMS Meter | 6.5393 | 6.4026 | 0 | 6.5393 | 2.0908 | 5.4474
5818 | BMANZ | EAST | SHIVAJINAGAR | E9 & AVALAHALLI | GEDDALAHALLI | 1130305903010203 | F10-HOSAKOTE | URBAN MIXED LOAD | DLMS Meter | 14.7139 | 6.1797 | 7.7225 | 6.9914 | 11.6107 | 13.0897
5819 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | GUTTUR_66 | 1310301902010301 | F01-HARIHAR-W/W | WATER WORKS | DLMS Meter | 0.92355 | 0.84311 | 0.01395 | 0.9096 | 7.31 | 24.9718
5820 | CTAZ | DAVANAGERE | HARIHARA | HARIHARA | GUTTUR_66 | 1310301902010102 | F03-KHB | DOMESTIC | DLMS Meter | 1.3243 | 0.71031 | 0.56177 | 0.76257 | 6.8542 | 22.4666
5821 | BMASZ | SOUTH | KORAMANGALA | S3 & E6 | HAL_220 | 1110203905010305 | F10-TEXAS | COMMERCIAL | DLMS Meter | 3.353 | 2.9442 | 0.27454 | 3.0784 | 4.3594 | 15.6529
5822 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | HALUVAGALU_66 | 1310303902020305 | F02- KANVI | AGRI | DLMS Meter | 0.4074 | 0.36662 | 0 | 0.4074 | 10.0098 | 10.0098
5823 | BMANZ | EAST | SHIVAJINAGAR | E5 & E9 | HBRLAYOUT_66 | 1130305902020302 | F08-RACHENAHALLI | URBAN MIXED LOAD | DLMS Meter | 4.6333 | 4.2712 | 0.012965 | 4.6203 | 7.5561 | 10.7177
5824 | BMANZ | EAST | SHIVAJINAGAR | E5 & E9 | HBRLAYOUT_66 | 1130305902020303 | F09-TITAN-GARAGE | URBAN MIXED LOAD | DLMS Meter | 5.0978 | 4.9456 | 0.003554 | 5.0942 | 2.9175 | 5.8174
5825 | BMANZ | EAST | SHIVAJINAGAR | E1 & C4 | HEBBAL_220 | 1120301901010101 | F01-VYALIKAVAL | DOMESTIC | DLMS Meter | 5.8402 | 4.0414 | 1.5693 | 4.2709 | 5.3736 | 14.2102
5826 | BMANZ | NORTH | HEBBAL | C5 | HEBBAL_220 | 1120301901010109 | F09-A-STATION | DOMESTIC | DLMS Meter | 5.2443 | 2.7237 | 2.4014 | 2.8429 | 4.1957 | 13.1889
5827 | BMASZ | WEST | KENGERI | K1 & BIDADI | HEJJALA_66 | 1220101902020303 | F11-KHBHAMPAPURA1 | DOMESTIC | DLMS Meter | 0.12262 | 0.11762 | 0 | 0.12262 | 4.0777 | 27.1651
5828 | BMASZ | WEST | KENGERI | K1 & BIDADI | HEJJALA_66 | 1220101902020304 | F12-KHBHAMPAPURA2 | DOMESTIC | DLMS Meter | 0.011249 | 0.010749 | 0 | 0.011249 | 4.4448 | 22.0218
5829 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | HIREHALLY_66 | 1320105902020304 | F09-MARNAYAKANAPALYA | DOMESTIC | DLMS Meter | 6.3071 | 3.7972 | 2.1317 | 4.1755 | 9.0586 | 35.0886
5830 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | HIRIYUR_66 | 1310401902010107 | F11-CHALLAKERE WATER WORKS | WATER WORKS | DLMS Meter | 0.76974 | 0.62023 | 0.098173 | 0.67157 | 7.6451 | 81.6381
5831 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906020503 | F15-HOSKOTE-OLD-TOWN | DOMESTIC | DLMS Meter | 8.2854 | 4.1797 | 5.419 | 2.8664 | 8.1256 | 27.4931
5832 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906030901 | F18-AYYAPPA-TEMPLE | DOMESTIC | DLMS Meter | 4.2275 | 2.8449 | 2.3666 | 1.8609 | 4.075 | 39.8915
5833 | BRAZ | BANGALORE RURAL | HOSAKOTE | HOSAKOTE | HOSAKOTE_66 | 1210201906031101 | F22-OLD-MADRAS-ROAD | DOMESTIC | DLMS Meter | 5.5548 | 3.1845 | 3.1839 | 2.3709 | 9.5871 | 16.8626
5834 | BMASZ | SOUTH | HSR | S13 & VEERASANDRA | HSRLAYOUT_220 | 1110303904010309 | F16-SOMASUNDAR-PALYA | DOMESTIC | DLMS Meter | 7.4763 | 4.6508 | 2.529 | 4.9473 | 5.9929 | 6.7274
5835 | BMANZ | NORTH | MALLESHWARA | C1 & C2 | IISC_66 | 1120202901010103 | F05-GANESHATEMPLE | URBAN MIXED LOAD | DLMS Meter | 3.4491 | 3.1938 | 0.15652 | 3.2926 | 2.9994 | 7.0027
5836 | BMANZ | NORTH | MALLESHWARA | C1, C2 & C6 | IISC_66 | 1120202901010104 | F07-MYSORE-LAMPS | URBAN MIXED LOAD | DLMS Meter | 4.6978 | 2.3224 | 2.2155 | 2.4823 | 6.4398 | 39.4931
5837 | BMASZ | SOUTH | JAYANAGAR | S5 & S18 | ISKCON_66 | 1110103904020203 | F03-RAGHUVANAHALLI | URBAN MIXED LOAD | DLMS Meter | 3.714 | 3.1977 | 0.40852 | 3.3055 | 3.2634 | 7.5977
5838 | BMANZ | EAST | INDIRA NAGAR | E10 & E12 | ITI_66 | 1130204901020106 | F16-MAPLE-HEIGHTS-APARTMENTS | URBAN MIXED LOAD | DLMS Meter | 6.0861 | 3.2396 | 2.6855 | 3.4006 | 4.7337 | 7.4713
5839 | BMASZ | SOUTH | HSR | S20 & S4 | JAKKASANDRA_66 | 1110305901010102 | F04-HSR 5TH SECTOR | URBAN MIXED LOAD | DLMS Meter | 7.0457 | 3.9501 | 2.8526 | 4.1931 | 5.7954 | 7.3905
5840 | BMASZ | SOUTH | JAYANAGAR | S1 & S14 | JAYADEVA_66 | 1110101903010202 | F05-SARAKKI-&-ADUGODI_-LINE | URBAN MIXED LOAD | DLMS Meter | 4.8482 | 2.8356 | 1.8051 | 3.043 | 6.8172 | 9.332
5841 | BMASZ | SOUTH | KORAMANGALA | S16 & S1 | JAYADEVA_66 | 1110101903010203 | F08-FCI-RMU | URBAN MIXED LOAD | DLMS Meter | 6.3414 | 3.6614 | 2.4155 | 3.9259 | 6.7382 | 8.2894
5842 | BMASZ | SOUTH | HSR | S19 & S14 | JAYADEVA_66 | 1110101903020304 | F13-VIJAYA-BANK-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 5.7572 | 3.3594 | 2.2886 | 3.4686 | 3.1501 | 6.5262
5843 | BMASZ | SOUTH | KORAMANGALA | S16 & S1 | JAYADEVA_66 | 1110101903010205 | F14-SUBRAMANYA-ARCADE | URBAN MIXED LOAD | DLMS Meter | 2.7746 | 2.067 | 0.545 | 2.2296 | 7.2903 | 18.7195
5844 | BMASZ | SOUTH | KORAMANGALA | S16 & S14 | JAYADEVA_66 | 1110101903020308 | F18-DIVYA-SHREE-TOWERS | URBAN MIXED LOAD | DLMS Meter | 9.0686 | 4.9269 | 3.9246 | 5.144 | 4.2217 | 4.2217
5845 | BMASZ | SOUTH | KORAMANGALA | S16 & S14 | JAYADEVA_66 | 1110101903020403 | F20-BTM-I-STAGE | URBAN MIXED LOAD | DLMS Meter | 5.1234 | 3.1054 | 1.7905 | 3.3329 | 6.8264 | 10.8016
5846 | BMASZ | SOUTH | KORAMANGALA | S16 & S14 | JAYADEVA_66 | 1110101903020405 | F22-SHOBHA-GARDEN | URBAN MIXED LOAD | DLMS Meter | 11.0173 | 6.8234 | 3.6718 | 7.3455 | 7.108 | 9.2183
5847 | BMASZ | SOUTH | KORAMANGALA | S7 & E4 | KACHAMARANAHALLI_66 | 1130202906010101 | F05-KM-HALLI-&-GUNJUR | URBAN MIXED LOAD | DLMS Meter | 6.5059 | 3.7428 | 2.6458 | 3.8601 | 3.0399 | 8.7196
5848 | BMANZ | EAST | WHITEFIELD | E4 & AVALAHALLI | KACHAMARANAHALLI_66 | 1130202906020305 | F11-MADURANAGAR & VALEPURA | DOMESTIC | DLMS Meter | 8.9813 | 3.6532 | 4.9151 | 4.0661 | 10.1541 | 30.0839
5849 | BMASZ | SOUTH | KORAMANGALA | S7 & S17 | KADABISANAHALLI_66 | 1110203901010302 | F07-FMULTIPLEX-MARATHALLY | URBAN MIXED LOAD | DLMS Meter | 7.7786 | 5.5641 | 1.7732 | 6.0054 | 7.3491 | 12.3839
5850 | BRAZ | RAMANAGAR | KANAKAPUR | KANAKAPUR URBAN | KANAKAPURA_66 | 1220301901020303 | F10-TOWN-1 | URBAN MIXED LOAD | DLMS Meter | 6.1852 | 2.9143 | 4.2139 | 1.9713 | 8.0233 | 20.7215
5851 | BMASZ | SOUTH | JAYANAGAR | S2 & E3 | KANTEERVA_66 | 1130103901010111 | F13-RMU-02 SR NAGARA | URBAN MIXED LOAD | DLMS Meter | 3.4009 | 1.6202 | 1.713 | 1.6879 | 4.0129 | 4.0129
5852 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902030503 | F03-VOLGAMADHI | AGRI | DLMS Meter | 1.4995 | 1.3658 | 0 | 1.4995 | 8.9163 | 8.9163
5853 | BRAZ | KOLAR | KGF | KGF | KGF_66 | 1230201902020302 | F06-SUNDARAPALYA | AGRI | DLMS Meter | 1.577 | 1.4229 | 0 | 1.577 | 9.7743 | 12.0141
5854 | BMANZ | NORTH | HEBBAL | C7 & C9 | KHB_66 | 1120303902010103 | F03-ANANTHAPURA | INDUSTRIAL | DLMS Meter | 2.8971 | 2.8156 | 0 | 2.8971 | 2.8128 | 4.4946
5855 | BRAZ | BANGALORE RURAL | NELAMANGALA | DODDABALAPURA (U) | KIADB_220 | 1210101907020303 | F08-TOWN | URBAN MIXED LOAD | DLMS Meter | 3.689 | 3.2841 | 0 | 3.689 | 10.9753 | 10.9753
5856 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902010107 | F12-GAJALDINNE | URBAN MIXED LOAD | DLMS Meter | 2.539 | 1.1051 | 1.3142 | 1.2248 | 9.7694 | 28.2198
5857 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | KOLAR_220 | 1230101902020306 | F13-MAHALAKSHMI-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 10.5141 | 4.0272 | 6.0573 | 4.4569 | 9.6411 | 30.5914
5858 | BMANZ | EAST | WHITEFIELD | E7 & AVALAHALLI | KONADASPURA_66 | 1210201901010102 | F01-BHATTARAHALLI | DOMESTIC | DLMS Meter | 5.6741 | 5.0769 | 0.39284 | 5.2812 | 3.8701 | 9.315
5859 | BMANZ | EAST | INDIRA NAGAR | E11 & AVALAHALLI | KONADASPURA_66 | 1210201901010109 | F02-MEDAHALLI | DOMESTIC | DLMS Meter | 6.9458 | 5.3899 | 1.1323 | 5.8135 | 7.2863 | 10.9944
5860 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902010103 | F13-VISHAKA-FACTORY | INDUSTRIAL | DLMS Meter | 4.9994 | 4.8695 | 0 | 4.9994 | 2.5981 | 2.8042
5861 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL | KUKKAWADA_66 | 1310103903020501 | F10-MATHI | AGRI | DLMS Meter | 0.6184 | 0.55654 | 0 | 0.6184 | 10.0031 | 10.0031
5862 | BMASZ | SOUTH | KORAMANGALA | S3 & E6 | LEELAVENTURE_66 | 1130203901020101 | F02-AUSTIN-CHECKPOST | URBAN MIXED LOAD | DLMS Meter | 2.38 | 1.8098 | 0.5008 | 1.8792 | 3.6964 | 5.9637
5863 | BMASZ | SOUTH | KORAMANGALA | S3 & E6 | LEELAVENTURE_66 | 1130203901020102 | F03-HAL-MANIPAL-RMU | URBAN MIXED LOAD | DLMS Meter | 4.9847 | 3.9741 | 0.83504 | 4.1497 | 4.2311 | 6.6581
5864 | BMASZ | SOUTH | KORAMANGALA | S3 & E6 | LEELAVENTURE_66 | 1130203901020104 | F06-FHAL-NAL-RMU | URBAN MIXED LOAD | DLMS Meter | 2.5995 | 0.59801 | 1.9669 | 0.63267 | 5.4773 | 6.7061
5865 | BMASZ | SOUTH | KORAMANGALA | S3 & E6 | LEELAVENTURE_66 | 1130203901020105 | F08-BRITANIA | URBAN MIXED LOAD | DLMS Meter | 3.9126 | 3.2521 | 0.4882 | 3.4244 | 5.0317 | 6.0746
5866 | BMANZ | EAST | INDIRA NAGAR | E3 & E6 | LEELAVENTURE_66 | 1130203901020303 | F09-B'STATION-LPSC(ISRO) | URBAN MIXED LOAD | DLMS Meter | 3.1739 | 2.4063 | 0.62405 | 2.5499 | 5.6293 | 7.2672
5867 | BMANZ | EAST | SHIVAJINAGAR | E9 & C4 | LRBANDE_66 | 1120302901010101 | F03-DASARAHALLI | URBAN MIXED LOAD | DLMS Meter | 1.1989 | 0.033885 | 1.1623 | 0.036605 | 7.4312 | 14.7401
5868 | BMANZ | NORTH | HEBBAL | C4 & C6 | MATHIKERE_66 | 1120204901010102 | F03-DOLLARS-COLONY | DOMESTIC | DLMS Meter | 1.6717 | 1.2482 | 0.3257 | 1.346 | 7.2647 | 15.4071
5869 | BMANZ | NORTH | HEBBAL | C4 & C6 | MATHIKERE_66 | 1120204901010103 | F04-FT-ROAD | DOMESTIC | DLMS Meter | 7.0585 | 2.9243 | 3.9818 | 3.0768 | 4.957 | 11.1989
5870 | BMANZ | NORTH | JALAHALLI | N9 & N5 | MEILAYOUT_66 | 1120102903010104 | F04-PIPELINE T-DASARAHALLY | URBAN MIXED LOAD | DLMS Meter | 6.6465 | 3.11 | 3.2806 | 3.3658 | 7.5998 | 17.4841
5871 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906010102 | F02-URBAN | URBAN MIXED LOAD | DLMS Meter | 3.9283 | 2.3849 | 1.3228 | 2.6055 | 8.4657 | 29.7747
5872 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906020302 | F07-LOCAL | DOMESTIC | DLMS Meter | 6.0048 | 2.6068 | 3.1429 | 2.8619 | 8.9117 | 37.2545
5873 | BRAZ | KOLAR | KGF | MULABAGILU | MULBAGAL_66 | 1230202906020101 | F15-TOWN | DOMESTIC | DLMS Meter | 10.7184 | 5.5935 | 4.8745 | 5.8439 | 4.2851 | 28.2636
5874 | BMASZ | SOUTH | HSR | S8 & S20 | NAGANATHAPURA_66 | 1110303901020102 | F02-CHENNAKESHAVA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 4.6734 | 3.9717 | 0.42235 | 4.251 | 6.5697 | 8.5215
5875 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901020101 | F01-BASAPURA | DOMESTIC | DLMS Meter | 3.6216 | 3.2531 | 0.30446 | 3.3171 | 1.9292 | 3.7066
5876 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901020103 | F03-SINGASANDRA | URBAN MIXED LOAD | DLMS Meter | 3.1686 | 2.9978 | 0 | 3.1686 | 5.3913 | 5.3913
5877 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901020104 | F04-KASAVANAHALLI | DOMESTIC | DLMS Meter | 6.0761 | 5.1152 | 0.69164 | 5.3845 | 5.001 | 10.0597
5878 | BMASZ | SOUTH | HSR | S13 | NAGANATHAPURA_66 | 1110303901020105 | F05-A.E.C.S-LAYOUT-ST-BLOCK | URBAN MIXED LOAD | DLMS Meter | 3.7781 | 3.6061 | 0.026524 | 3.7516 | 3.8772 | 8.2324
5879 | BMASZ | SOUTH | HSR | S8 | NAGANATHAPURA_66 | 1110303901020106 | F06-FHONGASANDRA | URBAN MIXED LOAD | DLMS Meter | 4.7903 | 4.0649 | 0.337 | 4.4533 | 8.7224 | 8.7224
5880 | BMASZ | SOUTH | HSR | S13 & VEERASANDRA | NAGANATHAPURA_66 | 1110303901020107 | F07-HUSKUR | URBAN MIXED LOAD | DLMS Meter | 4.6031 | 2.4893 | 1.8931 | 2.71 | 8.1435 | 9.2236
5881 | BMASZ | WEST | RAJAJINAGAR | N1 & C1 | NANDINILAYOUT_66 | 1120103902020302 | F04-GKW-&-KIRLOSKAR | URBAN MIXED LOAD | DLMS Meter | 5.4843 | 2.1115 | 3.2893 | 2.195 | 3.8018 | 8.7442
5882 | BMASZ | WEST | RR NAGAR | W2 & W6 | NATIONAL_COLLEGE_66 | 1140202901010105 | F03- 5-TH-MAIN-ROAD-VIJAYA-ENCLAVE | URBAN MIXED LOAD | DLMS Meter | 3.979 | 2.0765 | 1.747 | 2.2321 | 6.968 | 13.736
5883 | BMASZ | WEST | RR NAGAR | W2 & W6 | NATIONAL_COLLEGE_66 | 1140202901010102 | F04-KANNADA-SAHITHYA-PARISHATH | URBAN MIXED LOAD | DLMS Meter | 3.5489 | 3.3757 | 0.0254 | 3.5235 | 4.1939 | 15.0639
5884 | BMASZ | WEST | RR NAGAR | W2 & W8 | NATIONAL_COLLEGE_66 | 1140202901020301 | F08-I-BEAM-RMU | URBAN MIXED LOAD | DLMS Meter | 3.9393 | 2.9288 | 0.85674 | 3.0826 | 4.9902 | 11.7054
5885 | BMASZ | WEST | RR NAGAR | W2 & W6 | NATIONAL_COLLEGE_66 | 1140202901020302 | F09-UTTARADI-MUTT-RMU | URBAN MIXED LOAD | DLMS Meter | 2.0129 | 1.5963 | 0.2923 | 1.7206 | 7.2218 | 14.0401
5886 | BMASZ | WEST | RR NAGAR | W2 & W8 | NATIONAL_COLLEGE_66 | 1140202901020304 | F11-POLICE-STATION-RMU | URBAN MIXED LOAD | DLMS Meter | 4.2261 | 2.5901 | 1.4996 | 2.7265 | 5.003 | 12.0091
5887 | BMASZ | WEST | RR NAGAR | W2 & S2 | NATIONAL_COLLEGE_66 | 1140202901020305 | F12-NATIONAL-COLLEGE | URBAN MIXED LOAD | DLMS Meter | 6.9678 | 3.5302 | 3.2895 | 3.6783 | 4.0277 | 9.8509
5888 | BMASZ | WEST | KENGERI | K2 & N4 | NELAKEDIRENAHALLI_66 | 1120101901020303 | F13-KEMPAIAH GARDEN | INDUSTRIAL | DLMS Meter | 3.3821 | 2.895 | 0.3466 | 3.0355 | 4.6273 | 5.6981
5889 | BMANZ | EAST | INDIRA NAGAR | E3 & E6 | NGEF_66 | 1130205901010105 | F07-FB'-STATION | COMMERCIAL | DLMS Meter | 3.2354 | 1.9793 | 1.156 | 2.0794 | 4.8116 | 7.4583
5890 | BMASZ | WEST | RR NAGAR | W2 & S1 | NIMHANS_66 | 1110101902010302 | F10-RV-ROAD | URBAN MIXED LOAD | DLMS Meter | 3.521 | 2.2042 | 1.168 | 2.353 | 6.3238 | 10.9219
5891 | BMASZ | SOUTH | JAYANAGAR | S1 & S2 | NIMHANS_66 | 1110101902010108 | F14-NIMHANS-HOSPITAL | HOSPITAL | DLMS Meter | 4.27 | 3.5205 | 0.6882 | 3.5818 | 1.7118 | 1.7118
5892 | BMASZ | WEST | RAJAJINAGAR | N1 & C1 | NRS_220 | 1140101901020303 | F07-F--II-BLOCK-&-C | URBAN MIXED LOAD | DLMS Meter | 2.9239 | 2.203 | 0.56788 | 2.356 | 6.4945 | 9.1217
5893 | BMASZ | WEST | RAJAJINAGAR | N2 & N10 | NRS_220 | 1140101901010301 | F18-VIJAYANAGR-TELE-EXCH. | URBAN MIXED LOAD | DLMS Meter | 5.5618 | 4.8143 | 0.372 | 5.1898 | 7.236 | 7.5207
5894 | BMASZ | SOUTH | JAYANAGAR | S5 & S9 | PADMANABHANAGAR_66 | 1110105901020304 | F10-YARAB-NAGAR | URBAN MIXED LOAD | DLMS Meter | 4.4526 | 4.081 | 0.135 | 4.3176 | 5.4782 | 10.2419
5895 | BMASZ | WEST | RR NAGAR | W2 & W8 | PADMANABHANAGAR_66 | 1110105901020305 | F11-TATA-SILK-FARM | URBAN MIXED LOAD | DLMS Meter | 3.5043 | 3.1534 | 0.21527 | 3.289 | 4.1236 | 14.9551
5896 | BMASZ | WEST | RR NAGAR | W8 & S9 | PADMANABHANAGAR_66 | 1110105901010202 | F13-SAROJA-COMPLEX | URBAN MIXED LOAD | DLMS Meter | 2.1633 | 2.0529 | 0 | 2.1633 | 5.1039 | 7.6564
5897 | BMANZ | EAST | SHIVAJINAGAR | E1 & E5 | POTTERYROAD_66 | 1130303901010103 | F03-CLARENCE-SCHOOL | URBAN MIXED LOAD | DLMS Meter | 3.7758 | 2.1693 | 1.3737 | 2.4022 | 9.6941 | 16.7378
5898 | BMANZ | EAST | SHIVAJINAGAR | E1 & E5 | POTTERYROAD_66 | 1130303901010108 | F15-E-SUB-DIVISION-RMU | URBAN MIXED LOAD | DLMS Meter | 3.2626 | 2.3413 | 0.7776 | 2.485 | 5.7831 | 11.4276
5899 | BMASZ | WEST | RR NAGAR | W7 & K1 | RAJARAJESHWARINAGAR_66 | 1140204901010304 | F10-GLOBAL-VILLAGE | INDUSTRIAL | DLMS Meter | 4.1478 | 3.8277 | 0.18109 | 3.9667 | 3.5042 | 21.9858
5900 | BMASZ | WEST | RR NAGAR | W6 & N2 | REMCO_66 | 1140203902010303 | F09-SKY-LINE-APARTMENT | URBAN MIXED LOAD | DLMS Meter | 2.9273 | 2.4519 | 0.28827 | 2.6391 | 7.0917 | 10.6989
5901 | BMASZ | WEST | RR NAGAR | W2 & W6 | REMCO_66 | 1140203902010304 | F11-V-V-PURAM | URBAN MIXED LOAD | DLMS Meter | 5.1632 | 4.307 | 0.55979 | 4.6034 | 6.4398 | 14.5506
5902 | BMASZ | WEST | RR NAGAR | W1 & W6 | REMCO_66 | 1140203902010305 | F12-MUNEESHWARA-BLOCK | URBAN MIXED LOAD | DLMS Meter | 3.5445 | 3.344 | 0.10141 | 3.4431 | 2.8768 | 15.8856
5903 | BMANZ | NORTH | MALLESHWARA | C2 & C6 | RMV_66 | 1120204902010101 | F01-MALLESHWARAM | URBAN MIXED LOAD | DLMS Meter | 6.1415 | 4.8025 | 1.026 | 5.1155 | 6.1194 | 6.5159
5904 | BMANZ | NORTH | HEBBAL | C4, C2 & C6 | RMV_66 | 1120204902020102 | F06-FIISC-SWITCHING-STATION | URBAN MIXED LOAD | DLMS Meter | 7.6199 | 1.9264 | 5.6354 | 1.9845 | 2.9137 | 5.3288
5905 | BMANZ | NORTH | MALLESHWARA | C2 & C6 | RMV_66 | 1120204902020103 | F08-ISRO&LG-HALLI | URBAN MIXED LOAD | DLMS Meter | 3.6623 | 1.4766 | 2.103 | 1.5593 | 5.3038 | 9.2999
5906 | BMANZ | NORTH | HEBBAL | C4 & C9 | RMV_66 | 1120204902020104 | F09-IISC-LAYOUT | DOMESTIC | DLMS Meter | 7.2876 | 3.553 | 3.5388 | 3.7488 | 5.2242 | 9.036
5907 | BMANZ | NORTH | HEBBAL | C4 & C9 | SAHAKARINAGAR_66 | 1120304901020106 | F06-KEMPA-PURA | URBAN MIXED LOAD | DLMS Meter | 3.2001 | 2.1246 | 0.91196 | 2.2881 | 7.1443 | 12.5692
5908 | BMANZ | NORTH | HEBBAL | C8 & C9 | SAHAKARINAGAR_66 | 1120304901020306 | F12-MLA-HOUSE | URBAN MIXED LOAD | DLMS Meter | 3.5269 | 2.54 | 0.8205 | 2.7064 | 6.1479 | 6.1479
5909 | BMASZ | SOUTH | JAYANAGAR | S1 & S6 | SARAKKI_66 | 1110104901010101 | F06-FJAYANAGAR-SWITCH-STATION | COMMERCIAL | DLMS Meter | 3.3185 | 3.1043 | 0 | 3.3185 | 6.4555 | 7.3336
5910 | BMASZ | SOUTH | HSR | S19 & S14 | SARAKKI_66 | 1110104901030503 | F15-JP-NAGAR-ND-PHASE | DOMESTIC | DLMS Meter | 2.4245 | 1.5933 | 0.73091 | 1.6936 | 5.9217 | 8.0367
5911 | BMANZ | EAST | WHITEFIELD | E4 & E12 | SHANTHINIKETHAN_66 | 1130202904010109 | F15-RELIANCE-COMMUNICATIONS,-SADARAMANGALA-I/A | URBAN MIXED LOAD | DLMS Meter | 11.6561 | 7.1254 | 4.2969 | 7.3592 | 3.1767 | 3.1767
5912 | CTAZ | TUMKUR | TIPTUR | CN HALLY | SHETYKERE_110 | 1320203904010105 | F05-KUPPUR-NJY | RURAL MIXED LOAD | DLMS Meter | 0.36543 | 0.3204 | 0.006 | 0.35943 | 10.8589 | 60.1917
5913 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903010106 | F10-KSRTC DEPO | DOMESTIC | DLMS Meter | 0.60791 | 0.32884 | 0.26931 | 0.3386 | 2.8826 | 15.8935
5914 | BMASZ | WEST | RAJAJINAGAR | N8 & K4 | SIRMV_LAYOUT_66 | 1140301903010106 | F09-RHCS-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 7.6276 | 4.7934 | 2.5575 | 5.0701 | 5.4574 | 5.4574
5915 | BMANZ | EAST | SHIVAJINAGAR | E9 & C8 | SOBHA_CITY_66 | 1130305904010105 | F03-CHOKKANAHALLI | COMMERCIAL | DLMS Meter | 6.1402 | 2.8926 | 2.9982 | 3.142 | 7.9365 | 10.0957
5916 | BMANZ | EAST | SHIVAJINAGAR | E9 & C8 | SOBHA_CITY_66 | 1130305904020105 | F10-SAMPIGEHALLI POLICE STATION | URBAN MIXED LOAD | DLMS Meter | 7.669 | 3.2336 | 4.0949 | 3.574 | 9.5266 | 14.4234
5917 | BMANZ | EAST | SHIVAJINAGAR | E9 & C8 | SOBHA_CITY_66 | 1130305904020104 | F11-BRIGADE NORTHRIDGE | URBAN MIXED LOAD | DLMS Meter | 7.0941 | 3.9987 | 2.8641 | 4.23 | 5.4667 | 9.0072
5918 | BMASZ | SOUTH | KORAMANGALA | S16 & S14 | STJOHNSWOOD_66 | 1110202902020101 | F01-BTM-I-STAGE | URBAN MIXED LOAD | DLMS Meter | 9.4155 | 5.4836 | 3.7253 | 5.6903 | 3.631 | 7.4775
5919 | BMASZ | SOUTH | KORAMANGALA | S16 & S14 | STJOHNSWOOD_66 | 1110202902020103 | F03-AXA | URBAN MIXED LOAD | DLMS Meter | 6.808 | 3.0781 | 3.5458 | 3.2623 | 5.6441 | 12.6027
5920 | BMASZ | SOUTH | KORAMANGALA | S16 & S14 | STJOHNSWOOD_66 | 1110202902020104 | F04-BTM-LAYOUTIDLE | URBAN MIXED LOAD | DLMS Meter | 7.457 | 2.3338 | 5.0247 | 2.4323 | 4.0518 | 10.6898
5921 | BMASZ | SOUTH | JAYANAGAR | S5 & S18 | SUBRAMANYAPURA_66 | 1110103901010106 | F08-BASAVANA GUDI | URBAN MIXED LOAD | DLMS Meter | 2.5223 | 2.2472 | 0.13252 | 2.3898 | 5.9661 | 15.3768
5922 | BRAZ | KOLAR | KOLAR | KOLAR URBAN | TAMAKA_66 | 1230101901010102 | F02-BASAVANATHA | DOMESTIC | DLMS Meter | 8.0798 | 3.5533 | 4.1855 | 3.8944 | 8.7576 | 9.9609
5923 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905010102 | F02-DADAPURA | AGRI | DLMS Meter | 0.44308 | 0.39879 | 0 | 0.44308 | 9.9964 | 9.9964
5924 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905010103 | F03-KANDIKERI | AGRI | DLMS Meter | 1.1906 | 1.072 | 0 | 1.1906 | 9.9611 | 9.9611
5925 | CTAZ | DAVANAGERE | HARIHARA | TELIGI | TELAGI_66 | 1310303905020302 | F05-ALAGILAWADA, | AGRI | DLMS Meter | 0.79142 | 0.6627 | 0.055 | 0.73642 | 10.0103 | 10.0103
5926 | BMANZ | EAST | VIDHANASOUDHA | W3 & W4 | TELECOMLAYOUT_66 | 1130101901020105 | F10-BALAKI-MANDI | URBAN MIXED LOAD | DLMS Meter | 3.359 | 2.1688 | 0.8996 | 2.4594 | 11.8179 | 14.077
5927 | BMASZ | WEST | RR NAGAR | W2 & W3 | TELECOMLAYOUT_66 | 1130101901020302 | F11-MYSORE-ROAD | URBAN MIXED LOAD | DLMS Meter | 1.5685 | 1.3932 | 0.007 | 1.5615 | 10.7761 | 10.7761
5928 | BMASZ | WEST | RR NAGAR | W2 & W3 | TELECOMLAYOUT_66 | 1130101901020303 | F12-ABB-RMU-JJR-NAGAR-POLICE-STATION | URBAN MIXED LOAD | DLMS Meter | 6.8468 | 5.8045 | 0.077 | 6.7698 | 14.2596 | 22.7998
5929 | BMANZ | EAST | VIDHANASOUDHA | W3 & W4 | TELECOMLAYOUT_66 | 1130101901020106 | F14-ETA-GARDENS | DOMESTIC | DLMS Meter | 2.3206 | 1.607 | 0.49438 | 1.8262 | 12.0051 | 38.1088
5930 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901010101 | F01-HALEPALYA | URBAN MIXED LOAD | DLMS Meter | 1.7286 | 1.1068 | 0.4754 | 1.2532 | 11.6819 | 11.6819
5931 | CTAZ | TUMKUR | TIPTUR | TIPTUR | TIPTUR_110 | 1320201901020101 | F07-TOWN | URBAN MIXED LOAD | DLMS Meter | 2.8136 | 2.2377 | 0.315 | 2.4986 | 10.4413 | 12.8962
5932 | BMASZ | WEST | RR NAGAR | W2 & W6 | VICTORIAHOSPITAL_66 | 1130103902020107 | F02-RMU06 | URBAN MIXED LOAD | DLMS Meter | 2.5974 | 1.845 | 0.63862 | 1.9587 | 5.8093 | 8.5807
5933 | BMASZ | WEST | RR NAGAR | W2, W3 & W4 | VICTORIAHOSPITAL_66 | 1130103902020108 | F07-BINNY-PET/DATTA-RMU | URBAN MIXED LOAD | DLMS Meter | 4.7134 | 2.1301 | 2.2816 | 2.4318 | 12.4082 | 17.4882
5934 | BMANZ | EAST | VIDHANASOUDHA | W4 & W5 | VICTORIAHOSPITAL_66 | 1130103902010301 | F08-JANATHA-RMU | URBAN MIXED LOAD | DLMS Meter | 3.0408 | 2.8931 | 0 | 3.0408 | 4.8568 | 4.8756
5935 | BMASZ | WEST | RR NAGAR | W2, W3 & W5 | VICTORIAHOSPITAL_66 | 1130103902010303 | F11-RMU-(JOLLY-MOHALLA) | URBAN MIXED LOAD | DLMS Meter | 3.9137 | 3.0886 | 0.30528 | 3.6084 | 14.4067 | 14.6613
5936 | BMASZ | WEST | RR NAGAR | W2 & W5 | VICTORIAHOSPITAL_66 | 1130103902020303 | F12-DENTAL-COLLEGE-RMU | URBAN MIXED LOAD | DLMS Meter | 2.9166 | 2.0558 | 0.77569 | 2.1409 | 3.9744 | 7.5981
5937 | BMASZ | WEST | RR NAGAR | W2 & W6 | VICTORIAHOSPITAL_66 | 1130103902020304 | F14-GANDHI-BAZAR-RMU | URBAN MIXED LOAD | DLMS Meter | 4.4621 | 3.1243 | 1.1671 | 3.295 | 5.1814 | 17.568
5938 | BMASZ | WEST | RAJAJINAGAR | N2 & N10 | VIJAYNAGAR_66 | 1140102902010103 | F08-FPRASHANTHNAGAR | URBAN MIXED LOAD | DLMS Meter | 4.716 | 3.2603 | 1.3149 | 3.4011 | 4.1401 | 10.5954
5939 | BMASZ | WEST | RR NAGAR | W6 & W7 | VRISHABAVATHY_66 | 1140203901020301 | F01-LEO-METAL | URBAN MIXED LOAD | DLMS Meter | 5.6593 | 2.0615 | 3.5012 | 2.1581 | 4.4745 | 4.4745
5940 | BMASZ | WEST | RR NAGAR | W6 & W7 | VRISHABAVATHY_66 | 1140203901020204 | F04-GOVT-PRESS | URBAN MIXED LOAD | DLMS Meter | 4.3508 | 1.5741 | 2.617 | 1.7338 | 9.2089 | 16.5056
5941 | BMASZ | WEST | RR NAGAR | W6 & W7 | VRISHABAVATHY_66 | 1140203901020207 | F09-MARAPPA-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 3.0596 | 2.7877 | 0.15211 | 2.9075 | 4.1188 | 4.1188
5942 | BMASZ | WEST | RR NAGAR | W6 & W7 | VRISHABAVATHY_66 | 1140203901020208 | F10-KENCHANAHALLI | URBAN MIXED LOAD | DLMS Meter | 6.0898 | 5.4543 | 0.30915 | 5.7807 | 5.6465 | 13.8064
5943 | BMASZ | WEST | RR NAGAR | W6 & W7 | VRISHABAVATHY_66 | 1140203901010103 | F13-PRESTIGE | DOMESTIC | DLMS Meter | 3.353 | 0.73408 | 2.5623 | 0.79062 | 7.1516 | 7.1516
5944 | BMANZ | NORTH | JALAHALLI | N9 & NELAMANGALA | WIDIA_66 | 1120102906010101 | F01-DASARAHALLI | URBAN MIXED LOAD | DLMS Meter | 2.493 | 2.3516 | 0 | 2.493 | 5.6732 | 12.5827
5945 | BMANZ | NORTH | PEENYA | N5 & NELAMANGALA | WIDIA_66 | 1120102906010103 | F02-CHOKKASANDRA | IDLE | DLMS Meter | 1.9203 | 1.888 | 0 | 1.9203 | 1.6814 | 4.3647
5946 | BMANZ | NORTH | JALAHALLI | N9 & NELAMANGALA | WIDIA_66 | 1120102906010106 | F04-VIJAYALAKSHMI LAYOUT | DOMESTIC | DLMS Meter | 0.3241 | 0.30996 | 0 | 0.3241 | 4.3611 | 20.7877
5947 | BMANZ | NORTH | JALAHALLI | N9 & NELAMANGALA | WIDIA_66 | 1120102906010104 | F05 M.S.RAMAIAH-LAYOUT | URBAN MIXED LOAD | DLMS Meter | 1.1297 | 1.0439 | 0 | 1.1297 | 7.5978 | 21.4157
5948 | BMANZ | NORTH | JALAHALLI | N9 & NELAMANGALA | WIDIA_66 | 1120102906010302 | F06-MANJUNATHA-NAGAR | URBAN MIXED LOAD | DLMS Meter | 2.2518 | 1.7956 | 0.25823 | 1.9936 | 9.933 | 20.5917
5949 | BMANZ | NORTH | JALAHALLI | N9 & NELAMANGALA | WIDIA_66 | 1120102906010303 | F07- SIDEDAHALLI | URBAN MIXED LOAD | DLMS Meter | 15.1933 | 2.8037 | 12.1638 | 3.0295 | 7.4541 | 24.4576
5950 | BMASZ | WEST | KENGERI | K2 & NELAMANGALA | WIDIA_66 | 1120102906010305 | F09-PAERLE-G | URBAN MIXED LOAD | DLMS Meter | 25.457 | 3.0508 | 22.0243 | 3.4327 | 11.1267 | 17.0098
5951 | CTAZ | DAVANAGERE | DAVANAGERE | DAVANAGERE RURAL & DAVANAGERE URBAN SUBDIVISION-2 | YARAGUNTA_66 | 1310103901010706 | F19-STP | INDUSTRIAL | DLMS Meter | 0.1708 | 0.1756 | 0 | 0.1708 | -2.8126 | 100
5952 | BMANZ | NORTH | HEBBAL | C8 & C9 | YELAHANKA_66 | 1120303901020304 | F08-,GKVK | URBAN MIXED LOAD | DLMS Meter | 5.7834 | 3.4342 | 2.086 | 3.6974 | 7.1197 | 14.0543
5953 | CTAZ | DAVANAGERE | CHITRADURGA | CHITRADURGA URBAN | CHITRADURGA_66 | 1310201901010105 | F05-BELAGATTA | AGRI | DLMS Meter | 0.711 | 0.55997 | 0.088689 | 0.62231 | 10.0185 | 10.0185
5954 | BRAZ | BANGALORE RURAL | NELAMANGALA | DABASPETE | TYAMAGONDLU_66 | 1210104901010106 | F10-DODDABELE-NJY | RURAL MIXED LOAD | DLMS Meter | 0.5778 | 0.3034 | 0.24 | 0.3378 | 10.1822 | 45.7365
5955 | BRAZ | KOLAR | KGF | KGF | ANDERSONPET_66 | 1230201901010103 | F03-ANDERSONPET | DOMESTIC | DLMS Meter | 2.1083 | 1.9123 | 0 | 2.1083 | 9.2972 | 44.2417
5956 | BRAZ | KOLAR | KGF | KGF | ANDERSONPET_66 | 1230201901020304 | F08-ROBERTSONPET | HOSPITAL | DLMS Meter | 0.93838 | 0.84604 | 0 | 0.93838 | 9.8405 | 27.8293
5957 | CTAZ | RAMANAGAR | MAGADI | KUDUR | KUDUR_66 | #N/A | F06-MADIGONDANAHALLI | #N/A | DLMS Meter | 0.8252 | 0.72142 | 0 | 0.8252 | 12.576 | 12.5882
5958 | BRAZ | SOUTH | KORAMANGALA | S7 | SUPREMEBUILDCAP_66F08 | #N/A | SUPREMEBUILDCAP_66F08 | #N/A | DLMS Meter | 0.70008 | 0.67488 | 0 | 0.70008 | 3.5992 | 8.7366
5959 | BRAZ | DAVANAGERE | DAVANAGERE | SANTEBENNUR | SHANTHISAGARA JACKWELL_EHT_66 | #N/A | 66 KV SHANTHISAGARA WATER WORKS | #N/A | DLMS Meter | 1.0462 | 1.0462 | 0 | 1.0462 | 0 | 97.6894
5960 | CTAZ | DAVANAGERE | CHITRADURGA | SRIRAMPURA | MATHOD_66 | #N/A | 66KV RAMCO CEMENTS | #N/A | DLMS Meter | 0.0594 | 0.0594 | 0 | 0.0594 | 0 | 0
5961 | CTAZ | RAMANAGAR | MAGADI | TAVAREKERE | TGHALLI_66F05-STAX | #N/A | TGHALLI_66F05-STAX | #N/A | DLMS Meter | 0.00067 | 0 | 0 | 0.00067 | 0 | #DIV/0!
5962 | BRAZ | DAVANAGERE | HARIHARA | TELIGI | HARAPPANAHALLI_66 | 1310303907010103 | F03-GOWRIHALLI | AGRI | DLMS Meter | 0.59364 | 0.49089 | 0.048 | 0.54564 | 10.0335 | 10.0335
5963 | BRAZ | DAVANAGERE | HARIHARA | TELIGI | HARAPPANAHALLI_66 | 1310303907010105 | F05-YALLAPURA | AGRI | DLMS Meter | 0.47103 | 0.42411 | 0 | 0.47103 | 9.9609 | 9.9609
5964 | BRAZ | DAVANAGERE | HARIHARA | TELIGI | NEELAGUNDA_220 | 1310303901010101 | F02-JITTINAKATTE | AGRI | DLMS Meter | 0.7848 | 0.6289 | 0.086 | 0.6988 | 10.0026 | 10.0026
5965 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KIADB_VNP_220 | 1320103905020103 | F10-MAHALAKSHMI | INDUSTRIAL | DLMS Meter | 0.0014 | 0 | 0.0014 | 0 | 0 | #DIV/0!
5966 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION1 | KORA_66 | 1320103902010103 | F10-MAJJIGEKEMPANAHALLI | AGRI | DLMS Meter | 0.9549 | 0.83042 | 0 | 0.9549 | 13.0358 | 13.0399
5967 | CTAZ | TUMKUR | TUMKUR | TUMKUR RURAL SUB DIVISION2 | MALLASANDRA_66 | 1320104902020302 | F14-KALLIPALYA | AGRI | DLMS Meter | 0 | 0.011704 | 0 | 0 | 0 | #DIV/0!
5968 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THANDAGA_110 | 1320202904010101 | F01-IDLE | IDLE | DLMS Meter | 0.01602 | 0.014812 | 0 | 0.01602 | 7.5406 | 7.5406
5969 | CTAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | KIADB HARDWARE PARK_220 | #N/A | 66KV BPH MINI IRRIGATION | #N/A | DLMS Meter | 1.9453 | 1.9453 | 0 | 1.9453 | 0 | 0
5970 | BRAZ | BANGALORE RURAL | HOSAKOTE | VIDYANAGAR | KIADB HARDWARE PARK_220 | #N/A | 66KV SHELL | #N/A | DLMS Meter | 4.4613 | 4.4613 | 0 | 4.4613 | 0 | 0.106
5971 | CTAZ | DAVANAGERE | HIRIYURU | HIRIYUR | PD KOTE_66 | #N/A | F07-KARIDASARAHALLI | #N/A | DLMS Meter | 0.15976 | 0 | 0 | 0.15976 | 0 | #DIV/0!
5972 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903030506 | F21-NJY BOOKSAGARA | RURAL MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5973 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_66 | 1320110903030507 | F22-NJY KAPANIPALYA | RURAL MIXED LOAD | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5974 | CTAZ | TUMKUR | MADHUGIRI | SIRA URBAN | SIRA_66 | 1320302903020507 | F18-PANJIGANAHALLI NJY | IDLE | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5975 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | THALKERE_110 | 1320202903010105 | F05-IDLE | IDLE | DLMS Meter | 0 | 0.001779 | 0 | 0 | 0 | #DIV/0!
5976 | CTAZ | TUMKUR | TIPTUR | TURUVEKERE | GOWRASAMUDRA_66 | 1310403901010101 | F01-IDLE | AGRI | DLMS Meter | 0.17362 | 0.019569 | 0.17362 | 0 | 0 | #DIV/0!
5977 | CTAZ | TUMKUR | TUMKUR | KYATSANDRA | URDIGERE_66 | #N/A | F05-SEETHAKALLU | #N/A | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5978 | BMANZ | EAST | INDIRA NAGAR | E10 | BAGHMANE_TECHPARK_66 | #N/A | F18-PURVA SEASONS | #N/A | DLMS Meter | 0 | 0 | 0 | 0 | 0 | #DIV/0!
5979 | BMANZ | EAST | INDIRA NAGAR | E11 | ITI_66 | #N/A | F01-BHATTARAHALLI | #N/A | DLMS Meter | 1.6888 | 0.12395 | 1.5602 | 0.12853 | 3.5596 | 3.5596
5980 | BMANZ | EAST | INDIRA NAGAR | E6 | B_STATION_66 | #N/A | F02-AUSTIN-CHECKPOST | #N/A | DLMS Meter | 0.3928 | 0 | 0 | 0.3928 | 0 | #DIV/0!
5981 | BMANZ | EAST | VIDHANASOUDHA | W3 & W4 | KANTEERVA_66 | #N/A | F07-BINNY-PET/DATTA-RMU | #N/A | DLMS Meter | 0.22852 | 0.22256 | 4e-05 | 0.22848 | 2.5902 | 9.5468
5982 | BMANZ | EAST | VIDHANASOUDHA | W5 | KANTEERVA_66 | #N/A | F03--SUNKALPET | #N/A | DLMS Meter | 1.035 | 0.75767 | 0.20522 | 0.82973 | 8.6854 | 14.2529
5983 | BMASZ | West | RR NAGAR | W2 | NATIONAL_COLLEGE_66 | #N/A | F03-5-TH-MAIN-ROAD-VIJAYA-ENCLAVE | #N/A | DLMS Meter | 1.6206 | 1.0454 | 0.5028 | 1.1178 | 6.4752 | 12.7285
5984 | BMASZ | South | JAYANAGAR | S6 | RBI_66 | #N/A | F16-BRIGADE-GARDENIA | #N/A | DLMS Meter | 0.27307 | 0.26384 | 0 | 0.27307 | 3.3812 | 3.4347
5985 | CTAZ | TUMKUR | KUNIGAL | KUNIGAL | ANCHEPALYA_220 | #N/A | 66KV VIJAYA STEEL | #N/A | DLMS Meter | 0 | 0.0288 | 0 | 0 | 0 | #DIV/0!
5986 | BMASZ | West | RR NAGAR | W6 | VRISHABAVATHY | #N/A | F17-BWSSB 2 | #N/A | DLMS Meter | 1.392 | 1.2958 | 0 | 1.392 | 6.9083 | 6.9744
5987 | BMASZ | South | KORAMANGALA | S7 | ADARSHA | #N/A | F14-RMZ | #N/A | DLMS Meter | 0.90926 | 0.48737 | 0.42 | 0.48926 | 0.38747 | 0.38747
5988 | BMASZ | South | KORAMANGALA | S7 | ADARSHA | #N/A | F8-RMZ-Campus 4C | #N/A | DLMS Meter | 0.27449 | 0.2665 | 0 | 0.27449 | 2.9125 | 2.9125
Reasons for high or low losses
1. Frequent Changeoverof feeders during faulty Conditions in Urban areas
2. Changeover of feeders during to OverHead to UG cable work
3.Input energy or sales is 0 due to cable fault or breaker problem resulting in complete shifting of load to other feeders
4.Inter ESCOMS sharing of feeders
5. Dedicated/Express feeders have Negative losses which may be either due to meter accuracy problems at Station and Consumer end or Reading of installations on 1st day of the month but feeder input readings are read of 31st midnight of previous month.
6.Collection Efficiency limited to 100%
Reasons for not audited
1.Feeders are be kept idle during the month
2.In the urban areas alternate source feeders are present which are used for emergency purposes.
3.Feeders which are newly created in mid/end of the month which will not be audited during the months
a