## Feb 19 Anx-1
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -I Form-I
RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR February'2019 OF FY 2018-19
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cummulative Outage due to Incoming Supply Failure( in Hrs) | Outage at 11 KV Level (in Hrs) |  |  | Reliability for Feb-2019 |  |  |  | Reliability for cummulative period From Apr-2018 |  |  |  | SAIFI & SAIDI of feeders for Feb-2019
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hr:mm:ss) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder Relaibility Index @ 11 KV feeder level in % | Cummulative Relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total No of consumers | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI |  |  |  |  | 227.2353
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 18 | 19=17/3 | 20=18/3
1 | Davangere | 35 | 32 | 9:56 | 54:25 | 251:35 | 51:53 | 303:28 | 313:24 | 8.9544 | 98.7097 | 98.6675 | 4579:17 | 130.8369 | 98.3872 | 98.3678 | 571 | 157116 | 313.4033 | 16.3143 | 8.9544 | 30 | 30 | 1012 | 157116 | 313.4033 | 28.9143 | 8.9544
2 | Chitradurga | 11 | 11 | 3:40 | 38:22 | 72:19 | 47:33 | 119:52 | 123:32 | 11.2303 | 98.3784 | 98.3288 | 2309:36 | 209.9636 | 97.4242 | 97.3807 | 793 | 42244 | 123.5333 | 72.0909 | 11.2303
3 | Tumkur | 30 | 30 | 12:00 | 147:04 | 255:00 | 115:00 | 370:00 | 382:00 | 12.7333 | 98.1647 | 98.1052 | 4663:48 | 155.46 | 98.1218 | 98.0606 | 586 | 98569 | 382 | 19.5333 | 12.7333
4 | BMAZ South | 756 | 597 | 201:56 | 2096:24 | 2782:37 | 2330:53 | 5113:30 | 5315:26 | 7.031 | 98.9935 | 98.9537 | 3084.8591 | 97.932 | 98.8129 | 98.7783 | 6975.0049 | 2553936 | 5315.4333 | 9.2262 | 7.031
5 | BMAZ North | 677 | 625 | 267:20 | 2322:29 | 3670:50 | 3783:17 | 7454:07 | 7721:27 | 11.4054 | 98.3615 | 98.3028 | 3168.234 | 112.3155 | 98.6417 | 98.5989 | 5762 | 2681397 | 7721.445 | 8.5111 | 11.4054
4 | BMAZ | 1433 | 1222 | 469:16 | 4418:53 | 6453:27 | 6114:10 | 12567:37 | 13036:53 | 9.0976 | 98.6949 | 98.6462 | 6253.0931 | 104.7273 | 98.732 | 98.6935 | 12737.0049 | 5235333 | 13036.8783 | 8.8883 | 9.0976
5 | Ramanagara | 4 | 4 | 0:18 | 35:00 | 15:38 | 11:00 | 26:38 | 26:56 | 6.7333 | 99.0092 | 98.998 | 477:14 | 119.3083 | 98.6208 | 98.5116 | 91 | 38846 | 26.9333 | 22.75 | 6.7333
6 | Kolar | 17 | 17 | 123:40 | 436:08 | 161:50 | 109:21 | 271:11 | 394:51 | 23.2265 | 97.6262 | 96.5437 | 4858:50 | 285.8138 | 96.7545 | 96.4345 | 541 | 51234 | 394.85 | 31.8235 | 23.2265
7 | CBPura | 9 | 9 | 92:20 | 346:55 | 142:10 | 27:00 | 169:10 | 261:30 | 29.0556 | 97.2029 | 95.6763 | 2383:24 | 264.8223 | 97.1772 | 96.6963 | 291 | 55866 | 261.5 | 32.3333 | 29.0556
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the month]
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Feeders x 24 hrs x No. of days in the Month]
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 14} x 100 / [Total No of
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a
Note: One new feeder in Sir MV Station in Kengeri Division is charged during Feb'2019.
| Assistant Executive Engineer(Ele)-3 | [12 empty] | Deputy General Manager(Ele)
| Operations-3 | [12 empty] | Operation-3
Chief General Manager(Ele)
Operations
[6 empty] | 26:49 | 12:01
[6 empty] | 150:58 | 84:53
[6 empty] | 148:29 | 35:55
There was a maintainence work in 66/11KV Tamaka ,Vemgal ,Dalasanuru , Kyalanuru , Somayajalahalli stations, hence Incoming Supply Failure is more in Kolar division. However, change over has been arranged & hence less interruptions affected to consumers.
There was a maintainence work in 66/11kV Tubagere, D.Cross stations. However, hence Outage due to Incoming Supply Failure is more in Doddaballapura Taluk. However, change over has been arranged & hence less interruptions affected to consumers
31

## Feb19 ANX11
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -II Form-II
RELIABILITY INDICES FOR TOWNS AND CITIES IN BESCOM FOR February-2019 OF FY 2018-19
Sl. No | Name of the Towns & Cities | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure(In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Feb-2019 |  |  |  | Reliability for Cummulative period From Apr-2018 |  |  |  | SAIFI & SAIDI of feeders for Feb-2019
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hr:mm:ss) | Outage duration per feeder(in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder Relaibility Index @ 11 KV feeder level in % | Cummulative Relaibility of supply of Power to consumers | Total No. of Feeder Interruptions | Total No. of Consumer | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 18 | 19=17/3 | 20=18/3
1 | Jagalur | 1 | 1 | 3:05 | 57:15 | 11:33 | 1:36 | 13:09 | 16:14 | 16.2333 | 98.0432 | 97.5843 | 231:09 | 231.15 | 97.8306 | 97.1164 | 35 | 7693 | 16.2333 | 35 | 16.2333
2 | Channagiri | 1 | 1 | 6:55 | 225:25 | 19:03 | 0:33 | 19:36 | 26:31 | 26.5167 | 97.0833 | 96.0541 | 524:25 | 524.4167 | 96.27 | 93.4579 | 65 | 7989 | 26.5167 | 65 | 26.5167
3 | Harihara | 11 | 11 | 2:15 | 21:55 | 153:36 | 24:04 | 177:40 | 179:55 | 16.3561 | 97.5965 | 97.5661 | 1844:09 | 167.65 | 97.9334 | 97.9086 | 307 | 14402 | 179.9167 | 27.9091 | 16.3561
4 | Honnali | 2 | 2 | 1:20 | 16:03 | 39:55 | 2:15 | 42:10 | 43:30 | 21.75 | 96.8626 | 96.7634 | 422:13 | 211.1083 | 97.4665 | 97.3664 | 70 | 12996 | 43.5 | 35 | 21.75
5 | Harapanahalli | 4 | 4 | 0:30 | 6:39 | 49:05 | 17:10 | 66:15 | 66:45 | 16.6875 | 97.5353 | 97.5167 | 599:44 | 149.9333 | 98.1503 | 98.1296 | 58 | 3931 | 66.75 | 14.5 | 16.6875
6 | Holalkere | 1 | 1 | 2:10 | 19:13 | 13:09 | 9:33 | 22:42 | 24:52 | 24.8667 | 96.622 | 96.2996 | 315:58 | 315.9667 | 96.298 | 96.0583 | 81 | 4636 | 24.8667 | 81 | 24.8667
7 | Hosadurga | 2 | 2 | 3:15 | 42:15 | 24:53 | 21:14 | 46:07 | 49:22 | 24.6833 | 96.5687 | 96.3269 | 622:48 | 311.4 | 96.3788 | 96.1153 | 143 | 11625 | 49.3667 | 71.5 | 24.6833
8 | Hiriyur | 3 | 3 | 19:46 | 95:16 | 28:33 | 10:23 | 38:56 | 58:42 | 19.5639 | 98.0688 | 97.0887 | 743:53 | 247.9586 | 97.3028 | 96.9067 | 152 | 3495 | 58.6918 | 50.6667 | 19.5639
9 | Challakere | 5 | 5 | 20:31 | 98:56 | 40:45 | 13:34 | 54:19 | 74:50 | 14.9671 | 98.3834 | 97.7728 | 1080:28 | 216.0917 | 97.5511 | 97.3042 | 231 | 17818 | 74.8356 | 46.2 | 14.9671
10 | Molakalmuru | 1 | 1 | 12:10 | 58:37 | 1:57 | 0:35 | 2:32 | 14:42 | 14.6927 | 99.623 | 97.8136 | 241:18 | 241.3056 | 97.721 | 96.9897 | 18 | 896 | 14.6927 | 18 | 14.6927
11 | Tumkur | 6 | 6 | 19:30 | 166:22 | 113:21 | 91:06 | 204:27 | 223:57 | 37.325 | 94.9293 | 94.4457 | 2192:51 | 365.4736 | 95.7866 | 95.4407 | 325 | 25893 | 223.95 | 54.1667 | 37.325
12 | Tiptur | 11 | 11 | 26:00 | 310:21 | 315:00 | 165:00 | 480:00 | 506:00 | 46 | 93.5065 | 93.1548 | 4299:20 | 390.8481 | 95.4761 | 95.1242 | 903 | 33646 | 506 | 82.0909 | 46
13 | Madhugiri | 8 | 8 | 37:50 | 497:48 | 89:03 | 38:36 | 127:39 | 165:29 | 20.6854 | 97.6256 | 96.9218 | 2873:04 | 359.1342 | 96.2961 | 95.5198 | 330 | 47990 | 165.4833 | 41.25 | 20.6854
14 | Srinivaspura | 4 | 4 | 6:45 | 51:00 | 52:00 | 24:50 | 76:50 | 83:35 | 20.8958 | 97.1416 | 96.8905 | 1278:05 | 319.5208 | 96.173 | 96.014 | 152 | 12335 | 83.5833 | 38 | 20.8958
15 | KGF | 30 | 30 | 7:04 | 36:05 | 418:30 | 446:20 | 864:50 | 871:54 | 29.0633 | 95.7102 | 95.6751 | 8219:58 | 273.9989 | 96.5969 | 96.5819 | 998 | 99066 | 871.9 | 33.2667 | 29.0633
16 | CB Pura | 11 | 11 | 17:05 | 602:05 | 56:55 | 47:03 | 103:58 | 121:03 | 11.0045 | 98.5935 | 98.3624 | 2273:09 | 206.65 | 98.1049 | 97.422 | 233 | 41122 | 121.05 | 21.1818 | 11.0045
17 | Chintamani | 15 | 15 | 5:50 | 168:22 | 135:20 | 53:48 | 189:08 | 194:58 | 12.9978 | 98.1237 | 98.0658 | 3998:23 | 266.5589 | 96.8147 | 96.6747 | 259 | 37305 | 194.9667 | 17.2667 | 12.9978
18 | Devanahalli | 60 | 60 | 301:46 | 2031:50 | 808:15 | 859:55 | 1668:10 | 1969:56 | 32.8322 | 95.8627 | 95.1143 | 18217:15 | 303.6208 | 96.6348 | 96.2123 | 122 | 67005 | 1969.9333 | 2.0333 | 32.8322
19 | Hosakote | 61 | 61 | 109:48 | 2760:24 | 769:56 | 260:41 | 1030:37 | 1140:25 | 18.6954 | 97.4858 | 97.218 | 18803:11 | 308.2488 | 96.7191 | 96.1546 | 107 | 91997 | 1140.4167 | 1.7541 | 18.6954
20 | Nelamangala | 63 | 63 | 62:07 | 929:36 | 552:03 | 255:49 | 807:52 | 869:59 | 13.8093 | 98.0918 | 97.9451 | 14942:30 | 237.1825 | 97.2252 | 97.0411 | 83 | 109352 | 869.9833 | 1.3175 | 13.8093
21 | Doddaballapura | 53 | 53 | 41:16 | 1095:42 | 470:42 | 984:12 | 1454:54 | 1496:10 | 28.2296 | 95.915 | 95.7992 | 14649:50 | 276.4119 | 96.8097 | 96.5517 | 103 | 87097 | 1496.1667 | 1.9434 | 28.2296
22 | Bangalore south | 20 | 20 | 60:45 | 599:41 | 246:48 | 60:12 | 307:00 | 367:45 | 18.3875 | 97.7158 | 97.2638 | 5546:09 | 277.3075 | 96.9146 | 96.5406 | 628 | 6238 | 367.75 | 31.4 | 18.3875
23 | Magadi | 12 | 12 | 38:20 | 664:11 | 247:50 | 79:17 | 327:07 | 365:27 | 30.4542 | 95.9435 | 95.4681 | 3339:11 | 278.2653 | 97.2191 | 96.5286 | 233 | 38386 | 365.45 | 19.4167 | 30.4542
24 | Anekal | 127 | 127 | 621:41 | 5796:22 | 1239:10 | 705:28 | 1944:38 | 2566:19 | 20.2072 | 97.7214 | 96.993 | 1459.3014 | 275.7735 | 97.1291 | 96.5597 | 3651 | 238089 | 2566.3167 | 28.748 | 20.2072
25 | Ramanagara | 35 | 35 | 0:47 | 120:26 | 313:53 | 107:34 | 421:27 | 422:14 | 12.0638 | 98.2081 | 98.2048 | 6585:45 | 188.1643 | 97.6956 | 97.6526 | 985 | 5671 | 422.2333 | 28.1429 | 12.0638
26 | Channapatna | 7 | 7 | 10:31 | 288:38 | 130:35 | 19:28 | 150:03 | 160:34 | 22.9381 | 96.8102 | 96.5866 | 1969:13 | 281.3167 | 97.0049 | 96.4906 | 652 | 35024 | 160.5667 | 93.1429 | 22.9381
27 | Kanakapura | 22 | 22 | 5:50 | 81:49 | 241:20 | 79:17 | 320:37 | 326:27 | 14.8386 | 97.8313 | 97.7919 | 4021:36 | 182.8 | 97.766 | 97.7196 | 1926 | 19922 | 326.45 | 87.5455 | 14.8386
|  | 576 | 576 | 60.2022 | #REF! | 274.2986 | 182.4812 | 10962:43 | 516.9821 | 21.5409 | 97.1678 | 96.7945 | 7097.2066 | 295.7169 | #REF! | 96.3109 |  |  |  |  | 0
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in in a month) | [20 empty] | #DIV/0!
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month) | [20 empty] | #DIV/0!
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [20 empty] | #DIV/0!
#DIV/0!
#DIV/0!
Note: 1. In Devanahalli division, 4 feeders were newly added in the month of Feb-18.

## Feb19- ANX111
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Annexure -III Form-III
RELIABILITY INDICES FOR RURAL AREAS IN BESCOM FOR February-2019 OF FY 2018-19
Sl. No | Name of the Division | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cummulative Outage due to Incoming Supply Failure ( in Hrs) | Outage at 11 KV Level(in Hrs) |  |  | Reliability for Feb-2019 |  |  |  | Reliability for cummulative period From Apr-2018 |  |  |  | SAIFI & SAIDI of feeders for Feb-2019
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hr:mm:ss) | Outage duration per feeder (in Hrs/Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cummulative outage duration of all feeders (In Hrs) | Cummulative outage duration of all feeders (In Hrs/Feeder) | Cummulative feeder relaibility Index @ 11 KV feeder level in % | Cummulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total No. of Consumers | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2a | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 18 | 19=17/3 | 20=18/3
1 | Davanagere | 269 | 267 | 274:34 | 2578:38 | 4673:51 | 1486:11 | 6160:02 | 6434:36 | 17.9403 | 96.5923 | 96.4404 | 3841.4993 | 342.736 | 95.8439 | 95.7244 | 11683.2674 | 265364 | 6434.5967 | 43.4322 | 23.9204
2 | Harihara | 197 | 197 | 15:55 | 146:55 | 3864:18 | 1203:12 | 5067:30 | 5083:25 | 19.3531 | 96.1721 | 96.1601 | 3220.9187 | 392.3962 | 95.1141 | 95.1048 | 6271 | 207717 | 5083.4167 | 31.8325 | 25.8041
3 | Chitradurga | 178 | 178 | 91:45 | 769:03 | 1344:30 | 2461:46 | 3806:16 | 3898:01 | 16.4242 | 96.8179 | 96.7412 | 2248.0854 | 303.1126 | 96.2726 | 96.2187 | 12717 | 218511 | 3898.0167 | 71.4438 | 21.899
4 | Hiriyur | 212 | 212 | 196:01 | 666:05 | 3607:05 | 1152:57 | 4760:02 | 4956:03 | 17.5332 | 96.6588 | 96.5212 | 2669.2201 | 302.1759 | 96.2695 | 96.2303 | 6109 | 248901 | 4956.0437 | 28.816 | 23.3776
5 | Tumkur | 305 | 305 | 68:00 | 977:00 | 3125:00 | 2856:00 | 5981:00 | 6049:00 | 14.8746 | 97.0819 | 97.0487 | 3479.3025 | 273.7812 | 96.6245 | 96.5846 | 8532 | 262246 | 6049 | 27.9738 | 19.8328
6 | Tiptur | 194 | 194 | 58:00 | 653:00 | 2185:00 | 3856:00 | 6041:00 | 6099:00 | 23.5786 | 95.3662 | 95.3217 | 2847.0961 | 352.2181 | 95.6481 | 95.6061 | 6523 | 204762 | 6099 | 33.6237 | 31.4381
7 | Madhugiri | 307 | 307 | 72:00 | 1215:07 | 3056:00 | 1629:00 | 4685:00 | 4757:00 | 11.6213 | 97.7291 | 97.6942 | 3614.3093 | 282.5519 | 96.5245 | 96.4752 | 6894 | 400356 | 4757 | 22.456 | 15.4951
8 | Kunigal | 105 | 105 | 36:00 | 444:35 | 1952:00 | 1245:00 | 3197:00 | 3233:00 | 23.0929 | 95.4691 | 95.4181 | 1751.3285 | 400.3037 | 95.059 | 95.0062 | 2954 | 45623 | 3233 | 28.1333 | 30.7905
9 | Kolar | 152 | 152 | 1323:21 | 7268:59 | 1193:39 | 2968:55 | 4162:34 | 5485:55 | 27.0687 | 95.9248 | 94.6292 | 2619.3681 | 413.5844 | 95.4371 | 94.8405 | 3481 | 149061 | 5485.9167 | 22.9013 | 36.0916
10 | KGF | 197 | 183 | 13:28 | 156:56 | 1996:40 | 4510:30 | 6507:10 | 6520:38 | 24.8247 | 95.0846 | 95.0745 | 3137.4028 | 382.2217 | 95.2417 | 95.2318 | 5252 | 292779 | 6520.6333 | 26.6599 | 33.0997
11 | CB Pura | 194 | 194 | 1009:20 | 9842:36 | 1457:32 | 976:58 | 2434:30 | 3443:50 | 13.3138 | 98.1326 | 97.3584 | 1931.6771 | 238.9704 | 97.6518 | 97.0188 | 4115 | 210619 | 3443.8333 | 21.2113 | 17.7517
12 | Chintamani | 147 | 147 | 26:45 | 387:22 | 1338:02 | 476:45 | 1814:47 | 1841:32 | 9.3956 | 98.1629 | 98.1358 | 1368.8403 | 223.4841 | 97.2449 | 97.212 | 1240 | 193270 | 1841.5336 | 8.4354 | 12.5274
13 | Devanahalli | 33 | 33 | 195:37 | 984:23 | 582:48 | 498:32 | 1081:20 | 1276:57 | 29.0216 | 95.1239 | 94.2417 | 11914:43 | 361.052 | 95.868 | 95.4959 | 1293 | 36681 | 1276.95 | 39.1818 | 38.6955
14 | Hosakote | 32 | 32 | 57:10 | 1125:30 | 120:41 | 95:39 | 216:20 | 273:30 | 6.4102 | 98.994 | 98.7281 | 7128:00 | 222.75 | 97.66 | 97.2212 | 624 | 29484 | 273.5 | 19.5 | 8.5469
15 | Nelamangala | 15 | 15 | 32:09 | 206:26 | 157:59 | 156:47 | 314:46 | 346:55 | 17.3458 | 96.8773 | 96.5584 | 3586:14 | 239.0822 | 97.1891 | 97.0174 | 25 | 23101 | 346.9167 | 1.6667 | 23.1278
16 | Doddaballapura | 39 | 39 | 43:22 | 1016:46 | 311:21 | 345:23 | 656:44 | 700:06 | 13.4635 | 97.4941 | 97.3287 | 8581:59 | 220.0509 | 97.5801 | 97.2549 | 95 | 32827 | 700.1 | 2.4359 | 17.9513
17 | Magadi | 42 | 42 | 14:41 | 286:29 | 526:21 | 606:23 | 1132:44 | 1147:25 | 20.4896 | 95.9866 | 95.9346 | 12625:46 | 300.6135 | 96.3349 | 96.2498 | 2193 | 52475 | 1147.4167 | 52.2143 | 27.3194
18 | Chandapura | 19 | 19 | 41:24 | 140:47 | 155:53 | 74:47 | 230:40 | 272:04 | 10.7395 | 98.1934 | 97.8692 | 4377:48 | 230.4105 | 97.2181 | 97.1256 | 368 | 45213 | 272.0667 | 19.3684 | 14.3193
19 | Ramanagara | 39 | 39 | 7:17 | 123:52 | 428:59 | 275:35 | 704:34 | 711:51 | 13.6894 | 97.3116 | 97.2838 | 12460:25 | 319.4978 | 96.0539 | 96.0142 | 3481 | 37532 | 711.8503 | 89.2564 | 18.2526
20 | Channapatna | 47 | 47 | 34:05 | 334:34 | 335:28 | 342:36 | 678:04 | 712:09 | 11.3641 | 97.8531 | 97.7452 | 16544:26 | 352.0092 | 95.6975 | 95.6087 | 4965 | 52050 | 712.15 | 105.6383 | 15.1521
21 | Kanakapura | 110 | 110 | 27:02 | 283:56 | 1901:45 | 1649:28 | 3551:13 | 3578:15 | 24.3972 | 95.1959 | 95.1593 | 1389.5514 | 303.1749 | 96.2501 | 96.2179 | 1287 | 101838 | 3578.25 | 11.7 | 32.5295
|  | 2246 | 2230 | 138.9271 | #REF! | 1062.4576 | 1002.1034 | 2064.561 | 2203.4881 | 17.6593 | 96.7171 | 96.4962 | 29631.1167 | 316.6281 | #REF! | 96.05 |  |  |  | 0
* Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the Month] - [outage duration of all 11kv feeders during the month in hrs as in column 8]} x 100 / [Total No of 11kv Feeders x 24 hrs x No. of days in | [19 empty] | #DIV/0!
#DIV/0!
**Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the Month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs as in column 9]} x 100 / [Total No of Fee | [19 empty] | #DIV/0!
#DIV/0!
#DIV/0!
* Cummulative Feeder Reliabilty Index at 11kv feeder level = {[Total No of 11kv Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [outage duration of all 11kv feeders during the year in hrs as in column 13} x 100 / [Total No of | [19 empty] | #DIV/0!
#DIV/0!
**Cummulative Reliabilty of supply of power to consumers= {[Total No of Feeders x 24 hrs x No. of days in the year from Apr-09 to current month] - [Sum of outage duration including outage in higher voltages along with 11kv Outage during the month in hrs a | [19 empty] | #DIV/0!
#DIV/0!
Note : IN KGF DIVISION, NEW FEEDER OF TEKAL MUSS -F11 NOOTUVE FEEDER HAS BEEN ADDED