## Annexure 1
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR THE MONTH OF MAY-2019 OF FY 2019-20
ANX-I
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY… | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for MAY-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=18/4
1 | Davangere | 36 | 33 | 3:54 | 6:00 | 432:01 | 200:58 | 632:59 | 638:59 | 17:45 | 97.6367 | 97.6143 | 945:23 | 26:16 | 98.2176 | 98.2062 | 1025 | 58962 | 638.97 | 31.0606 | 19.3627 | 24:00 | 0.96667
2 | Chitradurga | 11 | 11 | 2:50 | 5:00 | 112:17 | 73:35 | 185:52 | 190:52 | 17:21 | 97.7289 | 97.6678 | 370:39 | 33:42 | 97.7294 | 97.6984 | 947 | 42244 | 190.87 | 86.0909 | 17.3518 | 24:00 | 0.86667
3 | Tumkur | 30 | 30 | 14:23 | 24:23 | 214:20 | 224:26 | 438:47 | 463:10 | 15:26 | 98.0341 | 97.9249 | 916:35 | 30:33 | 97.9686 | 97.9131 | 697 | 98569 | 463.17 | 23.2333 | 15.439 | 24:00 | 0.16667
4 | BMAZ, North | 679 | 630 | 753:18 | 1005:04 | 180:13 | 1870:33 | 2050:46 | 3055:50 | 4:30 | 99.594 | 99.3951 | 13560:47 | 19:58 | 98.7369 | 98.6358 | 5735 | 1209160 | 3055.83 | 9.1032 | 4.8505 | 24:00 | 0.83333 | 0.63333
5 | BMAZ, South | 766 | 619 | 409:11 | 621:06 | 4108:09 | 7198:19 | 11306:28 | 11927:34 | 15:34 | 98.0161 | 97.9071 | 22519:33 | 29:24 | 98.0473 | 97.9919 | 14052 | 2566358 | 11927.55 | 22.7011 | 19.2691 | 24:00 | 0.55
5 | Ramanagara | 4 | 4 | 1:50 | 3:40 | 21:15 | 9:30 | 30:45 | 34:25 | 8:36 | 98.9667 | 98.8435 | 67:32 | 16:53 | 98.9094 | 98.8468 | 2 | 169870 | 34.42 | 0.5 | 8.605 | 24:00 | 0.41667 | 2
6 | Kolar | 17 | 17 | 4:25 | 14:55 | 197:10 | 422:26 | 619:36 | 634:31 | 37:19 | 95.1012 | 94.9833 | 1054:01 | 62:00 | 95.8249 | 95.765 | 924 | 51239 | 634.52 | 54.3529 | 37.3247 | 24:00 | 0.51667 | 726
7 | CBPura | 9 | 9 | 76:01 | 76:01 | 136:01 | 80:15 | 216:16 | 292:17 | 32:29 | 96.7702 | 95.635 | 496:03 | 55:07 | 96.8121 | 96.2352 | 440 | 55861 | 292.28 | 48.8889 | 32.4756 | 24:00 | 0.28333 | 350
NOTE:
1. 02 New Feeders were added in BMAZ, South. 02 nos of feeders ( F1, F2) emanating from 66/11 KV "B" Station.
2. 02 New Feeders were added in BMAZ, North. 02 nos of feeders ( F25, F26) emanating from 66/11 KV Manyatha Station.
3. 01 New NJY Feeder F21 (Taralaballu) was added to Davanagere district head Quarters emanating from 66/11 KV SRS Davanagere.
Assitant General Manager-3(Elec) | [6 empty] | Chief General Manager(Elec) | [8 empty] | Deputy General Manager(Elec)
Operations-3, BESCOM | [6 empty] | Operations, BESCOM | [8 empty] | Operations-3,BESCOM

## Annexure II
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
B. RELIABILITY INDICES FOR TOWNS AND CITIES BESCOM FOR THE MONTH OF MAY-2019 OF FY 2019-20
ANX-II
Sl. No | Name of the TOWNS & CITIES | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY… | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for MAY-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=18/4
1 | Jagalur | 1 | 1 | 14:40 | 19:55 | 8:21 | 2:12 | 10:33 | 25:13 | 25:13 | 98.582 | 96.6107 | 38:34 | 38:34 | 98.7261 | 97.3657 | 31 | 7782 | 25.21 | 31 | 25.21 | 24:00 |  | 0.21667 | 146:58
2 | Channagiri | 1 | 1 | 8:15 | 27:55 | 20:24 | 2:30 | 22:54 | 31:09 | 31:09 | 96.922 | 95.8132 | 64:34 | 64:34 | 97.4966 | 95.5897 | 92 | 8134 | 31.15 | 92 | 31.15 | 24:00 |  | 0.15 | 285:43
3 | Harihara | 11 | 11 | 2:25 | 5:40 | 118:50 | 56:38 | 175:28 | 177:53 | 16:10 | 97.856 | 97.8264 | 447:20 | 40:40 | 97.2574 | 97.2222 | 441 | 14402 | 177.88 | 40.0909 | 16.1709 | 24:00 |  | 0.88333 | 169:27
4 | Honnali | 2 | 2 | 1:20 | 2:25 | 15:50 | 5:30 | 21:20 | 22:40 | 11:20 | 98.5663 | 98.4767 | 46:00 | 23:00 | 98.5115 | 98.429 | 86 | 12996 | 22.67 | 43 | 11.335 | 24:00 |  | 0.66667
5 | Harapanahalli | 4 | 4 | 0:55 | 2:05 | 22:25 | 17:30 | 39:55 | 40:50 | 10:12 | 98.6587 | 98.6279 | 88:25 | 22:06 | 98.5257 | 98.4902 | 86 | 3931 | 40.83 | 21.5 | 10.2075 | 24:00 |  | 0.83333 | 395:34
6 | Holalkere | 1 | 1 | 2:15 | 3:50 | 16:47 | 11:55 | 28:42 | 30:57 | 30:57 | 96.1425 | 95.8401 | 60:29 | 60:29 | 96.1305 | 95.8686 | 95 | 4636 | 30.95 | 95 | 30.95 | 24:00 |  | 0.95 | 714:19
7 | Hosadurga | 2 | 2 | 2:40 | 4:15 | 32:09 | 25:58 | 58:07 | 60:47 | 30:23 | 96.0943 | 95.9151 | 118:59 | 59:30 | 96.0815 | 95.9364 | 171 | 11625 | 28.78 | 85.5 | 14.39 | 24:00 |  | 0.78333 | 412:12
8 | Hiriyur | 3 | 3 | 3:34 | 5:58 | 16:55 | 31:41 | 48:36 | 52:11 | 17:24 | 97.8226 | 97.6624 | 91:38 | 30:33 | 98.0495 | 97.9138 | 226 | 3495 | 52.17 | 75.3333 | 17.39 | 24:00 |  | 0.16667
9 | Challakere | 5 | 5 | 3:43 | 6:11 | 97:12 | 57:32 | 154:44 | 158:27 | 31:41 | 95.8405 | 95.7407 | 233:48 | 46:46 | 96.8905 | 96.806 | 460 | 17818 | 158.43 | 92 | 31.686 | 24:00 |  | 0.43333
10 | Molakalmuru | 1 | 1 | 2:12 | 3:40 | 13:12 | 16:38 | 29:50 | 32:02 | 32:02 | 95.9901 | 95.6944 | 46:49 | 46:49 | 97.0526 | 96.8021 | 106 | 896 | 32.03 | 106 | 32.03 | 24:00 |  | 0.75
11 | Tumkur | 6 | 6 | 12:03 | 31:43 | 121:30 | 115:03 | 236:33 | 248:36 | 41:26 | 94.7009 | 94.431 | 395:34 | 65:56 | 95.8578 | 95.4967 | 594 | 25893 | 248.6 | 99 | 41.4333 | 24:00 |  | 0.45
12 | Tiptur | 11 | 11 | 21:36 | 48:36 | 208:15 | 198:45 | 407:00 | 428:36 | 38:58 | 95.0269 | 94.763 | 714:19 | 64:56 | 95.8662 | 95.5644 | 1031 | 33646 | 428.6 | 93.7273 | 38.9636 | 24:00
13 | Madhugiri | 8 | 8 | 29:45 | 68:45 | 155:02 | 57:58 | 213:00 | 242:45 | 30:21 | 96.4214 | 95.9215 | 412:12 | 51:32 | 97.0675 | 96.4805 | 468 | 47990 | 242.75 | 58.5 | 30.3438 | 24:00
14 | Srinivaspura | 4 | 4 | 6:10 | 11:10 | 65:40 | 149:55 | 215:35 | 221:45 | 55:26 | 92.7559 | 92.5487 | 352:20 | 88:05 | 94.1741 | 93.9834 | 291 | 12339 | 221.75 | 72.75 | 55.4375 | 24:00 | 52.75 | 32.6458
15 | KGF | 30 | 30 | 2:18 | 3:44 | 658:10 | 584:30 | 1242:40 | 1244:58 | 41:30 | 94.4325 | 94.4222 | 1958:34 | 65:17 | 95.5491 | 95.5406 | 1467 | 99066 | 1244.9667 | 48.9 | 41.4989 | 24:00 | 47.8667 | 23.7867
16 | CB Pura | 11 | 11 | 25:55 | 42:45 | 187:22 | 192:32 | 379:54 | 405:49 | 36:54 | 95.358 | 95.0413 | 551:09 | 50:06 | 96.843 | 96.5776 | 715 | 41122 | 405.8167 | 65 | 36.8924 | 24:00 | 33.3636 | 13.2122
17 | Chintamani | 15 | 15 | 7:35 | 14:19 | 433:40 | 195:04 | 628:44 | 636:19 | 42:25 | 94.3662 | 94.2982 | 932:14 | 62:09 | 95.82 | 95.7549 | 605 | 37305 | 636.3167 | 40.3333 | 42.4211 | 24:00 | 28.8 | 19.7278
18 | Devanahalli | 60 | 60 | 218:28 | 346:57 | 1908:03 | 6502:17 | 8410:20 | 8628:48 | 143:49 | 81.1596 | 80.6703 | 17167:37 | 286:08 | 80.8508 | 80.4558 | 305 | 66640 | 8628.8 | 5.0833 | 143.8133 | 24:00 | 1.6833 | 142.3136
19 | Hosakote | 61 | 61 | 153:58 | 198:25 | 979:18 | 1019:50 | 1999:08 | 2153:06 | 35:18 | 95.5951 | 95.2558 | 4196:41 | 68:48 | 95.5229 | 95.3007 | 199 | 66443 | 2153.1 | 3.2623 | 35.2967 | 24:00 | 1.2623 | 33.5014
20 | Nelamangala | 66 | 66 | 18:53 | 37:46 | 609:43 | 896:54 | 1506:37 | 1525:30 | 23:07 | 96.9318 | 96.8933 | 3051:00 | 46:14 | 96.8815 | 96.8424 | 62 | 109399 | 1525.5 | 0.93939 | 23.1136 | 24:00 | 0.93939 | 23.1136
21 | Doddaballapura | 53 | 53 | 131:36 | 263:12 | 526:41 | 938:14 | 1464:55 | 1596:31 | 30:07 | 96.285 | 95.9512 | 3193:02 | 60:15 | 96.2241 | 95.8848 | 128 | 86649 | 1596.5167 | 2.4151 | 30.123 | 24:00 | 2.4151 | 30.123
22 | Bangalore south | 20 | 20 | 184:11 | 234:45 | 367:19 | 455:57 | 823:16 | 1007:27 | 50:22 | 94.4673 | 93.2295 | 1620:52 | 81:03 | 95.266 | 94.4643 | 1389 | 6390 | 1007.45 | 69.45 | 50.3725 | 24:00 | 0 | 0
23 | Magadi | 11 | 11 | 24:15 | 33:57 | 201:46 | 312:32 | 514:18 | 538:33 | 48:58 | 93.7158 | 93.4195 | 845:08 | 76:50 | 94.9628 | 94.752 | 483 | 38386 | 1200.35 | 43.9091 | 109.1227 | 24:00 | 29.3333 | 97.475
24 | Anekal | 127 | 127 | 1028:28 | 1299:51 | 2892:58 | 2704:57 | 5597:55 | 6626:23 | 52:11 | 94.0755 | 92.9871 | 9854:55 | 77:36 | 95.3987 | 94.6996 | 6583 | 239573 | 6626.3833 | 51.8346 | 52.1762 | 24:00 | 38.1102 | 25.4215
25 | Ramanagara | 35 | 35 | 5:46 | 17:12 | 313:53 | 530:11 | 844:04 | 849:50 | 24:17 | 96.7586 | 96.7364 | 1339:59 | 38:17 | 97.4185 | 97.3849 | 1431 | 5752 | 849.8333 | 40.8857 | 24.281 | 24:00 | 28.8286 | 14.0043
26 | Channapatna | 7 | 7 | 10:31 | 21:02 | 157:50 | 108:05 | 265:55 | 276:26 | 39:29 | 94.8941 | 94.6921 | 418:57 | 59:51 | 96.1171 | 95.9119 | 659 | 35208 | 276.4333 | 94.1429 | 39.4905 | 24:00 | 94.1429 | 20.3595
27 | Kanakapura | 22 | 22 | 8:10 | 16:20 | 241:20 | 79:17 | 320:37 | 328:47 | 14:57 | 98.0412 | 97.9913 | 657:34 | 29:53 | 98.0091 | 97.9584 | 1941 | 20114 | 328.7833 | 88.2273 | 14.9447 | 24:00 | 88.2273 | 14.9447
NOTE:
01. Reliability Index of Devanahalli has reduced as 05 nos of feeders (F12, F14 of 66/11 KV Muss Budhigere and F18, F20, F29 of 66/11 KV Muss Devenahalli) were faulty due to cable fault, since the load change over was done, no load was affected.
02. In Magadi town from the month of April-2019 out of 12 feeders 01 feeder is converted into NJY feeder i.e. F1-Ajjanahalli feeder from V.G. doddi MUSS

## ANX-III
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
RELIABILITY INDICES FOR RURAL AREAS BESCOM FOR THE MONTH OF MAY-19 OF FY 2019-20
ANX-III
Sl. No | Name of the DIVISION | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY 19-20 | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for MAY-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=18/4
1 | Davanagere | 276 | 274 | 311:45 | 612:42 | 5835:29 | 5024:58 | 10860:26 | 11172:11 | 40:29 | 94.7111 | 94.5593 | 18794:58 | 68:06 | 95.5002 | 95.3485 | 16581 | 267520 | 11172.18 | 60.5146 | 40.7744 | 24:00 | 0.7
2 | Harihara | 197 | 197 | 18:25 | 38:20 | 4657:25 | 4203:01 | 8860:26 | 8878:51 | 45:04 | 93.9547 | 93.9422 | 17025:37 | 86:25 | 94.11 | 94.0967 | 9301 | 207717 | 8878.85 | 47.2132 | 45.0703 | 24:00
3 | Chitradurga | 178 | 178 | 114:45 | 218:35 | 1991:14 | 2871:02 | 4862:16 | 4977:01 | 27:58 | 96.3285 | 96.2418 | 9696:22 | 54:28 | 96.363 | 96.2791 | 15215 | 218511 | 4977.02 | 85.4775 | 27.9608 | 24:00
4 | Hiriyur | 215 | 215 | 17:12 | 31:24 | 5691:50 | 6349:40 | 12041:30 | 12058:42 | 56:05 | 92.4722 | 92.4614 | 19723:34 | 91:44 | 93.7438 | 93.7338 | 13239 | 253786 | 12058.7 | 61.5767 | 56.087 | 24:00
5 | Tumkur | 322 | 322 | 60:00 | 120:00 | 3467:25 | 6094:06 | 9561:31 | 9621:31 | 29:53 | 96.0088 | 95.9838 | 16458:31 | 51:07 | 96.5341 | 96.5086 | 9035 | 2622465 | 9621.52 | 28.059 | 29.8805 | 24:00 | 0.51667
6 | Tiptur | 194 | 194 | 51:00 | 102:00 | 3128:19 | 10994:43 | 14123:02 | 14174:02 | 73:04 | 90.2152 | 90.1798 | 20186:02 | 104:03 | 92.9286 | 92.8926 | 12228 | 204762 | 14714.03 | 63.0309 | 75.8455 | 24:00 | 0.033333
7 | Madhugiri | 307 | 307 | 64:00 | 128:00 | 6074:32 | 7777:35 | 13852:08 | 13916:08 | 45:20 | 93.9354 | 93.9073 | 18828:08 | 61:20 | 95.8393 | 95.8108 | 12443 | 400356 | 7841.58 | 40.5309 | 25.5426 | 24:00 | 0.58333
8 | Kunigal | 105 | 105 | 32:00 | 64:00 | 990:43 | 3775:05 | 4765:48 | 4797:48 | 45:42 | 93.8994 | 93.8584 | 7727:48 | 73:36 | 95.0144 | 94.9728 | 2428 | 45623 | 4797.78 | 23.1238 | 45.6931 | 24:00 | 0.78333
9 | Kolar | 160 | 160 | 605:58 | 1079:39 | 2766:07 | 7219:02 | 9985:09 | 10591:07 | 66:12 | 91.6119 | 91.1029 | 16795:57 | 104:58 | 93.2905 | 92.8296 | 7579 | 149063 | 10591.1167 | 47.3687 | 66.1945 | 24:00
10 | KGF | 197 | 183 | 5:45 | 8:00 | 3891:30 | 9999:00 | 13890:30 | 13896:15 | 70:32 | 90.5228 | 90.5189 | 20453:47 | 103:50 | 92.9108 | 92.908 | 7762 | 292779 | 13896.25 | 42.4153 | 75.9358 | 24:00
11 | CB Pura | 194 | 194 | 601:04 | 892:05 | 2913:13 | 3921:17 | 6834:30 | 7435:34 | 38:20 | 95.2649 | 94.8484 | 10972:42 | 56:34 | 96.4507 | 96.1366 | 11503 | 210624 | 7435.5667 | 59.2938 | 38.3277 | 24:00
12 | Chintamani | 147 | 147 | 19:04 | 42:19 | 1429:01 | 3894:02 | 5323:03 | 5342:07 | 36:20 | 95.1329 | 95.1155 | 8582:21 | 58:23 | 96.0317 | 96.0121 | 2542 | 193270 | 5342.1167 | 17.2925 | 36.3409 | 24:00
13 | Devanahalli | 33 | 33 | 25:03 | 50:06 | 2388:13 | 1359:56 | 3748:09 | 3773:12 | 114:20 | 84.7338 | 84.6318 | 6758:32 | 204:48 | 86.1144 | 86.0107 | 45 | 36850 | 3773.2 | 1.3636 | 114.3394 | 24:00
14 | Hosakote | 32 | 32 | 69:59 | 89:31 | 270:35 | 625:35 | 896:10 | 966:09 | 30:12 | 96.2359 | 95.9419 | 1517:00 | 47:24 | 96.9529 | 96.7619 | 90 | 26828 | 966.15 | 2.8125 | 30.1922 | 24:00
15 | Nelamangala | 17 | 17 | 11:08 | 22:16 | 152:18 | 358:09 | 510:27 | 521:35 | 30:41 | 95.9642 | 95.8762 | 1032:02 | 60:42 | 95.9428 | 95.8533 | 20 | 24522 | 521.5833 | 1.1765 | 30.6814 | 24:00
16 | Doddaballapura | 40 | 40 | 79:41 | 159:22 | 611:40 | 1203:04 | 1814:44 | 1894:25 | 47:22 | 93.9021 | 93.6344 | 3709:09 | 92:44 | 93.9382 | 93.6661 | 105 | 61577 | 1894.4167 | 2.625 | 47.3604 | 24:00
17 | Magadi | 42 | 42 | 13:19 | 20:09 | 526:21 | 606:23 | 1132:44 | 1146:03 | 27:17 | 96.375 | 96.3324 | 2272:18 | 54:06 | 96.3373 | 96.3045 | 3317 | 52468 | 1146.05 | 78.9762 | 27.2869 | 24:00
18 | Chandapura | 19 | 19 | 11:17 | 21:44 | 286:47 | 211:38 | 498:25 | 509:42 | 26:50 | 96.4741 | 96.3943 | 756:23 | 39:49 | 97.3589 | 97.2808 | 715 | 45583 | 509.7 | 37.6316 | 26.8263 | 24:00
19 | Ramanagara | 39 | 39 | 20:40 | 34:17 | 671:50 | 456:35 | 1128:25 | 1149:05 | 29:28 | 96.111 | 96.0398 | 2270:28 | 58:13 | 96.0835 | 96.0234 | 5585 | 38024 | 1149.0903 | 143.2051 | 29.4639 | 24:00
20 | Channapatna | 47 | 47 | 34:05 | 68:10 | 420:51 | 1955:19 | 2376:10 | 2410:15 | 51:17 | 93.2047 | 93.1073 | 3827:49 | 81:27 | 94.536 | 94.437 | 4965 | 52541 | 2410.25 | 105.6383 | 51.2819 | 24:00
21 | Kanakapura | 110 | 110 | 26:27 | 46:39 | 1901:45 | 1649:28 | 3551:13 | 3577:40 | 32:31 | 95.6608 | 95.6285 | 7122:38 | 64:45 | 95.6061 | 95.5771 | 1287 | 101838 | 3577.6667 | 11.7 | 32.5242 | 24:00
Note :
1. 10 Nos of New NJY feeders added in Tumkur division. F1, F2, F3, F4, F8 emanating from 66/11 KV Muss Halagavadi and F23 emanating from 66/11 KV Muss Melekote and F9, F7, F4, F8 emanating from 66/11 KV Muss Thovinakere.
2. 05 Nos of New feeders added in Kolar division. F10, F11, F13, F12, emanating from 66/11 KV Muss Addagal and F06 emanating from 66/11 KV Muss Dalasanur
3. Reliability Index of Devanahalli has reduced as 05 nos of feeders (F12, F14 of 66/11 KV Muss Budhigere and F18, F20, F29 of 66/11 KV Muss Devenahalli) were faulty due to cable fault, since the load change over was done, no load was affected.