## Annexure 1
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR THE MONTH OF JULY-2019 OF FY 2019-20
ANX-I
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure (in Hrs) for FY 19-20 | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for JULY-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Davangere | 36 | 33 | 0:10 | 14:03 | 401:44 | 71:09 | 472:53 | 473:03 | 13:08 | 98.2344 | 98.2338 | 2051:04 | 56:58 | 98.0675 | 98.0542 | 837 | 157321 | 473.05 | 25.3636 | 14.3348 | 24:00 | 0.71667 | 60
2 | Chitradurga | 11 | 11 | 1:52 | 8:37 | 96:20 | 68:38 | 164:58 | 166:50 | 15:10 | 97.9843 | 97.9615 | 721:50 | 65:37 | 97.7856 | 97.7588 | 922 | 42269 | 166.83 | 83.8182 | 15.1664 | 24:00 | 0.51667 | 60
3 | Tumkur | 30 | 30 | 10:00 | 44:48 | 280:00 | 152:00 | 432:00 | 442:00 | 14:44 | 98.0645 | 98.0197 | 2026:19 | 67:33 | 97.7442 | 97.6932 | 2275 | 99840 | 442 | 75.8333 | 14.7333 | 24:00 | 0.11667 | 60
4 | BMAZ, North | 685 | 626 | 201:02 | 1869:37 | 1229:50 | 3644:38 | 4874:28 | 5075:30 | 7:25 | 99.0435 | 99.0041 | 1430.61 | 50:07 | 98.3813 | 98.2881 | 8639 | 2645169 | 5075.05 | 13.8003 | 8.1071 | 24:00 | 0.83333 | 60 | 2624414 | 2595331 | 2633893
5 | BMAZ, South | 775 | 569 | 170:44 | 1268:05 | 2593:35 | 2074:49 | 4668:24 | 4839:08 | 6:15 | 99.1904 | 99.1607 | 1396.1624 | 43:14 | 98.5792 | 98.5234 | 8810 | 2575200 | 4839.13 | 15.4833 | 8.5046 | 24:00 | 0.23333 | 60
5 | Ramanagara | 4 | 4 | 1:50 | 6:50 | 13:09 | 12:15 | 25:24 | 27:14 | 6:49 | 99.1464 | 99.0848 | 115:21 | 28:50 | 99.0734 | 99.0151 | 54 | 39398 | 27.23 | 13.5 | 6.8075 | 24:00 | 0.083333 | 60
6 | Kolar | 17 | 17 | 0:00 | 19:52 | 209:45 | 136:38 | 346:23 | 346:23 | 20:23 | 97.2614 | 97.2614 | 2198:35 | 129:20 | 95.623 | 95.583 | 781 | 80055 | 346.38 | 45.9412 | 20.3753 | 24:00 | 0.6 | 60
7 | CBPura | 9 | 9 | 11:20 | 109:26 | 160:00 | 51:20 | 211:20 | 222:40 | 24:44 | 96.8439 | 96.6746 | 1019:53 | 113:19 | 96.545 | 96.1298 | 511 | 58733 | 222.67 | 56.7778 | 24.7411 | 24:00 | 0.36667 | 60
NOTE: Total 06 nos of New Feeders were added during the month of JULY-2019 in BMAZ, North. 03 nos of feeders (F17, F21, F22) emanating from 66/11 KV Muss Sahakar nagar, 02 nos of feeders (F4, F5) emanating from 220 KV R/s Hoody & 01 no of feeder F17 emanating from 66/11 KV 'B' Station. | [23 empty] | 60
Assitant General Manager-3(Elec) | [6 empty] | Chief General Manager(Elec) | [8 empty] | Deputy General Manager(Elec) | [7 empty] | 60
Operations-3, BESCOM | [6 empty] | Operations, BESCOM | [8 empty] | Operations-3,BESCOM | [7 empty] | 60

## Annexure II
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
B. RELIABILITY INDICES FOR TOWNS AND CITIES BESCOM FOR THE MONTH OF JULY-2019 OF FY 2019-20
ANX-II
Sl. No | Name of the TOWNS & CITIES | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY… | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for JULY-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Jagalur | 1 | 1 | 4:25 | 26:05 | 17:06 | 6:12 | 23:18 | 27:43 | 27:43 | 96.8683 | 96.2746 | 102:50 | 102:50 | 97.3788 | 96.4879 | 60 | 7822 | 27.72 | 60 | 27.72 | 24:00 |  | 0.55 | 146:58 | 1 | 1 | 1 | 1 | 1 | 1
2 | Channagiri | 1 | 1 | 8:05 | 38:05 | 32:03 | 2:27 | 34:30 | 42:35 | 42:35 | 95.3629 | 94.2764 | 133:32 | 133:32 | 96.7401 | 95.4394 | 121 | 8179 | 42.58 | 121 | 42.58 | 24:00 |  | 0.38333 | 285:43 | 1 | 1 | 1 | 1 | 1 | 1
3 | Harihara | 11 | 11 | 2:10 | 10:05 | 135:03 | 25:43 | 160:46 | 162:56 | 14:49 | 98.0356 | 98.0091 | 709:35 | 64:30 | 97.8282 | 97.7969 | 219 | 14484 | 162.93 | 19.9091 | 14.8118 | 24:00 |  | 0.31667 | 169:27 | 11 | 11 | 11 | 11 | 11 | 11
4 | Honnali | 2 | 2 | 1:50 | 5:15 | 16:35 | 2:55 | 19:30 | 21:20 | 10:40 | 98.6895 | 98.5663 | 92:35 | 46:18 | 98.5087 | 98.419 | 92 | 13009 | 21.33 | 46 | 10.665 | 24:00 |  | 0.25 |  | 2 | 2 | 2 | 2 | 2 | 2
5 | Harapanahalli | 4 | 4 | 0:25 | 2:55 | 31:40 | 7:25 | 39:05 | 39:30 | 9:52 | 98.6867 | 98.6727 | 237:05 | 59:16 | 98.0006 | 97.9757 | 80 | 3946 | 39.5 | 20 | 9.875 | 24:00 |  | 0.16667 | 323:56 | 4 | 4 | 4 | 4 | 4 | 4
6 | Holalkere | 1 | 1 | 1:15 | 7:00 | 15:20 | 11:28 | 26:48 | 28:03 | 28:03 | 96.3978 | 96.2298 | 119:03 | 119:03 | 96.1732 | 95.9341 | 91 | 4642 | 28.05 | 91 | 28.05 | 24:00 |  | 0.51667 | 695:39 | 1 | 1 | 1 | 1 | 1 | 1
7 | Hosadurga | 2 | 2 | 2:05 | 8:30 | 29:15 | 25:04 | 54:19 | 56:24 | 28:12 | 96.3497 | 96.2097 | 235:28 | 117:44 | 96.1242 | 95.9791 | 163 | 11634 | 56.4 | 81.5 | 28.2 | 24:00 |  | 0.083333 | 418:39 | 2 | 2 | 2 | 2 | 2 | 2
8 | Hiriyur | 3 | 3 | 6:42 | 18:01 | 24:34 | 19:28 | 44:02 | 50:44 | 16:55 | 98.0272 | 97.7269 | 225:29 | 75:10 | 97.6381 | 97.4329 | 177 | 3513 | 50.73 | 59 | 16.91 | 24:00 |  | 0.11667 |  | 3 | 3 | 3 | 3 | 3 | 3
9 | Challakere | 7 | 7 | 6:58 | 18:43 | 98:54 | 69:23 | 168:17 | 175:15 | 25:02 | 96.7688 | 96.6351 | 543:49 | 77:41 | 97.438 | 97.3467 | 342 | 17846 | 175.23 | 48.8571 | 25.0329 | 24:00 |  | 0.76667 |  | 5 | 5 | 5 | 5 | 5 | 5
10 | Molakalmuru | 1 | 1 | 4:07 | 11:06 | 11:51 | 2:05 | 13:56 | 18:04 | 18:04 | 98.1272 | 97.5728 | 97:24 | 97:24 | 97.052 | 96.6732 | 43 | 904 | 18.05 | 43 | 18.05 | 24:00 |  | 0.53333 |  | 1 | 1 | 1 | 1 | 1 | 1
11 | Tumkur | 6 | 6 | 22:42 | 73:25 | 119:21 | 34:55 | 154:16 | 176:58 | 29:30 | 96.5442 | 96.0357 | 826:35 | 137:46 | 95.7128 | 95.2949 | 245 | 34833 | 175.97 | 40.8333 | 29.3283 | 24:00 |  | 0.05 | [5 empty] | 6 | 6
12 | Tiptur | 11 | 11 | 25:35 | 101:11 | 264:16 | 120:05 | 384:21 | 409:56 | 37:16 | 95.3036 | 94.991 | 1829:42 | 166:20 | 94.6333 | 94.3191 | 949 | 33646 | 409.93 | 86.2727 | 37.2664 | 24:00 |  | 0.45 | [5 empty] | 11 | 11
13 | Madhugiri | 8 | 8 | 38:20 | 146:05 | 172:21 | 38:31 | 210:52 | 249:12 | 31:09 | 96.4572 | 95.8132 | 1371:31 | 171:26 | 94.7685 | 94.1449 | 446 | 47990 | 249.2 | 55.75 | 31.15 | 24:00 |  | 0 | [5 empty] | 8 | 8
14 | Srinivaspura | 4 | 4 | 22:20 | 44:55 | 59:30 | 58:40 | 118:10 | 140:30 | 35:08 | 96.0293 | 95.2789 | 623:05 | 155:46 | 95.0635 | 94.68 | 192 | 21603 | 140.5 | 48 | 35.125 | 24:00 | 52.75 | 0.25 |  | 4 | 4 | 4 | 4 | 4 | 4
15 | KGF | 30 | 30 | 0:44 | 10:31 | 609:00 | 199:10 | 808:10 | 808:54 | 26:58 | 96.3792 | 96.3759 | 3747:21 | 124:55 | 95.7459 | 95.7339 | 1520 | 88517 | 808.9 | 50.6667 | 26.9633 | 24:00 | 47.8667 | 0.88333 |  | 30 | 30 | 30 | 30 | 30 | 30
16 | CB Pura | 11 | 11 | 16:25 | 81:25 | 108:25 | 53:40 | 162:05 | 178:30 | 16:14 | 98.0195 | 97.8189 | 966:52 | 87:54 | 97.2508 | 96.9981 | 385 | 44720 | 178.5 | 35 | 16.2273 | 24:00 | 33.3636 | 0.21667 |  | 11 | 11 | 11 | 11 | 11 | 11
17 | Chintamani | 15 | 15 | 5:35 | 26:34 | 234:04 | 108:55 | 342:59 | 348:34 | 23:14 | 96.9267 | 96.8766 | 1820:28 | 121:22 | 95.9155 | 95.855 | 562 | 37580 | 348.56 | 37.4667 | 23.2373 | 24:00 | 28.8 | 0.66667 |  | 15 | 15 | 15 | 15 | 15 | 15
18 | Devanahalli | 60 | 60 | 40:59 | 434:06 | 1849:20 | 4735:06 | 6584:26 | 6625:25 | 110:25 | 85.2499 | 85.1581 | 1314.766 | 525:54 | 82.2858 | 82.0387 | 3661 | 67407 | 6625.42 | 61.0167 | 110.4237 | 24:00 | 1.6833 | 0.35 |  | 60 | 60 | 60 | 60 | 60 | 60
19 | Hosakote | 61 | 61 | 71:45 | 325:53 | 854:42 | 620:06 | 1474:48 | 1546:33 | 25:21 | 96.7504 | 96.5923 | 7678:38 | 125:53 | 95.8833 | 95.7008 | 3001 | 88503 | 1546.55 | 49.1967 | 25.3533 | 24:00 | 1.2623 | 0.4 |  | 61 | 61 | 61 | 61 | 61 | 61
20 | Nelamangala | 67 | 67 | 17:21 | 84:25 | 871:52 | 376:55 | 1248:47 | 1266:08 | 18:54 | 97.4948 | 97.46 | 6628:49 | 98:56 | 96.664 | 96.621 | 2422 | 143621 | 1266.12 | 36.1493 | 18.8973 | 24:00 | 0.93939 | 0.68333 |  | 66 | 66 | 66 | 66 | 66 | 66
21 | Doddaballapura | 54 | 54 | 35:10 | 338:39 | 711:38 | 1277:25 | 1989:03 | 2024:13 | 37:29 | 95.0492 | 94.9616 | 8516:40 | 157:43 | 94.8277 | 94.6135 | 1778 | 58952 | 2024.22 | 32.9259 | 37.4856 | 24:00 | 2.4151 | 0.41667 |  | 54 | 54 | 53 | 53 | 53 | 53
22 | Bangalore south | 20 | 20 | 71:24 | 455:27 | 340:33 | 147:20 | 487:53 | 559:17 | 27:58 | 96.7212 | 96.2414 | 2941:23 | 147:04 | 95.7549 | 94.9771 | 1239 | 6681 | 559.28 | 61.95 | 27.964 | 24:00 | 0 | 0.23333 |  | 20 | 20 | 20 | 20 | 20 | 20
23 | Magadi | 11 | 11 | 76:57 | 173:26 | 238:04 | 223:31 | 461:35 | 538:32 | 48:57 | 94.3599 | 93.4197 | 1976:16 | 179:40 | 94.4025 | 93.8641 | 571 | 32656 | 538.53 | 51.9091 | 48.9573 | 24:00 | 29.3333 | 0.68333 |  | 12 | 12 | 12 | 12 | 12 | 12
24 | Anekal | 127 | 127 | 553:20 | 2653:19 | 2157:32 | 898:42 | 3056:14 | 3609:34 | 28:25 | 96.7655 | 96.1799 | 20352:25 | 160:15 | 95.2403 | 94.5268 | 5664 | 242914 | 3609.57 | 44.5984 | 28.4218 | 24:00 | 38.1102 | 0.93333 |  | 127 | 127 | 127 | 127 | 127 | 127
25 | Ramanagara | 35 | 35 | 17:51 | 52:54 | 313:53 | 432:53 | 746:46 | 764:37 | 21:51 | 97.1322 | 97.0637 | 2869:13 | 81:59 | 97.2518 | 97.2002 | 1373 | 27151 | 764.62 | 39.2286 | 21.8463 | 24:00 | 28.8286 | 0.61667 |  | 35 | 35 | 35 | 35 | 35 | 35
26 | Channapatna | 7 | 7 | 10:31 | 42:04 | 378:31 | 94:30 | 473:01 | 483:32 | 69:05 | 90.9175 | 90.7156 | 1386:01 | 198:00 | 93.4429 | 93.2376 | 659 | 38402 | 483.53 | 94.1429 | 69.0757 | 24:00 | 94.1429 | 0.53333 |  | 7 | 7 | 7 | 7 | 7 | 7
27 | Kanakapura | 22 | 22 | 5:10 | 26:40 | 241:20 | 79:17 | 320:37 | 325:47 | 14:48 | 98.0412 | 98.0096 | 1309:08 | 59:30 | 98.0091 | 97.9677 | 1941 | 29303 | 325.78 | 88.2273 | 14.8082 | 24:00 | 88.2273 | 0.78333 |  | 22 | 22 | 22 | 22 | 22 | 22
NOTE: 02 no. of New Urban Feeders KHB-1 & KHB-2 was added in challkere town emanating from 66/11 KV Chalkere station.
01 no. of New Feeders F23 was added in Nelmangala town emanating from 66/11 KV Nelmangala Station.
Reason for Below 95 % in Devanahalli sub division,OLP Relay set for 40Amps instead of 60amps. Because of which Agri feeders cannot be supplied Single phase load. Ankonahalli & Kondenahalli feeders Partial feeders. Due to Cable Fault at F18 ISRO Feeder & F8 Aerospace feeder load change over done to Bhuvanahalli feeder & F9 feeders respectively

## ANX-III
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
C. RELIABILITY INDICES FOR RURAL AREAS BESCOM FOR THE MONTH OF JULY-19 OF FY 2019-20
ANX-III
Sl. No | Name of the DIVISION | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY… | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for JULY-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Davanagere | 278 | 274 | 182:45 | 921:07 | 6761:06 | 5496:58 | 12258:04 | 12440:49 | 44:45 | 94.0734 | 93.9851 | 1888.2403 | 163:01 | 94.5458 | 94.4326 | 17036 | 276843 | 12440.8 | 62.1752 | 45.4044 | 24:00 | 276 | 274 | 276 | 274 |  | 276 | 274 | 276 | 274
2 | Harihara | 197 | 197 | 19:10 | 72:45 | 6681:04 | 5544:01 | 12225:05 | 12244:15 | 62:09 | 91.6591 | 91.646 | 1759.9715 | 214:25 | 92.6898 | 92.6772 | 11977 | 208967 | 12244.25 | 60.797 | 62.1536 | 24:00 | 197 | 197 | 197 | 197 |  | 197 | 197 | 197 | 197
3 | Chitradurga | 178 | 178 | 108:15 | 430:10 | 1723:08 | 2804:44 | 4527:52 | 4636:07 | 26:03 | 96.581 | 96.4992 | 19280:29 | 108:19 | 96.3832 | 96.3006 | 14500 | 218594 | 4636.12 | 81.4607 | 26.0456 | 24:00 | 178 | 178 | 178 | 178 |  | 178 | 178 | 178 | 178
4 | Hiriyur | 215 | 215 | 29:40 | 86:52 | 6932:24 | 4128:12 | 11060:36 | 11090:16 | 51:35 | 93.0854 | 93.0668 | 1800.0151 | 200:56 | 93.1514 | 93.1376 | 12578 | 258473 | 11090.27 | 58.5023 | 51.5827 | 24:00 | 215 | 215 | 215 | 215 |  | 215 | 215 | 215 | 215
5 | Tumkur | 322 | 322 | 68:00 | 248:00 | 4628:00 | 1553:00 | 6181:00 | 6249:00 | 19:24 | 97.4199 | 97.3916 | 1850.4509 | 137:55 | 95.3159 | 95.2896 | 10218 | 262465 | 6249 | 31.7329 | 19.4068 | 24:00 | 322 | 322 | 322 | 322 |  | 312 | 312 | 322 | 322
6 | Tiptur | 205 | 205 | 55:00 | 202:00 | 2733:00 | 2165:00 | 4898:00 | 4953:00 | 24:10 | 96.7886 | 96.7526 | 1592.2095 | 186:24 | 93.6674 | 93.6337 | 9790 | 210785 | 4953 | 47.7561 | 24.161 | 24:00 | 205 | 205 | 194 | 194 | -11 | 194 | 194 | 194 | 194
7 | Madhugiri | 322 | 322 | 60:00 | 242:00 | 5683:00 | 5383:00 | 11066:00 | 11126:00 | 34:33 | 95.3809 | 95.3558 | 1965.2135 | 146:29 | 95.0231 | 94.9974 | 12293 | 456836 | 11126 | 38.177 | 34.5528 | 24:00 | 322 | 322 | 307 | 307 | -15 | 307 | 307 | 307 | 307
8 | Kunigal | 109 | 109 | 40:00 | 139:00 | 1662:00 | 3492:00 | 5154:00 | 5194:00 | 47:39 | 93.6446 | 93.5952 | 20826:48 | 191:04 | 93.5179 | 93.4743 | 3509 | 46120 | 5194 | 32.1927 | 47.6514 | 24:00 | 109 | 109 | 105 | 105 | -4 | 105 | 105 | 105 | 105
9 | Kolar | 164 | 164 | 474:35 | 2312:27 | 2674:30 | 3590:15 | 6264:45 | 6739:20 | 41:06 | 94.8656 | 94.4767 | 1373.5722 | 201:01 | 93.6165 | 93.1349 | 5836 | 100949 | 6739.33 | 35.5854 | 41.0935 | 24:00 | 164 | 164 | 160 | 160 |  | 155 | 155 | 160 | 160
10 | KGF | 198 | 183 | 2:13 | 44:20 | 3171:10 | 3346:00 | 6517:10 | 6519:23 | 32:56 | 95.5759 | 95.5744 | 1595.0882 | 193:21 | 93.4044 | 93.3967 | 8062 | 280486 | 6519.38 | 44.0546 | 35.625 | 24:00 | 197 | 183 | 197 | 183 |  | 197 | 183 | 197 | 183
11 | CB Pura | 194 | 194 | 485:00 | 1843:05 | 2296:25 | 2496:33 | 4792:58 | 5277:58 | 27:12 | 96.6793 | 96.3433 | 22749:27 | 117:16 | 96.3195 | 95.995 | 7860 | 211472 | 5277.96 | 40.5155 | 27.206 | 24:00 | 194 | 194 | 194 | 194 |  | 194 | 194 | 194 | 194
12 | Chintamani | 147 | 147 | 19:35 | 78:39 | 1369:02 | 2641:04 | 4010:06 | 4029:41 | 27:25 | 96.3334 | 96.3155 | 17112:53 | 116:25 | 96.0424 | 96.0241 | 3076 | 193911 | 4029.68 | 20.9252 | 27.4128 | 24:00 | 147 | 147 | 147 | 147 |  | 147 | 147 | 147 | 147
13 | Devanahalli | 33 | 33 | 22:03 | 108:19 | 2490:43 | 758:54 | 3249:37 | 3271:40 | 99:08 | 86.7644 | 86.6745 | 13547:33 | 410:32 | 86.0912 | 85.9791 | 2518 | 36850 | 3271.67 | 76.303 | 99.1415 | 24:00 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33
14 | Hosakote | 32 | 32 | 36:16 | 161:37 | 156:50 | 359:22 | 516:12 | 552:28 | 17:16 | 97.8318 | 97.6795 | 3087:16 | 96:29 | 96.8775 | 96.705 | 1091 | 26828 | 552.47 | 34.0938 | 17.2647 | 24:00 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32
15 | Nelamangala | 17 | 17 | 6:54 | 73:10 | 331:33 | 172:27 | 504:00 | 510:54 | 30:03 | 96.0152 | 95.9606 | 2562:37 | 150:45 | 94.9987 | 94.8517 | 920 | 61399 | 510.09 | 54.1176 | 30.0053 | 24:00 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17
16 | Doddaballapura | 40 | 40 | 55:55 | 240:21 | 266:18 | 951:19 | 1217:37 | 1273:32 | 31:50 | 95.9085 | 95.7207 | 7919:05 | 197:59 | 93.4437 | 93.2385 | 1908 | 25952 | 1273.53 | 47.7 | 31.8382 | 24:00 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40
17 | Magadi | 42 | 42 | 34:50 | 89:49 | 526:21 | 606:23 | 1132:44 | 1167:34 | 27:48 | 96.375 | 96.2635 | 4607:26 | 109:42 | 96.3264 | 96.2534 | 3343 | 64578 | 1167.57 | 79.5952 | 27.7993 | 24:00 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42
18 | Chandapura | 19 | 19 | 14:26 | 50:36 | 225:55 | 112:08 | 338:03 | 352:29 | 18:33 | 97.6086 | 97.5065 | 1461:21 | 76:55 | 97.4641 | 97.3732 | 537 | 46252 | 352.48 | 28.2632 | 18.5516 | 24:00 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19
19 | Ramanagara | 39 | 39 | 23:43 | 81:43 | 671:50 | 456:35 | 1128:25 | 1152:08 | 29:33 | 96.111 | 96.0293 | 4574:45 | 117:18 | 96.0654 | 95.9938 | 5361 | 38205 | 1152.13 | 137.4615 | 29.5418 | 24:00 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39
20 | Channapatna | 47 | 47 | 34:05 | 136:20 | 410:27 | 902:14 | 1312:41 | 1346:46 | 28:39 | 96.246 | 96.1486 | 6521:21 | 138:45 | 95.3603 | 95.2612 | 4965 | 57712 | 1346.77 | 105.6383 | 28.6547 | 24:00 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47
21 | Kanakapura | 110 | 110 | 29:12 | 105:03 | 1901:45 | 1649:28 | 3551:13 | 3580:25 | 32:33 | 95.6608 | 95.6251 | 14283:28 | 129:51 | 95.5979 | 95.5652 | 1287 | 103952 | 3580.42 | 11.7 | 32.5493 | 24:00 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110
NOTE:
1. 02 Nos of New NJY feeders Neetigere and Nibgur added in Davanegere Division emanating from 66/11 KV Muss Devarahally.
2. 01 nos of new feeders added in KGF division. F17, Industrial express Feeder emanating from 66/11 KV Muss Malur
6. Reliability Index of Dodaballapura has reduced as 05 nos of feeders (F12, F14 of 66/11 KV Muss Budhigere and F18, F20, F29 of 66/11 KV Muss Devenahalli) were faulty due to cable fault, since the load change over was done, no load was affected.
Note: In Davanagere division 2 Nos of NJY feeders Neetigere & Nibgur are newly commissioned on Devarahally 66/11KV station.