## Annexure 1
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR THE MONTH OF AUGUST-2019 OF FY 2019-20
ANX-I
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure (in Hrs) for FY 19-20 | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for Aug-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Davangere | 36 | 33 | 9:40 | 23:43 | 615:40 | 180:29 | 796:10 | 805:50 | 22:23 | 97.0275 | 96.9914 | 2856:53 | 79:21 | 97.3122 | 97.2897 | 1145 | 165016 | 805.82 | 34.697 | 24.4188 | 24:00 | 0.71667 | 60
2 | Chitradurga | 11 | 11 | 1:15 | 9:52 | 133:33 | 95:46 | 229:19 | 230:34 | 20:58 | 97.198 | 97.1827 | 952:24 | 86:35 | 97.0736 | 97.043 | 903 | 43174 | 230.57 | 82.0909 | 20.9609 | 24:00 | 0.51667 | 60
3 | Tumkur | 30 | 30 | 12:00 | 56:48 | 261:00 | 153:00 | 414:00 | 426:00 | 14:12 | 98.1452 | 98.0914 | 2452:19 | 81:45 | 97.2729 | 97.2082 | 620 | 99888 | 426 | 20.6667 | 14.2 | 24:00 | 0.11667 | 60
4 | BMAZ, North | 689 | 623 | 163:19 | 2032:56 | 2862:52 | 2584:39 | 5447:31 | 5610:50 | 8:09 | 98.9373 | 98.9055 | 1664.3947 | 57:59 | 98.1207 | 98.0199 | 8435 | 2657001 | 5610.83 | 13.5393 | 9.0061 | 24:00 | 0.83333 | 60 | 2624414 | 2595331 | 2633893
5 | BMAZ, South | 776 | 585 | 252:46 | 1520:51 | 2261:02 | 3781:55 | 6042:57 | 6295:43 | 8:07 | 98.9533 | 98.9095 | 1658.484 | 51:18 | 98.3151 | 98.2482 | 9742 | 2577518 | 6295.72 | 16.653 | 10.7619 | 24:00 | 0.23333 | 60
5 | Ramanagara | 4 | 4 | 1:25 | 8:15 | 16:05 | 12:13 | 28:18 | 29:43 | 7:26 | 99.0491 | 99.0015 | 145:04 | 36:16 | 98.8318 | 98.7613 | 50 | 39439 | 29.72 | 12.5 | 7.43 | 24:00 | 0.083333 | 60
6 | Kolar | 17 | 17 | 0:00 | 19:52 | 243:12 | 307:11 | 550:23 | 550:23 | 32:23 | 95.6485 | 95.6485 | 2748:58 | 161:42 | 94.5172 | 94.4773 | 842 | 80263 | 550.38 | 49.5294 | 32.3753 | 24:00 | 0.6 | 60
7 | CBPura | 9 | 9 | 28:35 | 138:01 | 145:15 | 76:15 | 221:30 | 250:05 | 27:47 | 96.6921 | 96.2652 | 1269:58 | 141:06 | 95.7045 | 95.1808 | 445 | 58884 | 250.08 | 49.4444 | 27.7867 | 24:00 | 0.36667 | 60
NOTE: | [23 empty] | 60
01. Total 06 nos of New Feeders F-1, F3, F8, F14, F22 emanating from 220 KV Manyatha GIS, were added during the month of AUG-2019 in BMAZ, North. Further 02 nos of 11 KV feeders emanating from 220 KV Hoody that were added during the last month was duplicated hence the total nos of feeders of BMAZ North is 689 instead of 691.
02. 01 no. of New Feeders F9 emanating from 66/11 KV Kodigehalli station was added in BMAZ South.
Assitant General Manager-3(Elec) | [6 empty] | Chief General Manager(Elec) | [8 empty] | Deputy General Manager(Elec) | [7 empty] | 60
Operations-3, BESCOM | [6 empty] | Operations, BESCOM | [8 empty] | Operations-3,BESCOM | [7 empty] | 60

## Annexure II
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
B. RELIABILITY INDICES FOR TOWNS AND CITIES BESCOM FOR THE MONTH OF AUGUST-2019 OF FY 2019-20
ANX-II
Sl. No | Name of the TOWNS & CITIES | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY… | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for Aug-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Jagalur | 1 | 1 | 2:05 | 28:10 | 10:39 | 3:00 | 13:39 | 15:44 | 15:44 | 98.1653 | 97.8853 | 118:34 | 118:34 | 96.9126 | 95.9506 | 38 | 7860 | 15.73 | 38 | 15.73 | 24:00 |  | 0.55 | 146:58 | 1 | 1 | 1 | 1 | 1 | 1
2 | Channagiri | 1 | 1 | 18:10 | 56:15 | 37:33 | 3:24 | 40:57 | 59:07 | 59:07 | 94.496 | 92.0542 | 192:39 | 192:39 | 95.3415 | 93.4204 | 123 | 8270 | 59.12 | 123 | 59.12 | 24:00 |  | 0.38333 | 285:43 | 1 | 1 | 1 | 1 | 1 | 1
3 | Harihara | 11 | 11 | 1:55 | 12:00 | 143:13 | 31:05 | 174:18 | 176:13 | 16:01 | 97.8702 | 97.8468 | 885:48 | 80:32 | 97.287 | 97.2498 | 310 | 42149 | 176.22 | 28.1818 | 16.02 | 24:00 |  | 0.31667 | 169:27 | 11 | 11 | 11 | 11 | 11 | 11
4 | Honnali | 2 | 2 | 1:55 | 7:10 | 32:15 | 6:50 | 39:05 | 41:00 | 20:30 | 97.3734 | 97.2446 | 133:35 | 66:48 | 97.8412 | 97.7189 | 158 | 14096 | 41 | 79 | 20.5 | 24:00 |  | 0.25 |  | 2 | 2 | 2 | 2 | 2 | 2
5 | Harapanahalli | 4 | 4 | 0:45 | 3:40 | 41:00 | 6:05 | 47:05 | 47:50 | 11:58 | 98.4179 | 98.3927 | 284:55 | 71:14 | 97.5986 | 97.5673 | 88 | 14880 | 47.84 | 22 | 11.96 | 24:00 |  | 0.16667 | 398:27 | 4 | 4 | 4 | 4 | 4 | 4
6 | Holalkere | 1 | 1 | 1:05 | 8:05 | 18:43 | 13:56 | 32:39 | 33:44 | 33:44 | 95.6116 | 95.4659 | 152:47 | 152:47 | 95.0581 | 94.782 | 86 | 4786 | 33.73 | 86 | 33.73 | 24:00 |  | 0.51667 | 618:49 | 1 | 1 | 1 | 1 | 1 | 1
7 | Hosadurga | 2 | 2 | 2:26 | 10:56 | 36:01 | 30:00 | 66:01 | 68:27 | 34:13 | 95.5634 | 95.3999 | 303:55 | 151:57 | 94.9969 | 94.8102 | 158 | 11838 | 68.45 | 79 | 34.225 | 24:00 |  | 0.083333 | 388:05 | 2 | 2 | 2 | 2 | 2 | 2
8 | Hiriyur | 3 | 3 | 8:23 | 26:24 | 17:25 | 14:12 | 31:37 | 40:00 | 13:20 | 98.5835 | 98.2081 | 265:29 | 88:30 | 97.2782 | 96.9776 | 149 | 3544 | 39.98 | 49.6667 | 13.3267 | 24:00 |  | 0.11667 |  | 3 | 3 | 3 | 3 | 3 | 3
9 | Challakere | 7 | 7 | 8:42 | 27:25 | 62:04 | 115:06 | 177:10 | 185:52 | 26:33 | 96.5982 | 96.4311 | 729:41 | 104:14 | 96.5736 | 96.4399 | 339 | 17858 | 185.87 | 48.4286 | 26.5529 | 24:00 |  | 0.76667 |  | 5 | 5 | 5 | 5 | 5 | 5
10 | Molakalmuru | 1 | 1 | 5:09 | 16:15 | 13:12 | 4:35 | 17:47 | 22:56 | 22:56 | 97.6098 | 96.9167 | 120:21 | 120:21 | 96.4447 | 95.8898 | 59 | 920 | 22.93 | 59 | 22.93 | 24:00 |  | 0.53333 |  | 1 | 1 | 1 | 1 | 1 | 1
11 | Tumkur | 6 | 6 | 3:35 | 77:00 | 176:12 | 71:42 | 247:54 | 251:29 | 41:55 | 94.4467 | 94.3665 | 1078:04 | 179:41 | 94.3018 | 93.8635 | 380 | 36534 | 251.47 | 63.3333 | 41.9117 | 24:00 |  | 0.05 | [5 empty] | 6 | 6
12 | Tiptur | 11 | 11 | 5:22 | 106:33 | 183:45 | 144:00 | 327:45 | 333:07 | 30:17 | 95.9952 | 95.9297 | 2162:49 | 196:37 | 93.6157 | 93.2849 | 695 | 33654 | 333.1 | 63.1818 | 30.2818 | 24:00 |  | 0.45 | [5 empty] | 11 | 11
13 | Madhugiri | 8 | 8 | 7:53 | 153:58 | 62:27 | 148:17 | 210:44 | 218:38 | 27:20 | 96.4593 | 96.3268 | 1590:08 | 198:46 | 93.8688 | 93.2115 | 485 | 48007 | 218.62 | 60.625 | 27.3275 | 24:00 |  | 0 | [5 empty] | 8 | 8
14 | Srinivaspura | 4 | 4 | 0:40 | 45:35 | 116:35 | 17:15 | 133:50 | 134:30 | 33:37 | 95.5029 | 95.4805 | 757:35 | 189:24 | 93.9208 | 93.5316 | 192 | 21691 | 134.5 | 48 | 33.625 | 24:00 | 52.75 | 0.25 |  | 4 | 4 | 4 | 4 | 4 | 4
15 | KGF | 30 | 30 | 1:30 | 12:01 | 521:17 | 289:42 | 810:59 | 812:29 | 27:05 | 96.3666 | 96.3598 | 4559:50 | 152:00 | 94.8226 | 94.8089 | 1574 | 88839 | 812.48 | 52.4667 | 27.0827 | 24:00 | 47.8667 | 0.88333 |  | 30 | 30 | 30 | 30 | 30 | 30
16 | CB Pura | 11 | 11 | 15:40 | 97:05 | 137:40 | 87:15 | 224:55 | 240:35 | 21:52 | 97.2518 | 97.0603 | 1207:27 | 109:46 | 96.5525 | 96.2511 | 354 | 44880 | 240.58 | 32.1818 | 21.8709 | 24:00 | 33.3636 | 0.21667 |  | 11 | 11 | 11 | 11 | 11 | 11
17 | Chintamani | 16 | 16 | 0:00 | 26:34 | 223:18 | 204:11 | 427:29 | 427:29 | 26:43 | 96.4089 | 96.4089 | 2247:57 | 140:30 | 95.2583 | 95.2016 | 782 | 55663 | 427.48 | 48.875 | 26.7175 | 24:00 | 28.8 | 0.66667 |  | 15 | 15 | 15 | 15 | 15 | 15
18 | Devanahalli | 60 | 60 | 63:05 | 497:11 | 1751:31 | 1444:42 | 3196:13 | 3259:18 | 54:19 | 92.84 | 92.6987 | 1450.5701 | 580:14 | 80.4665 | 80.1835 | 3592 | 68127 | 3259.28 | 59.8667 | 54.3213 | 24:00 | 1.6833 | 0.35 |  | 60 | 60 | 60 | 60 | 60 | 60
19 | Hosakote | 61 | 61 | 39:45 | 365:38 | 715:33 | 599:25 | 1314:58 | 1354:43 | 22:13 | 97.1026 | 97.015 | 9033:21 | 148:05 | 95.1471 | 94.9424 | 2769 | 89869 | 1354.72 | 45.3934 | 22.2085 | 24:00 | 1.2623 | 0.4 |  | 61 | 61 | 61 | 61 | 61 | 61
20 | Nelamangala | 67 | 67 | 1:07 | 85:32 | 628:19 | 391:59 | 1020:18 | 1021:25 | 15:15 | 97.9532 | 97.9509 | 7650:14 | 114:11 | 96.1439 | 96.1003 | 2212 | 159676 | 1021.42 | 33.0149 | 15.2451 | 24:00 | 0.93939 | 0.68333 |  | 66 | 66 | 66 | 66 | 66 | 66
21 | Doddaballapura | 54 | 54 | 15:53 | 354:32 | 602:06 | 495:07 | 1097:13 | 1113:06 | 20:37 | 97.269 | 97.2294 | 9629:46 | 178:20 | 94.1338 | 93.9095 | 1477 | 120622 | 1113.1 | 27.3519 | 20.613 | 24:00 | 2.4151 | 0.41667 |  | 54 | 54 | 53 | 53 | 53 | 53
22 | Bangalore south | 20 | 20 | 15:16 | 470:43 | 467:03 | 167:40 | 634:43 | 649:59 | 32:30 | 95.7344 | 95.6318 | 3591:22 | 179:34 | 94.671 | 93.8672 | 1268 | 6834 | 649.98 | 63.4 | 32.499 | 24:00 | 0 | 0.23333 |  | 20 | 20 | 20 | 20 | 20 | 20
23 | Magadi | 11 | 11 | 74:25 | 247:51 | 197:43 | 119:39 | 317:22 | 391:47 | 35:37 | 96.1221 | 95.2128 | 2368:03 | 215:17 | 93.4172 | 92.6476 | 459 | 33477 | 391.78 | 41.7273 | 35.6164 | 24:00 | 29.3333 | 0.68333 |  | 12 | 12 | 12 | 12 | 12 | 12
24 | Anekal | 127 | 127 | 8:05 | 2661:24 | 2896:21 | 1266:26 | 4162:47 | 4170:52 | 32:50 | 95.5944 | 95.5858 | 1021.8035 | 193:06 | 94.1209 | 93.4052 | 582 | 245788 | 4170.87 | 4.5827 | 32.8415 | 24:00 | 38.1102 | 0.93333 |  | 127 | 127 | 127 | 127 | 127 | 127
25 | Ramanagara | 35 | 35 | 28:31 | 81:25 | 1124:25 | 287:25 | 1411:50 | 1440:21 | 41:09 | 94.5782 | 94.4687 | 4309:34 | 123:08 | 95.8742 | 95.7947 | 1385 | 27475 | 1440.35 | 39.5714 | 41.1529 | 24:00 | 28.8286 | 0.61667 |  | 35 | 35 | 35 | 35 | 35 | 35
26 | Channapatna | 7 | 7 | 12:10 | 54:14 | 90:54 | 165:01 | 255:55 | 268:05 | 38:18 | 95.0861 | 94.8525 | 1654:06 | 236:18 | 92.1942 | 91.9296 | 399 | 41656 | 268.08 | 57 | 38.2971 | 24:00 | 94.1429 | 0.53333 |  | 7 | 7 | 7 | 7 | 7 | 7
27 | Kanakapura | 22 | 22 | 18:45 | 45:25 | 378:18 | 367:27 | 745:45 | 764:30 | 34:45 | 95.4439 | 95.3293 | 2073:38 | 94:15 | 96.8514 | 96.7809 | 492 | 37762 | 764.5 | 22.3636 | 34.75 | 24:00 | 88.2273 | 0.78333 |  | 22 | 22 | 22 | 22 | 22 | 22
NOTE: 01 no. of New Feeder F-16 Serco feeder was added in Chintamani town emanating from 66/11 KV Chintamni station.
Reason for Below 95 % in Devanahalli sub division, F18-ISRO,F20-SOBHA,F29-VILLA HIRANANDANI,F12- Hardware Park-2 and F14- Aerospace Package-1 THESE FEEDERS WAS UNDER FAULTY CONDITION. HENCE 744 HOURS OF UNDSCHEDULE POWER OUTGES WAS CONSIDERED and no load was affected as load changeover was done.

## ANX-III
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
C. RELIABILITY INDICES FOR RURAL AREAS BESCOM FOR THE MONTH OF AUGUST-19 OF FY 2019-20
ANX-III
Sl. No | Name of the DIVISION | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY… | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for Aug-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Davanagere | 278 | 276 | 175:15 | 1096:22 | 6874:34 | 7761:36 | 14636:10 | 14811:25 | 53:17 | 92.9236 | 92.8389 | 2505.3824 | 216:18 | 92.7477 | 92.613 | 16005 | 276845 | 14811.47 | 57.9891 | 53.6647 | 24:00 | 276 | 274 | 276 | 274 |  | 276 | 274 | 276 | 274
2 | Harihara | 197 | 197 | 20:45 | 93:30 | 6136:00 | 8014:00 | 14150:00 | 14170:45 | 71:56 | 90.3458 | 90.3316 | 2350.4194 | 286:21 | 90.2366 | 90.2204 | 12906 | 208969 | 14170.75 | 65.5127 | 71.9327 | 24:00 | 197 | 197 | 197 | 197 |  | 197 | 197 | 197 | 197
3 | Chitradurga | 178 | 178 | 99:45 | 529:55 | 2335:22 | 3222:06 | 5557:28 | 5657:13 | 31:47 | 95.8035 | 95.7282 | 1039.0708 | 140:06 | 95.3169 | 95.2152 | 14137 | 218596 | 5657.22 | 79.4213 | 31.7821 | 24:00 | 178 | 178 | 178 | 178 |  | 178 | 178 | 178 | 178
4 | Hiriyur | 215 | 215 | 44:30 | 131:22 | 5231:11 | 3921:25 | 9152:36 | 9197:06 | 42:47 | 94.2782 | 94.2504 | 2183.2278 | 243:43 | 91.6975 | 91.6766 | 13479 | 258475 | 9197.1 | 62.693 | 42.7772 | 24:00 | 215 | 215 | 215 | 215 |  | 215 | 215 | 215 | 215
5 | Tumkur | 322 | 322 | 60:00 | 308:00 | 4586:00 | 1496:00 | 6082:00 | 6142:00 | 19:04 | 97.4613 | 97.4362 | 2106.3675 | 157:00 | 94.6708 | 94.6381 | 7586 | 262471 | 6142 | 23.559 | 19.0745 | 24:00 | 322 | 322 | 322 | 322 |  | 312 | 312 | 322 | 322
6 | Tiptur | 205 | 205 | 51:00 | 253:00 | 2935:00 | 6128:00 | 9063:00 | 9114:00 | 44:28 | 94.0578 | 94.0244 | 1971.9595 | 230:52 | 92.1575 | 92.1153 | 6235 | 210789 | 9114 | 30.4146 | 44.4585 | 24:00 | 205 | 205 | 194 | 194 | -11 | 194 | 194 | 194 | 194
7 | Madhugiri | 322 | 322 | 64:00 | 306:00 | 5568:00 | 6516:00 | 12084:00 | 12148:00 | 37:44 | 94.9559 | 94.9292 | 2471.3802 | 184:12 | 93.7414 | 93.7089 | 7015 | 456841 | 12148 | 21.7857 | 37.7267 | 24:00 | 322 | 322 | 307 | 307 | -15 | 307 | 307 | 307 | 307
8 | Kunigal | 109 | 109 | 32:00 | 171:00 | 1623:00 | 3420:00 | 5043:00 | 5075:00 | 46:34 | 93.7814 | 93.742 | 1079.2414 | 237:38 | 91.9378 | 91.8842 | 2865 | 46128 | 5075 | 26.2844 | 46.5596 | 24:00 | 109 | 109 | 105 | 105 | -4 | 105 | 105 | 105 | 105
9 | Kolar | 164 | 164 | 728:30 | 3040:57 | 2353:08 | 3850:43 | 6203:51 | 6932:21 | 42:16 | 94.9155 | 94.3185 | 1662.4201 | 243:17 | 92.3245 | 91.6912 | 6126 | 101133 | 6932.35 | 37.3537 | 42.2704 | 24:00 | 164 | 164 | 160 | 160 |  | 155 | 155 | 160 | 160
10 | KGF | 198 | 183 | 9:54 | 54:14 | 3376:05 | 4558:05 | 7934:10 | 7944:04 | 40:07 | 94.614 | 94.6073 | 1926.091 | 233:28 | 92.0358 | 92.0264 | 9629 | 282544 | 7944.06 | 52.6175 | 43.4102 | 24:00 | 197 | 183 | 197 | 183 |  | 197 | 183 | 197 | 183
11 | CB Pura | 194 | 194 | 223:10 | 2066:15 | 2682:05 | 2532:16 | 5214:21 | 5437:31 | 28:02 | 96.3874 | 96.2327 | 1174.457 | 145:18 | 95.4015 | 95.0378 | 8252 | 211485 | 5437.52 | 42.5361 | 28.0285 | 24:00 | 194 | 194 | 194 | 194 |  | 194 | 194 | 194 | 194
12 | Chintamani | 148 | 148 | 2:35 | 81:14 | 1245:04 | 3679:02 | 4924:06 | 4926:41 | 33:17 | 95.5281 | 95.5258 | 22039:34 | 148:55 | 94.9328 | 94.9141 | 7054 | 193982 | 4926.68 | 47.6622 | 33.2884 | 24:00 | 147 | 147 | 147 | 147 |  | 147 | 147 | 147 | 147
13 | Devanahalli | 33 | 33 | 30:20 | 138:39 | 680:58 | 628:45 | 1309:43 | 1340:03 | 40:36 | 94.6655 | 94.542 | 14887:36 | 451:08 | 84.7357 | 84.5922 | 2521 | 39092 | 1340.05 | 76.3939 | 40.6076 | 24:00 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33
14 | Hosakote | 32 | 32 | 12:05 | 173:42 | 238:35 | 437:55 | 676:30 | 688:35 | 21:31 | 97.1585 | 97.1078 | 3775:51 | 118:00 | 96.1555 | 95.9701 | 1323 | 30354 | 688.58 | 41.3438 | 21.5181 | 24:00 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32
15 | Nelamangala | 17 | 17 | 0:24 | 73:34 | 300:31 | 282:18 | 582:49 | 583:13 | 34:18 | 95.392 | 95.3889 | 3145:50 | 185:03 | 93.8278 | 93.68 | 859 | 61577 | 583.22 | 50.5294 | 34.3071 | 24:00 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17
16 | Doddaballapura | 40 | 40 | 28:08 | 268:29 | 265:58 | 902:02 | 1168:00 | 1196:08 | 29:54 | 96.0753 | 95.9807 | 9115:13 | 227:53 | 92.4464 | 92.2172 | 1591 | 26521 | 1196.13 | 39.775 | 29.9033 | 24:00 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40
17 | Magadi | 42 | 42 | 12:49 | 102:38 | 700:13 | 848:35 | 1548:48 | 1561:37 | 37:11 | 95.0435 | 95.0025 | 6169:03 | 146:53 | 95.067 | 94.9835 | 1958 | 64613 | 1561.62 | 46.619 | 37.1814 | 24:00 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42
18 | Chandapura | 19 | 19 | 6:32 | 57:08 | 195:22 | 170:40 | 366:02 | 372:34 | 19:37 | 97.4106 | 97.3644 | 1833:55 | 96:31 | 96.8062 | 96.7035 | 546 | 46726 | 372.57 | 28.7368 | 19.6089 | 24:00 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19
19 | Ramanagara | 39 | 39 | 26:42 | 108:25 | 740:08 | 862:44 | 1602:52 | 1629:34 | 41:47 | 94.4759 | 94.3839 | 6204:19 | 159:05 | 94.6617 | 94.5668 | 2757 | 38234 | 1629.57 | 70.6923 | 41.7838 | 24:00 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39
20 | Channapatna | 47 | 47 | 38:15 | 174:35 | 1287:26 | 582:48 | 1870:14 | 1908:29 | 40:36 | 94.6516 | 94.5422 | 8429:50 | 179:21 | 94.0012 | 93.8744 | 5515 | 62604 | 1908.48 | 117.3404 | 40.606 | 24:00 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47
21 | Kanakapura | 110 | 110 | 26:10 | 131:13 | 2849:05 | 1485:24 | 4334:29 | 4360:39 | 39:39 | 94.7037 | 94.6717 | 18644:07 | 169:30 | 94.2521 | 94.2113 | 5765 | 104097 | 4360.65 | 52.4091 | 39.6423 | 24:00 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110
NOTE:
1. 01 no. of New Feeder F-16 Serco feeder was added in Chintamani town emanating from 66/11 KV Chintamni station.
6. Reliability Index of Dodaballapura has reduced as 05 nos of feeders (F12, F14 of 66/11 KV Muss Budhigere and F18, F20, F29 of 66/11 KV Muss Devenahalli) were faulty due to cable fault, since the load change over was done, no load was affected.
Note: In Davanagere division 2 Nos of NJY feeders Neetigere & Nibgur are newly commissioned on Devarahally 66/11KV station.