## Annexure 1
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR THE MONTH OF SEPTEMBER-2019 OF FY 2019-20
ANX-I
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure (in Hrs) for FY 19-20 | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for Sept-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Davangere | 36 | 33 | 5:26 | 29:09 | 319:18 | 141:17 | 460:35 | 466:01 | 12:57 | 98.2231 | 98.2021 | 3322:54 | 92:18 | 97.9168 | 97.8984 | 653 | 165467 | 466 | 19.7879 | 14.1212 | 24:00 | 0.71667 | 60
2 | Chitradurga | 11 | 11 | 1:22 | 11:14 | 319:18 | 141:17 | 460:35 | 461:57 | 42:00 | 94.1846 | 94.1673 | 1414:21 | 128:35 | 97.0957 | 97.0725 | 947 | 43297 | 461.933 | 86.0909 | 41.9939 | 24:00 | 0.51667 | 60
3 | Tumkur | 30 | 30 | 9:15 | 66:03 | 319:18 | 141:17 | 460:35 | 469:50 | 15:40 | 97.8677 | 97.8249 | 2922:09 | 97:24 | 97.8324 | 97.7822 | 890 | 99896 | 469.82 | 29.6667 | 15.6607 | 24:00 | 0.11667 | 60
4 | BMAZ, North | 704 | 645 | 448:02 | 2480:58 | 2132:41 | 2830:24 | 4963:05 | 5411:07 | 7:41 | 99.0209 | 98.9325 | 1889.8579 | 64:26 | 98.6133 | 98.5331 | 7976 | 2571795 | 5411.12 | 12.3659 | 8.3893 | 24:00 | 0.83333 | 60 | 2624414 | 2595331 | 2633893
5 | BMAZ, South | 776 | 590 | 169:56 | 1690:47 | 2475:48 | 2745:13 | 5221:01 | 5390:57 | 6:57 | 99.0655 | 99.0351 | 1883.1069 | 58:14 | 98.7236 | 98.6739 | 8577 | 2581022 | 5390.95 | 14.5373 | 9.1372 | 24:00 | 0.23333 | 60
5 | Ramanagara | 4 | 4 | 1:39 | 9:54 | 17:18 | 17:18 | 34:36 | 36:15 | 9:04 | 98.7986 | 98.7413 | 181:19 | 45:20 | 99.0242 | 98.9679 | 45 | 38682 | 36.25 | 11.25 | 9.0625 | 24:00 | 0.083333 | 60
6 | Kolar | 17 | 17 | 6:00 | 25:52 | 158:03 | 607:05 | 765:08 | 771:08 | 45:22 | 93.7489 | 93.6999 | 3520:06 | 207:04 | 95.3201 | 95.2854 | 672 | 64658 | 771.1333 | 39.5294 | 45.3608 | 24:00 | 0.6 | 60
7 | CBPura | 9 | 9 | 4:50 | 142:51 | 132:00 | 95:10 | 227:10 | 232:00 | 25:47 | 96.4943 | 96.4198 | 1501:58 | 166:53 | 96.5616 | 96.2002 | 381 | 55868 | 232 | 42.3333 | 25.7778 | 24:00 | 0.36667 | 60
NOTE: | [23 empty] | 60
Total 15 nos of feeders were added in BMAZ North during the month of Sept-2019. 05 nos of feeders (F1,F2,F4,F7,F8,F9) from 66/11 KV Shoba City. F1 from Platinum City, F13 from Nandhini Layout muss, F9, F3 from Welcast, F8 from Yelahanka, F12 from Brigade, F4 from Hennur Muss, F30 from SRS Peenya, F10 from Solladevanahalli Muss.
Assitant General Manager-3(Elec) | [6 empty] | Chief General Manager(Elec) | [8 empty] | Deputy General Manager(Elec) | [7 empty] | 60
Operations-3, BESCOM | [6 empty] | Operations, BESCOM | [8 empty] | Operations-3,BESCOM | [7 empty] | 60

## Annexure II
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
B. RELIABILITY INDICES FOR TOWNS AND CITIES BESCOM FOR THE MONTH OF SEPTEMBER-2019 OF FY 2019-20
ANX-II
Sl. No | Name of the TOWNS & CITIES | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY 19-20 | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for Sept-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Jagalur | 1 | 1 | 1:45 | 29:55 | 23:21 | 11:27 | 34:48 | 36:33 | 36:33 | 95.1667 | 94.9236 | 155:07 | 155:07 | 97.1494 | 96.4682 | 68 | 7889 | 36.55 | 68 | 36.55 | 24:00 |  | 0.55 | 146:58 | 1 | 1 | 1 | 1 | 1 | 1
2 | Channagiri | 1 | 1 | 3:15 | 59:30 | 20:00 | 1:39 | 21:39 | 24:54 | 24:54 | 96.9931 | 96.5417 | 217:33 | 217:33 | 96.4014 | 95.0467 | 93 | 8270 | 24.09 | 93 | 24.09 | 24:00 |  | 0.38333 | 285:43 | 1 | 1 | 1 | 1 | 1 | 1
3 | Harihara | 11 | 11 | 1:30 | 13:30 | 57:13 | 13:30 | 70:43 | 72:13 | 6:34 | 99.1071 | 99.0882 | 958:01 | 87:06 | 98.045 | 98.017 | 278 | 43199 | 72.22 | 25.2727 | 6.5655 | 24:00 |  | 0.31667 | 169:27 | 11 | 11 | 11 | 11 | 11 | 11
4 | Honnali | 1 | 1 | 0:45 | 7:55 | 9:15 | 1:20 | 10:35 | 11:20 | 11:20 | 98.5301 | 98.4259 | 144:55 | 144:55 | 96.8807 | 96.7004 | 40 | 9316 | 11.33 | 40 | 11.33 | 24:00 |  | 0.25 |  | 2 | 2 | 2 | 2 | 2 | 2
5 | Nynamati | 1 | 1 | 0:30 | 0:30 | 7:15 | 1:40 | 8:55 | 9:25 | 9:25 | 98.7616 | 98.6921 | 9:25 | 9:25 | 99.797 | 99.7856 | 47 | 4810 | 9.42 | 47 | 9.42 | 24:00
6 | Harapanahalli | 4 | 4 | 0:55 | 4:35 | 12:35 | 32:30 | 45:05 | 46:00 | 11:30 | 98.4346 | 98.4028 | 330:55 | 82:44 | 98.1425 | 98.1164 | 60 | 14910 | 11.5 | 15 | 2.875 | 24:00 |  | 0.16667 | 382:34 | 4 | 4 | 4 | 4 | 4 | 4
7 | Holalkere | 1 | 1 | 0:55 | 9:00 | 18:25 | 13:40 | 32:05 | 33:00 | 33:00 | 95.544 | 95.4167 | 185:47 | 185:47 | 95.9749 | 95.77 | 95 | 4798 | 33 | 95 | 33 | 24:00 |  | 0.51667 | 695:22 | 1 | 1 | 1 | 1 | 1 | 1
8 | Hosadurga | 2 | 2 | 1:45 | 12:41 | 35:25 | 28:28 | 63:53 | 65:38 | 32:49 | 95.5637 | 95.4421 | 369:33 | 184:46 | 95.9373 | 95.7929 | 171 | 11838 | 65.63 | 85.5 | 32.815 | 24:00 |  | 0.083333 | 460:50 | 2 | 2 | 2 | 2 | 2 | 2
9 | Hiriyur | 3 | 3 | 9:25 | 35:49 | 26:50 | 31:16 | 58:06 | 67:31 | 22:30 | 97.3102 | 96.8742 | 333:00 | 111:00 | 97.7445 | 97.4727 | 186 | 3646 | 67.52 | 62 | 22.5067 | 24:00 |  | 0.11667 |  | 3 | 3 | 3 | 3 | 3 | 3
10 | Challakere | 7 | 7 | 9:45 | 37:10 | 340:36 | 199:18 | 539:54 | 549:39 | 78:31 | 89.2877 | 89.0942 | 1279:20 | 182:46 | 95.9596 | 95.8387 | 376 | 18473 | 549.65 | 53.7143 | 78.5214 | 24:00 |  | 0.76667 |  | 5 | 5 | 5 | 5 | 5 | 5
11 | Molakalmuru | 1 | 1 | 6:27 | 22:42 | 10:07 | 19:47 | 29:54 | 36:21 | 36:21 | 95.8472 | 94.952 | 156:42 | 156:42 | 96.949 | 96.4323 | 89 | 1002 | 36.33 | 89 | 36.33 | 24:00 |  | 0.53333 |  | 1 | 1 | 1 | 1 | 1 | 1
12 | Tumkur | 6 | 6 | 21:36 | 98:36 | 150:00 | 64:00 | 214:00 | 235:36 | 39:16 | 95.0463 | 94.5463 | 1313:40 | 218:57 | 95.3891 | 95.0149 | 397 | 36534 | 235.6 | 66.1667 | 39.2667 | 24:00 |  | 0.05 | [5 empty] | 6 | 6
13 | Tiptur | 11 | 11 | 27:39 | 134:12 | 221:00 | 161:00 | 382:00 | 409:39 | 37:14 | 95.1768 | 94.8277 | 2572:28 | 233:52 | 94.9531 | 94.6753 | 766 | 33646 | 409.65 | 69.6364 | 37.2409 | 24:00 |  | 0.45 | [5 empty] | 11 | 11
14 | Madhugiri | 8 | 8 | 36:23 | 190:22 | 214:00 | 41:00 | 255:00 | 291:23 | 36:25 | 95.5729 | 94.9411 | 1881:32 | 235:11 | 95.1868 | 94.645 | 491 | 53736 | 291.03 | 61.375 | 36.3787 | 24:00 |  | 0 | [5 empty] | 8 | 8
15 | Srinivaspura | 4 | 4 | 10:55 | 56:30 | 58:05 | 61:00 | 119:05 | 130:00 | 32:30 | 95.8652 | 95.4861 | 887:35 | 221:54 | 95.2693 | 94.9477 | 239 | 12320 | 130 | 59.75 | 32.5 | 24:00 | 52.75 | 0.25 |  | 4 | 4 | 4 | 4 | 4 | 4
16 | KGF | 30 | 30 | 0:59 | 13:00 | 477:31 | 191:25 | 668:56 | 669:55 | 22:20 | 96.9031 | 96.8985 | 5229:45 | 174:20 | 96.0407 | 96.0309 | 1459 | 99066 | 669.9167 | 48.6333 | 22.3306 | 24:00 | 47.8667 | 0.88333 |  | 30 | 30 | 30 | 30 | 30 | 30
17 | CB Pura | 11 | 11 | 71:35 | 168:40 | 145:34 | 92:15 | 237:49 | 309:24 | 28:08 | 96.9973 | 96.0934 | 1516:51 | 137:54 | 97.2094 | 96.8603 | 412 | 40470 | 309.4 | 37.4545 | 28.1273 | 24:00 | 33.3636 | 0.21667 |  | 11 | 11 | 11 | 11 | 11 | 11
18 | Chintamani | 16 | 16 | 1:35 | 28:09 | 263:20 | 160:20 | 423:40 | 425:15 | 26:35 | 96.3223 | 96.3086 | 2673:12 | 167:05 | 96.236 | 96.1959 | 510 | 35925 | 425.25 | 31.875 | 26.5781 | 24:00 | 28.8 | 0.66667 |  | 15 | 15 | 15 | 15 | 15 | 15
19 | Devanahalli | 60 | 60 | 67:44 | 564:55 | 1463:00 | 1826:32 | 3289:32 | 3357:16 | 55:57 | 92.3853 | 92.2285 | 1590.4562 | 636:11 | 85.7293 | 85.515 | 3281 | 66640 | 3357.2667 | 54.6833 | 55.9544 | 24:00 | 1.6833 | 0.35 |  | 60 | 60 | 60 | 60 | 60 | 60
20 | Hosakote | 61 | 61 | 196:11 | 561:49 | 746:05 | 640:05 | 1386:10 | 1582:21 | 25:56 | 96.8439 | 96.3972 | 10615:42 | 174:02 | 96.2473 | 96.0376 | 2511 | 66443 | 1582.35 | 41.1639 | 25.9402 | 24:00 | 1.2623 | 0.4 |  | 61 | 61 | 61 | 61 | 61 | 61
21 | Nelamangala | 67 | 67 | 12:07 | 97:39 | 554:41 | 424:10 | 978:51 | 990:58 | 14:47 | 97.9709 | 97.9458 | 8641:12 | 128:58 | 97.0966 | 97.0635 | 2057 | 139043 | 990.9667 | 30.7015 | 14.7905 | 24:00 | 0.93939 | 0.68333 |  | 66 | 66 | 66 | 66 | 66 | 66
22 | Doddaballapura | 54 | 54 | 11:06 | 365:38 | 652:43 | 1597:01 | 2249:44 | 2260:50 | 41:52 | 94.2136 | 94.1851 | 11890:36 | 220:12 | 95.1406 | 94.9864 | 1536 | 64472 | 2260.8333 | 28.4444 | 41.8673 | 24:00 | 2.4151 | 0.41667 |  | 54 | 54 | 53 | 53 | 53 | 53
23 | Bangalore south | 20 | 20 | 15:16 | 485:59 | 482:34 | 328:51 | 811:25 | 826:41 | 41:20 | 94.3652 | 94.2591 | 4418:03 | 220:54 | 95.5236 | 94.9703 | 1268 | 36282 | 826.6833 | 63.4 | 41.3342 | 24:00 | 0 | 0.23333 |  | 20 | 20 | 20 | 20 | 20 | 20
24 | Magadi | 11 | 11 | 13:29 | 261:20 | 148:48 | 180:53 | 329:41 | 343:10 | 31:12 | 95.8373 | 95.6671 | 2711:13 | 246:28 | 94.929 | 94.3881 | 198 | 26660 | 343.1667 | 18 | 31.197 | 24:00 | 29.3333 | 0.68333 |  | 12 | 12 | 12 | 12 | 12 | 12
25 | Anekal | 127 | 127 | 37:45 | 2699:09 | 1883:52 | 868:55 | 2752:47 | 2790:32 | 21:58 | 96.9895 | 96.9482 | 1138.0757 | 215:04 | 95.5871 | 95.1032 | 2329 | 239663 | 2790.5333 | 18.3386 | 21.9727 | 24:00 | 38.1102 | 0.93333 |  | 127 | 127 | 127 | 127 | 127 | 127
26 | Ramanagara | 35 | 35 | 12:16 | 93:41 | 1109:15 | 181:04 | 1290:19 | 1302:35 | 37:13 | 94.8797 | 94.831 | 5612:09 | 160:21 | 96.4101 | 96.3491 | 543 | 5667 | 1302.5833 | 15.5143 | 37.2167 | 24:00 | 28.8286 | 0.61667 |  | 35 | 35 | 35 | 35 | 35 | 35
27 | Channapatna | 7 | 7 | 4:15 | 58:29 | 21:55 | 22:04 | 43:59 | 48:14 | 6:53 | 99.1273 | 99.043 | 1702:20 | 243:11 | 94.6531 | 94.4629 | 256 | 33104 | 48.2333 | 36.5714 | 6.8905 | 24:00 | 94.1429 | 0.53333 |  | 7 | 7 | 7 | 7 | 7 | 7
28 | Kanakapura | 22 | 22 | 6:15 | 51:40 | 548:00 | 314:44 | 862:44 | 868:59 | 39:30 | 94.5535 | 94.514 | 2942:37 | 133:45 | 97.008 | 96.9546 | 2418 | 19434 | 868.9833 | 109.9091 | 39.4992 | 24:00 | 88.2273 | 0.78333 |  | 22 | 22 | 22 | 22 | 22 | 22
NOTE:

## ANX-III
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
C. RELIABILITY INDICES FOR RURAL AREAS BESCOM FOR THE MONTH OF SEPTEMBER-19 OF FY 2019-20
ANX-III
Sl. No | Name of the DIVISION | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY 19-20 | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for Sept-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Davanagere | 280 | 278 | 187:20 | 1283:42 | 6094:46 | 6254:41 | 12349:28 | 12536:48 | 44:46 | 93.8743 | 93.7814 | 3027.7488 | 259:31 | 94.1954 | 94.091 | 14532 | 276847 | 12536.78 | 52.2734 | 45.0963 | 24:00 | 276 | 274 | 276 | 274 |  | 276 | 274 | 276 | 274
2 | Harihara | 197 | 197 | 17:40 | 111:10 | 5347:37 | 5851:32 | 11199:09 | 11216:49 | 56:56 | 92.1044 | 92.0919 | 2817.7868 | 343:17 | 92.1967 | 92.1839 | 10299 | 208973 | 11216.82 | 52.2792 | 56.9382 | 24:00 | 197 | 197 | 197 | 197 |  | 197 | 197 | 197 | 197
3 | Chitradurga | 178 | 178 | 85:20 | 615:15 | 2281:58 | 3176:46 | 5458:44 | 5544:04 | 31:09 | 95.7407 | 95.6741 | 1270.0736 | 171:15 | 96.1797 | 96.101 | 14500 | 218598 | 5544.06 | 81.4607 | 31.1464 | 24:00 | 178 | 178 | 178 | 178 |  | 178 | 178 | 178 | 178
4 | Hiriyur | 215 | 215 | 66:45 | 198:08 | 5378:53 | 5459:56 | 10838:49 | 10905:34 | 50:43 | 92.9982 | 92.9551 | 2637.6268 | 294:26 | 93.3171 | 93.2962 | 12281 | 258481 | 10905.56 | 57.1209 | 50.7235 | 24:00 | 215 | 215 | 215 | 215 |  | 215 | 215 | 215 | 215
5 | Tumkur | 322 | 322 | 65:18 | 373:18 | 4035:00 | 1481:00 | 5516:00 | 5581:18 | 17:20 | 97.6208 | 97.5926 | 2338.9217 | 174:20 | 96.0571 | 96.0307 | 8576 | 262465 | 5581.3 | 26.6335 | 17.3332 | 24:00 | 322 | 322 | 322 | 322 |  | 312 | 312 | 322 | 322
6 | Tiptur | 205 | 205 | 55:06 | 308:06 | 2718:00 | 5756:00 | 8474:00 | 8529:06 | 41:36 | 94.2588 | 94.2215 | 2327.3387 | 272:28 | 93.8305 | 93.7962 | 6456 | 210785 | 8529.1 | 31.4927 | 41.6054 | 24:00 | 205 | 205 | 194 | 194 | -11 | 194 | 194 | 194 | 194
7 | Madhugiri | 322 | 322 | 60:14 | 366:14 | 6678:00 | 8453:00 | 15131:00 | 15191:14 | 47:11 | 93.4735 | 93.4475 | 3104.3481 | 231:23 | 94.7577 | 94.7318 | 6794 | 456836 | 15191.22 | 21.0994 | 47.1777 | 24:00 | 322 | 322 | 307 | 307 | -15 | 307 | 307 | 307 | 307
8 | Kunigal | 109 | 109 | 40:05 | 211:05 | 1601:00 | 3623:00 | 5224:00 | 5264:05 | 48:18 | 93.3435 | 93.2925 | 1298.5781 | 285:56 | 93.5339 | 93.4899 | 2883 | 46120 | 5264.06 | 26.4495 | 48.2941 | 24:00 | 109 | 109 | 105 | 105 | -4 | 105 | 105 | 105 | 105
9 | Kolar | 164 | 164 | 1030:55 | 4071:52 | 1878:00 | 2617:25 | 4495:25 | 5526:20 | 33:42 | 96.1929 | 95.3198 | 1892.684 | 276:59 | 94.2589 | 93.6936 | 5390 | 149044 | 5526.3333 | 32.8659 | 33.6972 | 24:00 | 164 | 164 | 160 | 160 |  | 155 | 155 | 160 | 160
10 | KGF | 198 | 183 | 1:42 | 55:56 | 2778:10 | 5221:16 | 7999:26 | 8001:08 | 40:25 | 94.3887 | 94.3875 | 2259.4716 | 273:53 | 93.7707 | 93.7642 | 7748 | 292779 | 8001.1333 | 42.3388 | 43.722 | 24:00 | 197 | 183 | 197 | 183 |  | 197 | 183 | 197 | 183
11 | CB Pura | 194 | 194 | 1048:00 | 3114:15 | 2504:03 | 2532:03 | 5036:06 | 6084:06 | 31:22 | 96.3945 | 95.6443 | 1427.9611 | 176:39 | 96.3433 | 95.9778 | 7892 | 204799 | 6084.1 | 40.6804 | 31.3613 | 24:00 | 194 | 194 | 194 | 194 |  | 194 | 194 | 194 | 194
12 | Chintamani | 148 | 148 | 3:45 | 84:59 | 1239:01 | 3297:06 | 4536:07 | 4539:52 | 30:40 | 95.7431 | 95.7396 | 1107.4764 | 179:35 | 95.924 | 95.911 | 2835 | 190311 | 4539.8667 | 19.1554 | 30.6748 | 24:00 | 147 | 147 | 147 | 147 |  | 147 | 147 | 147 | 147
13 | Devanahalli | 33 | 33 | 39:27 | 178:06 | 1053:00 | 1483:34 | 2536:34 | 2576:01 | 78:04 | 89.3242 | 89.1582 | 17463:37 | 529:12 | 88.0737 | 87.9508 | 99.9944 | 36850 | 2576.0194 | 3.0301 | 78.0612 | 24:00 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33
14 | Hosakote | 32 | 32 | 60:25 | 234:07 | 182:55 | 445:47 | 628:42 | 689:07 | 21:32 | 97.2713 | 97.009 | 4464:58 | 139:32 | 96.9897 | 96.8231 | 99.9986 | 26828 | 689.1167 | 3.125 | 21.5349 | 24:00 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32
15 | Nelamangala | 17 | 17 | 5:10 | 78:44 | 250:29 | 271:19 | 521:48 | 526:58 | 31:00 | 95.7369 | 95.6947 | 3672:48 | 216:03 | 95.1863 | 95.0809 | 99.996 | 16170 | 526.9667 | 5.8821 | 30.998 | 24:00 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17
16 | Doddaballapura | 40 | 40 | 22:46 | 291:15 | 259:17 | 903:30 | 1162:47 | 1185:33 | 29:38 | 95.9626 | 95.8835 | 10300:46 | 257:31 | 94.3024 | 94.1366 | 99.9979 | 60914 | 1185.55 | 2.4999 | 29.6388 | 24:00 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40
17 | Magadi | 42 | 42 | 17:54 | 120:32 | 546:23 | 879:35 | 1425:58 | 1443:52 | 34:23 | 95.2845 | 95.2253 | 7612:55 | 181:16 | 95.9383 | 95.873 | 1838 | 52468 | 1443.8667 | 43.7619 | 34.3778 | 24:00 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42
18 | Chandapura | 19 | 19 | 15:00 | 72:08 | 138:54 | 98:13 | 237:07 | 252:07 | 13:16 | 98.2667 | 98.157 | 2086:02 | 109:47 | 97.5866 | 97.5002 | 339 | 44202 | 252.1167 | 17.8421 | 13.2693 | 24:00 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19
19 | Ramanagara | 39 | 39 | 16:35 | 125:00 | 703:16 | 912:20 | 1615:36 | 1632:11 | 41:51 | 94.2464 | 94.1874 | 7836:30 | 200:56 | 95.4979 | 95.425 | 832 | 34616 | 1632.1833 | 21.3333 | 41.8509 | 24:00 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39
20 | Channapatna | 47 | 47 | 18:27 | 193:02 | 1064:33 | 1424:52 | 2489:25 | 2507:52 | 53:22 | 92.6436 | 92.589 | 10937:42 | 232:43 | 94.7949 | 94.7013 | 1025 | 55557 | 2507.8667 | 21.8085 | 53.3589 | 24:00 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47
21 | Kanakapura | 110 | 110 | 10:12 | 141:25 | 2655:43 | 2473:12 | 5128:55 | 5139:07 | 46:43 | 93.5241 | 93.5112 | 23783:14 | 216:13 | 95.1064 | 95.0772 | 354 | 103670 | 5139.1167 | 3.2182 | 46.7192 | 24:00 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110
NOTE:
01. 02 nos of new feeders are added in Davanagere Division during the month of Sept-2019, F-21 Taralabalu NJY Feeder in SRS, Davangere & F-11 Yaraghatihalli NJY in Devarahalli Station
6. Reliability Index of Dodaballapura has reduced as 05 nos of feeders (F12, F14 of 66/11 KV Muss Budhigere and F18, F20, F29 of 66/11 KV Muss Devenahalli) were faulty due to cable fault, since the load change over was done, no load was affected.
Note: In Davanagere division 2 Nos of NJY feeders Neetigere & Nibgur are newly commissioned on Devarahally 66/11KV station.