## Annexure 1
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
A. RELIABILITY INDICES FOR DISTRICT HEAD QUARTERS IN BESCOM FOR THE MONTH OF DECEMBER-2019 FOR THE FY 2019-20
ANX-I
Sl. No | Name of the District Head Quarters | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure (in Hrs) for FY 19-20 | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for DEC-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4 | 275
1 | Davangere | 36 | 33 | 4:14 | 54:52 | 227:46 | 112:04 | 339:50 | 344:04 | 9:33 | 98.7312 | 98.7154 | 4549:08 | 126:22 | 98.1085 | 98.0854 | 645 | 166520 | 344.05 | 19.5455 | 10.4258 | 24:00 | 0.71667 | 60
2 | Chitradurga | 11 | 11 | 1:05 | 15:04 | 115:35 | 86:36 | 202:11 | 203:16 | 18:29 | 97.5295 | 97.5163 | 2037:12 | 185:12 | 97.2147 | 97.1939 | 826 | 43712 | 203.26 | 75.0909 | 18.4782 | 24:00 | 0.51667 | 60
3 | Tumkur | 30 | 30 | 19:00 | 104:03 | 318:00 | 63:00 | 381:00 | 400:00 | 13:20 | 98.293 | 98.2079 | 4229:09 | 140:58 | 97.9166 | 97.8641 | 586 | 100018 | 400 | 19.5333 | 13.3333 | 24:00 | 0.11667 | 60
4 | BMAZ, North | 707 | 646 | 231:54 | 3605:01 | 1160:53 | 2497:41 | 3658:34 | 3890:28 | 5:30 | 99.3045 | 99.2604 | 2540.6975 | 86:15 | 98.7705 | 98.6932 | 4900 | 2620174 | 3890.47 | 7.5851 | 6.0224 | 24:00 | 0.83333 | 60 | 2624414 | 2595331 | 2633893
5 | BMAZ, South | 776 | 593 | 188:52 | 2281:34 | 2072:51 | 1845:41 | 3918:32 | 4107:24 | 5:18 | 99.3213 | 99.2886 | 2493.2617 | 77:07 | 98.8762 | 98.8316 | 6382 | 2802974 | 4107.24 | 10.7622 | 6.9262 | 24:00 | 0.8 | 60
5 | Ramanagara | 4 | 4 | 1:41 | 14:32 | 17:15 | 6:15 | 23:30 | 25:11 | 6:18 | 99.2103 | 99.1539 | 252:37 | 63:09 | 99.0981 | 99.0431 | 39 | 39658 | 25.166 | 9.75 | 6.2915 | 24:00 | 0.083333 | 60 |  | 275
6 | Kolar | 7 | 7 | 0:00 | 31:57 | 98:23 | 36:41 | 135:04 | 135:04 | 19:18 | 97.4066 | 97.4066 | 5537:02 | 791:00 | 88.0842 | 88.0151 | 169 | 21804 | 135.06 | 24.1429 | 19.2943 | 24:00 | 0.6 | 60
7 | CBPura | 9 | 9 | 94:00 | 276:31 | 112:30 | 31:10 | 143:40 | 237:40 | 26:24 | 97.8544 | 96.4506 | 2204:58 | 245:00 | 96.7535 | 96.2879 | 270 | 59041 | 237.66 | 30 | 26.4067 | 24:00 | 0.36667 | 60
NOTE: | [23 empty] | 60
1. F16,F17 feeders emanating from 220/66/11 KV GIS R/s Manyatha commissioned during the month of DEC-19 in BMAZ north zone,
2. 10 number of feeders are included in the rural areas of Kolar division in the ANX-3, from the District headquarters of ANX-1.
Assitant General Manager-3(Elec) | [6 empty] | Chief General Manager(Elec) | [8 empty] | Deputy General Manager(Elec) | [7 empty] | 60
Operations-3, BESCOM | [6 empty] | Operations, BESCOM | [8 empty] | Operations-3,BESCOM | [7 empty] | 60
183

## Annexure II
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
B. RELIABILITY INDICES FOR TOWNS AND CITIES BESCOM FOR THE MONTH OF DECEMBER-2019 FOR THE FY 2019-20
ANX-II
Sl. No | Name of the TOWNS & CITIES | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY 19-20 | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for DEC-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder 11 in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Jagalur | 1 | 1 | 7:20 | 45:15 | 11:27 | 1:03 | 12:30 | 19:50 | 19:50 | 98.3199 | 97.3342 | 195:42 | 195:42 | 97.7205 | 97.0349 | 26 | 7969 | 19.83 | 26 | 19.83 | 24:00 |  | 0.55 | 146:58 | 1 | 1 | 1 | 1 | 1 | 1
2 | Channagiri | 1 | 1 | 5:55 | 81:18 | 19:00 | 1:06 | 20:06 | 26:01 | 26:01 | 97.2984 | 96.5031 | 312:45 | 312:45 | 96.4932 | 95.2614 | 82 | 8372 | 26.016 | 82 | 26.016 | 24:00 |  | 0.38333 | 285:43 | 1 | 1 | 1 | 1 | 1 | 1
3 | Harihara | 11 | 11 | 2:05 | 21:40 | 131:00 | 17:46 | 148:46 | 150:51 | 13:43 | 98.1822 | 98.1568 | 1510:15 | 137:18 | 97.9496 | 97.9198 | 286 | 43199 | 150.85 | 26 | 13.7136 | 24:00 |  | 0.31667 | 169:27 | 11 | 11 | 11 | 11 | 11 | 11
4 | Honnali | 1 | 1 | 0:50 | 10:00 | 9:50 | 0:50 | 10:40 | 11:30 | 11:30 | 98.5663 | 98.4543 | 183:05 | 183:05 | 97.3775 | 97.226 | 27 | 9316 | 11.5 | 27 | 11.5 | 24:00 |  | 0.25 |  | 2 | 2 | 2 | 2 | 2 | 2
5 | Nynamati | 1 | 1 | 1:05 | 4:45 | 5:00 | 2:10 | 7:10 | 8:15 | 8:15 | 99.0367 | 98.8911 | 49:23 | 49:23 | 99.3237 | 99.2518 | 34 | 4810 | 8.25 | 34 | 8.25 | 24:00
6 | Harapanahalli | 4 | 4 | 0:55 | 6:55 | 14:40 | 3:20 | 18:00 | 18:55 | 4:44 | 99.3952 | 99.3644 | 441:10 | 110:17 | 98.3551 | 98.3289 | 57 | 14910 | 18.92 | 14.25 | 4.73 | 24:00 |  | 0.16667 | 237:06 | 4 | 4 | 4 | 4 | 4 | 4
7 | Holalkere | 1 | 1 | 1:10 | 12:25 | 17:05 | 13:06 | 30:11 | 31:21 | 31:21 | 95.9431 | 95.7863 | 280:53 | 280:53 | 95.9323 | 95.7442 | 84 | 4810 | 31.35 | 84 | 31.35 | 24:00 |  | 0.51667 | 504:47 | 1 | 1 | 1 | 1 | 1 | 1
8 | Hosadurga | 2 | 2 | 1:42 | 17:53 | 32:45 | 28:20 | 61:05 | 62:47 | 31:24 | 95.8949 | 95.7807 | 560:16 | 280:08 | 95.891 | 95.7556 | 161 | 12004 | 62.78 | 80.5 | 31.39 | 24:00 |  | 0.083333 | 324:31 | 2 | 2 | 2 | 2 | 2 | 2
9 | Hiriyur | 3 | 3 | 7:15 | 54:09 | 31:54 | 8:53 | 40:47 | 48:02 | 16:01 | 98.1728 | 97.8479 | 569:10 | 189:43 | 97.3989 | 97.1255 | 75 | 3759 | 48.03 | 25 | 16.01 | 24:00 |  | 0.11667 |  | 3 | 3 | 3 | 3 | 3 | 3
10 | Challakere | 7 | 7 | 7:30 | 56:09 | 105:35 | 63:46 | 169:21 | 176:51 | 25:16 | 96.7483 | 96.6041 | 1899:31 | 271:22 | 96.01 | 95.8885 | 297 | 18593 | 176.85 | 42.4286 | 25.2643 | 24:00 |  | 0.76667 |  | 5 | 5 | 5 | 5 | 5 | 5
11 | Molakalmuru | 1 | 1 | 4:46 | 34:46 | 23:56 | 18:11 | 42:07 | 46:53 | 46:53 | 94.3392 | 93.6975 | 268:25 | 268:25 | 96.4598 | 95.9332 | 40 | 1012 | 43.88 | 40 | 43.88 | 24:00 |  | 0.53333 |  | 1 | 1 | 1 | 1 | 1 | 1
12 | Tumkur | 6 | 6 | 11:23 | 146:59 | 51:24 | 27:21 | 78:45 | 90:08 | 15:01 | 98.2359 | 97.981 | 1816:40 | 302:47 | 95.7836 | 95.4124 | 217 | 36709 | 90.12 | 36.1667 | 15.02 | 24:00 |  | 0.05 | [5 empty] | 6 | 6
13 | Tiptur | 11 | 11 | 15:06 | 209:42 | 149:36 | 54:22 | 203:58 | 219:04 | 19:55 | 97.5077 | 97.3232 | 3696:54 | 336:05 | 95.1967 | 94.9078 | 617 | 33646 | 219.06 | 56.0909 | 19.9145 | 24:00 |  | 0.45 | [5 empty] | 11 | 11
14 | Madhugiri | 8 | 8 | 9:44 | 279:21 | 127:00 | 18:19 | 145:19 | 155:04 | 19:23 | 97.5585 | 97.3948 | 2581:22 | 322:40 | 95.6401 | 95.111 | 264 | 53736 | 155.05 | 33 | 19.3813 | 24:00 |  | 0 | [5 empty] | 8 | 8
15 | Srinivaspura | 4 | 4 | 0:40 | 69:40 | 52:15 | 20:10 | 72:25 | 73:05 | 18:16 | 97.5666 | 97.5442 | 1226:30 | 306:37 | 95.6181 | 95.3542 | 179 | 21978 | 73.08 | 44.75 | 18.27 | 24:00 | 52.75 | 0.25 |  | 4 | 4 | 4 | 4 | 4 | 4
16 | KGF | 30 | 30 | 0:00 | 15:24 | 387:03 | 112:59 | 500:02 | 500:02 | 16:40 | 97.7597 | 97.7597 | 6796:08 | 226:32 | 96.5754 | 96.5676 | 983 | 89910 | 500.03 | 32.7667 | 16.6677 | 24:00 | 47.8667 | 0.88333 |  | 30 | 30 | 30 | 30 | 30 | 30
17 | CB Pura | 11 | 11 | 14:20 | 206:40 | 102:00 | 33:10 | 135:10 | 149:30 | 13:35 | 98.3484 | 98.1733 | 2003:41 | 182:09 | 97.5248 | 97.2401 | 279 | 52340 | 149.5 | 25.3636 | 13.5909 | 24:00 | 33.3636 | 0.21667 |  | 11 | 11 | 11 | 11 | 11 | 11
18 | Chintamani | 16 | 16 | 0:55 | 31:59 | 188:53 | 75:43 | 264:36 | 265:31 | 16:36 | 97.7772 | 97.7695 | 3696:10 | 231:01 | 96.5301 | 96.4998 | 261 | 56591 | 265.52 | 16.3125 | 16.595 | 24:00 | 28.8 | 0.66667 |  | 15 | 15 | 15 | 15 | 15 | 15
19 | Devanahalli | 60 | 60 | 81:23 | 734:12 | 988:15 | 444:26 | 1432:41 | 1514:04 | 25:14 | 96.7906 | 96.6083 | 1814.1618 | 725:40 | 89.1905 | 89.0051 | 2403 | 70978 | 1514.066 | 40.05 | 25.2344 | 24:00 | 1.6833 | 0.35 |  | 60 | 60 | 60 | 60 | 60 | 60
20 | Hosakote | 60 | 60 | 80:56 | 806:44 | 724:46 | 688:17 | 1413:03 | 1493:59 | 24:54 | 96.8346 | 96.6533 | 14829:54 | 247:10 | 96.4588 | 96.2551 | 2470 | 95244 | 1493.98 | 41.1667 | 24.8997 | 24:00 | 1.2623 | 0.4 |  | 61 | 61 | 61 | 61 | 61 | 61
21 | Nelamangala | 68 | 68 | 7:15 | 155:16 | 606:06 | 223:47 | 829:53 | 837:08 | 12:19 | 98.3597 | 98.3453 | 11849:46 | 174:16 | 97.3943 | 97.3597 | 1484 | 163093 | 837.01 | 21.8235 | 12.309 | 24:00 | 0.93939 | 0.68333 |  | 66 | 66 | 66 | 66 | 66 | 66
22 | Doddaballapura | 54 | 54 | 11:56 | 426:19 | 558:01 | 1741:25 | 2299:26 | 2311:22 | 42:48 | 94.2766 | 94.2469 | 20127:42 | 372:44 | 94.4721 | 94.3525 | 1520 | 111288 | 2311.37 | 28.1481 | 42.8031 | 24:00 | 2.4151 | 0.41667 |  | 54 | 54 | 53 | 53 | 53 | 53
23 | Bangalore south | 21 | 21 | 4:45 | 512:35 | 123:58 | 291:00 | 414:58 | 419:43 | 19:59 | 97.344 | 97.3136 | 5961:59 | 283:54 | 96.0683 | 95.6984 | 684 | 52614 | 419.72 | 32.5714 | 19.9867 | 24:00 | 0 | 0.23333 |  | 20 | 20 | 20 | 20 | 20 | 20
24 | Magadi | 11 | 11 | 7:28 | 291:24 | 118:41 | 114:46 | 233:27 | 240:55 | 21:54 | 97.1475 | 97.0562 | 3791:41 | 344:42 | 95.1787 | 94.7773 | 298 | 33675 | 240.92 | 27.0909 | 21.9018 | 24:00 | 29.3333 | 0.68333 |  | 12 | 12 | 12 | 12 | 12 | 12
25 | Anekal | 167 | 167 | 24:25 | 2782:28 | 1622:19 | 773:36 | 2395:55 | 2420:20 | 14:30 | 98.0717 | 98.052 | 1504.1528 | 216:10 | 96.9772 | 96.7248 | 3249 | 336892 | 2420.33 | 19.4551 | 14.493 | 24:00 | 38.1102 | 0.93333 |  | 127 | 127 | 127 | 127 | 127 | 127
26 | Ramanagara | 43 | 43 | 17:19 | 203:00 | 354:51 | 110:52 | 465:43 | 483:02 | 11:14 | 98.5443 | 98.4901 | 8032:56 | 186:49 | 97.241 | 97.1695 | 807 | 27734 | 483.03 | 18.7674 | 11.2333 | 24:00 | 28.8286 | 0.61667 |  | 35 | 35 | 35 | 35 | 35 | 35
27 | Channapatna | 5 | 5 | 7:37 | 132:43 | 88:24 | 7:04 | 95:28 | 103:05 | 20:37 | 97.4337 | 97.2289 | 2014:38 | 402:56 | 94.2972 | 93.8951 | 177 | 41876 | 103.08 | 35.4 | 20.616 | 24:00 | 94.1429 | 0.53333 |  | 7 | 7 | 7 | 7 | 7 | 7
28 | Kanakapura | 26 | 26 | 10:54 | 97:08 | 421:21 | 175:34 | 596:55 | 607:49 | 23:23 | 96.9142 | 96.8579 | 4844:40 | 186:20 | 97.2334 | 97.1768 | 604 | 37910 | 607.82 | 23.2308 | 23.3777 | 24:00 | 88.2273 | 0.78333 |  | 22 | 22 | 22 | 22 | 22 | 22
NOTE: New feeder F11 WINTAC emanating from 66/11 Kv T Begur MUSS was commissioned during the month of DEC-19 in Nelmangala town.

## ANX-III
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
C. RELIABILITY INDICES FOR RURAL AREAS BESCOM FOR THE MONTH OF DECEMBER-19 FOR THE FY 2019-20
ANX-III
Sl. No | Name of the DIVISION | Total No. of 11 KV Feeders | Total No. of Feeders affected | Outage due to Incoming Supply Failure (In Hrs) | Cumulative Outage due to Incoming Supply Failure ( in Hrs) for FY 19-20 | Outage at 11 KV Level (in Hrs) |  |  | Reliability for the month |  |  |  | Reliability for cumulative period FY 19-20 |  |  |  | SAIFI & SAIDI of feeders for DEC-19
[6 empty] | Scheduled Outage | Unscheduled Outage | Total | Sum of outage duration of all feeders (in Hrs) | Outage duration per feeder (in Hrs/ Fdr) | Feeder Reliability Index at 11 KV feeder in % | Reliability of supply of power to consumers in % | Cumulative outage duration of all feeders (In Hrs) for FY -19-20 | Cumulative outage duration of all feeders (In Hrs/ Feeder) | Cumulative feeder relaibility Index @ 11 KV feeder level in % | Cumulative relaibility of supply of Power to consumers | Total No. of Feeders Interruption | Total number of consmers connected with the feeder | Sum of outage duration of all feeders (in Hrs) | SAIFI | SAIDI
1 | 2 | 3 | 4 | 5 | 5a | 6 | 7 | 8=6+7 | 9=5+8 | 10=9/3 | 11* | 12** | 13 | 14=13/3 | 15 | 16 | 17 | 18 | 19 | 20=17/4 | 21=19/4
1 | Davanagere | 280 | 278 | 250:43 | 2017:29 | 5755:44 | 2681:28 | 8437:12 | 8687:55 | 31:02 | 95.9499 | 95.8295 | 4664.5827 | 399:49 | 94.0513 | 93.9421 | 14299 | 276849 | 8687.9 | 51.4353 | 31.2514 | 24:00 | 276 | 274 | 276 | 274 |  | 276 | 274 | 276 | 274
2 | Harihara | 197 | 197 | 26:15 | 195:40 | 5881:32 | 2104:29 | 7986:01 | 8012:16 | 40:40 | 94.5513 | 94.5334 | 4307.9312 | 524:49 | 92.0632 | 92.0481 | 8734 | 208975 | 8012.26 | 44.335 | 40.6714 | 24:00 | 197 | 197 | 197 | 197 |  | 197 | 197 | 197 | 197
3 | Chitradurga | 178 | 178 | 110:25 | 920:15 | 2044:36 | 3078:44 | 5123:20 | 5233:45 | 29:24 | 96.1313 | 96.048 | 1931.5097 | 260:26 | 96.1324 | 96.0541 | 13231 | 218599 | 5233.75 | 74.3315 | 29.4031 | 24:00 | 178 | 178 | 178 | 178 |  | 178 | 178 | 178 | 178
4 | Hiriyur | 215 | 215 | 37:35 | 308:14 | 3183:14 | 4070:54 | 7254:08 | 7291:43 | 33:55 | 95.465 | 95.4415 | 3871.7139 | 432:11 | 93.4734 | 93.4516 | 10807 | 258482 | 7291.72 | 50.2651 | 33.915 | 24:00 | 215 | 215 | 215 | 215 |  | 215 | 215 | 215 | 215
5 | Tumkur | 322 | 322 | 60:00 | 558:18 | 4032:00 | 5687:00 | 9719:00 | 9779:00 | 30:22 | 95.9431 | 95.9181 | 3895.755 | 290:22 | 95.6268 | 95.6005 | 9032 | 262695 | 9779 | 28.0497 | 30.3696 | 24:00 | 322 | 322 | 322 | 322 |  | 312 | 312 | 322 | 322
6 | Tiptur | 205 | 205 | 45:00 | 454:06 | 2614:00 | 4556:00 | 7170:00 | 7215:00 | 35:12 | 95.299 | 95.2695 | 3504.7077 | 410:18 | 93.8168 | 93.7832 | 9053 | 215849 | 7215 | 44.161 | 35.1951 | 24:00 | 205 | 205 | 194 | 194 | -11 | 194 | 194 | 194 | 194
7 | Madhugiri | 322 | 322 | 54:00 | 556:14 | 4770:00 | 3704:00 | 8474:00 | 8528:00 | 26:29 | 96.4628 | 96.4403 | 4752.0148 | 354:11 | 94.6597 | 94.6335 | 8995 | 456916 | 8528 | 27.9348 | 26.4845 | 24:00 | 322 | 322 | 307 | 307 | -15 | 307 | 307 | 307 | 307
8 | Kunigal | 109 | 109 | 35:00 | 312:05 | 1505:00 | 1811:00 | 3316:00 | 3351:00 | 30:45 | 95.911 | 95.8679 | 1766.9531 | 389:03 | 94.1486 | 94.1052 | 2361 | 46160 | 3351 | 21.6606 | 30.7431 | 24:00 | 109 | 109 | 105 | 105 | -4 | 105 | 105 | 105 | 105
9 | Kolar | 175 | 175 | 4:34 | 4082:20 | 1603:38 | 4418:15 | 6021:53 | 6026:27 | 34:26 | 95.3749 | 95.3714 | 2810.6734 | 385:28 | 94.5131 | 94.1596 | 6028 | 160038 | 6026.45 | 34.4457 | 34.4369 | 24:00 | 164 | 164 | 160 | 160 |  | 155 | 155 | 160 | 160
10 | KGF | 198 | 183 | 0:00 | 64:08 | 2058:55 | 2307:29 | 4366:24 | 4366:24 | 22:03 | 97.036 | 97.036 | 3107.3972 | 376:39 | 94.298 | 94.2931 | 5426 | 296891 | 4366.4 | 29.6503 | 23.8601 | 24:00 | 197 | 183 | 197 | 183 |  | 197 | 183 | 197 | 183
11 | CB Pura | 200 | 200 | 422:30 | 4343:25 | 1639:36 | 1206:35 | 2846:11 | 3268:41 | 16:21 | 98.0872 | 97.8033 | 2004.241 | 240:31 | 96.685 | 96.3559 | 4899 | 224667 | 3268.68 | 24.495 | 16.3434 | 24:00 | 194 | 194 | 194 | 194 |  | 194 | 194 | 194 | 194
12 | Chintamani | 149 | 149 | 2:35 | 96:54 | 1376:01 | 1089:04 | 2465:05 | 2467:40 | 16:34 | 97.7763 | 97.774 | 1525.8584 | 245:47 | 96.286 | 96.2761 | 1899 | 168611 | 2467.66 | 12.745 | 16.5615 | 24:00 | 147 | 147 | 147 | 147 |  | 147 | 147 | 147 | 147
13 | Devanahalli | 33 | 33 | 14:35 | 246:36 | 366:56 | 414:28 | 781:24 | 795:59 | 24:07 | 96.8174 | 96.758 | 20589:16 | 623:55 | 90.6599 | 90.5467 | 1360 | 44680 | 795.98 | 41.2121 | 24.1206 | 24:00 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33
14 | Hosakote | 32 | 32 | 32:35 | 342:12 | 128:15 | 329:22 | 457:37 | 490:12 | 15:19 | 98.0779 | 97.941 | 6451:25 | 201:36 | 97.1074 | 96.9454 | 819 | 35770 | 490.2 | 25.5938 | 15.3187 | 24:00 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32
15 | Nelamangala | 17 | 17 | 5:06 | 117:54 | 239:06 | 92:35 | 331:41 | 336:47 | 19:49 | 97.3776 | 97.3373 | 5580:31 | 328:16 | 95.1314 | 95.0263 | 570 | 37038 | 336.78 | 33.5294 | 19.8106 | 24:00 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17
16 | Doddaballapura | 40 | 40 | 95:44 | 443:25 | 138:34 | 335:10 | 473:44 | 569:28 | 14:14 | 98.4082 | 98.0865 | 14900:06 | 372:30 | 94.524 | 94.356 | 1081 | 23503 | 569.46 | 27.025 | 14.2365 | 24:00 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40
17 | Magadi | 60 | 60 | 9:20 | 153:18 | 992:48 | 434:25 | 1427:13 | 1436:33 | 23:57 | 96.8028 | 96.7819 | 13186:55 | 219:47 | 96.7087 | 96.67 | 1823 | 51665 | 1436.55 | 30.3833 | 23.9425 | 24:00 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42
18 | Chandapura | 20 | 20 | 28:15 | 141:07 | 465:13 | 274:16 | 739:29 | 767:44 | 38:23 | 95.0304 | 94.8405 | 3906:16 | 195:19 | 97.1476 | 97.0407 | 1083 | 50216 | 767.733 | 54.15 | 38.3866 | 24:00 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19
19 | Ramanagara | 55 | 55 | 10:26 | 169:48 | 816:57 | 314:35 | 1131:32 | 1141:58 | 20:46 | 97.2348 | 97.2093 | 12852:23 | 233:41 | 96.5062 | 96.4594 | 2254 | 34489 | 1141.96 | 40.9818 | 20.7629 | 24:00 | 39 | 39 | 39 | 39 |  | 39 | 39 | 39 | 39
20 | Channapatna | 76 | 76 | 23:52 | 456:34 | 966:43 | 638:07 | 1604:50 | 1628:42 | 21:26 | 97.1618 | 97.1196 | 20055:02 | 263:53 | 96.0928 | 96.0018 | 3926 | 62864 | 1624.7 | 51.6579 | 21.3776 | 24:00 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47
21 | Kanakapura | 111 | 111 | 28:13 | 230:42 | 2474:47 | 916:09 | 3390:56 | 3419:09 | 30:48 | 95.894 | 95.8598 | 1611.0153 | 348:20 | 94.7538 | 94.7223 | 4103 | 115531 | 3419.15 | 36.964 | 30.8032 | 24:00 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110
NOTE:
1. 10 number of feeder are included in the rural areas of Kolar division from the District headquarters of ANX-1.
2. 05 numbers of feeders F-6 Pathuru, F-7 Kotaladinna, F-8 Kothapally, F-7 Kolimpally, F-6 Gudipalli emanating from Mandilkal 66/11, Ramapura 66/11Kv, Chakavelu 66/11KV, Thimmampalli 66/11Kv, Pathapalya 66/11KV, repestively are commissioned feeding the rural reas of CB pura Division during the month of DEC-2019
2. 01 number of feeders F-4 Panasachowdanahalli emanating from 66/11Kv Kodihalli is commissioned, feeding the rural reas of Chintamani Division during the month of DEC-2019
6. Reliability Index of Dodaballapura has reduced as 05 nos of feeders (F12, F14 of 66/11 KV Muss Budhigere and F18, F20, F29 of 66/11 KV Muss Devenahalli) were faulty due to cable fault, since the load change over was done, no load was affected.
Note: In Davanagere division 2 Nos of NJY feeders Neetigere & Nibgur are newly commissioned on Devarahally 66/11KV station.