## M.I Gen & lines-16-11-2021
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED (WHOLLY OWNED BY GOVERNMENT OF KARNATAKA UNDERTAKING)
(B) INTERRUPTION DETAILS WITH REASONS ON |  |  | 2021-11-16
STATE GENERATOR OUTAGES
Sl.NO | GENERATION STATION/UNIT | OUTAGES |  | REMARKS
|  | FROM | TO
1 | UPCL: U1 | 22:31 (27.08.2021) |  | O/O COAL SHORTAGE & LATER TO RSD FROM 00HRS OF 19.10.2021
2 | UPCL: U2 | 21:49 (27.08.2021) |  | O/O COAL SHORTAGE & LATER TO RSD FROM 00HRS OF 19.10.2021
3 | RTPS: U7 | 04:42 (12.11.2021) |  | O/O RESERVE SHUTDOWN
4 | RTPS: U5 | 10:54 (09.11.2021) |  | O/O GT PROTEC OPERATED
5 | BTPS:U2 | 11:43 (09.11.2021) |  | O/O RESERVE SHUTDOWN
6 | RTPS: U3 | 21:11 (13.11.2021) |  | O/O RESERVE SHUTDOWN
7 | YTPS:U2 | 05:56 (15.11.2021) | 09:38 (16.11.2021) | O/O FURNACE PRESSURE LOW
8 | RTPS:U8 | 09:50 (10.11.2021) |  | O/O RESERVE SHUTDOWN
Sl.NO | NAME OF THE LINE | OUTAGES |  | REMARKS | PRESENT STATUS
|  | FROM | TO
1 | 220kV Kudugi-G M Navar#4 | 21:07 (28.08.2020) |  | TRIPPED | WORK UNDER PROGRESS(RELAY REPLACEMENT)
2 | 315 MVA ICT #2 at RTPS | 18:42 (23.07.2021) |  | Tripped
3 | 220KV-AMBEWADI - PONDA-1 | 17:21 (25.10.2021) |  | Tripped
4 | 400KV-KAIGA - GUTTUR-2 | 20:58 (10.11.2021) |  | O/O On OV
5 | 400KV-NARENDRA - GUTTUR-1 | 21:22 (10.11.2021) |  | O/O On OV
6 | 400KV-DONI - GUTTUR-1 | 10:39 (16.11.2021) | 17:34 (16.11.2021) | O/O on L/C | CHARGED
7 | 220KV-KAIGA - KADRA-1 | 06:17 (16.11.2021) | 12:24 (16.11.2021) | Tripped | CHARGED
8 | 220KV-KAIGA - KODASALLY-1 | 09:18 (16.11.2021) | 11:46 (16.11.2021) | Tripped | CHARGED
9 | 220kV Hubli-NRN#2 | 11:05 (16.11.2021) | 12:10 (16.11.2021) | O/O on L/C | CHARGED
10 | 220kV Lingapr-BTPS | 12:00 (16.11.2021) | 14:24 (16.11.2021) | Tripped | CHARGED
11 | 220kV Hubli-NRN#1 | 12:14 (16.11.2021) | 14:25 (16.11.2021) | O/O on L/C | CHARGED
12 | 220kV SGS-SMG#3 | 15:30 (16.11.2021) | 16:25 (16.11.2021) | Tripped | CHARGED
13 | 220kV SGS-SMG#4 | 15:30 (16.11.2021) | 16:22 (16.11.2021) | O/O on O/V | CHARGED
14 | 400kV UPCL-Hassan#2 | 23:22 (16.11.2021) | 07:36 (17.11.2021) | O/O on O/V | CHARGED
15 | 400kV BTPS-Hiriyur#2 | 23:42 (16.11.2021) | 07:38 (16.11.2021) | O/O on O/V | CHARGED
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32