## M.I Gen & lines-31-10-2021
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED (WHOLLY OWNED BY GOVERNMENT OF KARNATAKA UNDERTAKING)
(B) INTERRUPTION DETAILS WITH REASONS ON |  |  | 2021-10-31
STATE GENERATOR OUTAGES
Sl.NO | GENERATION STATION/UNIT | OUTAGES |  | REMARKS
|  | FROM | TO
1 | RTPS: U3 | 18:38 (02.10.2021) | 20:13 (30.10.2021) | O/O ON COAL SHORTAGE
2 | RTPS: U2 | 12:50 (18.10.2021) |  | O/O ASH EVACUATION WORK,LATER ON COAL SHORTAGE
3 | RTPS: U1 | 21:28 (31.10.2021) |  | O/O BOILER TUBE LEAKAGE
4 | RTPS: U8 | 06:49 (30.10.2021) |  | O/O BOILER TUBE LEAKAGE
5 | BTPS: U3 | 22:17 (24.09.2021) |  | O/O DUE TO BOILER AIR FLOW LOW, LATER ON COAL SHORTAGE
6 | YTPS: U2 | 17:01 (16.10.2021) | 02:23 (01.11.2021) | O/O TURBINE PROTECTION OPERATED
7 | YTPS: U1 | 16:54 (29.10.2021) |  | O/O BOILER TUBE LEAKAGE
8 | UPCL: U1 | 22:31 (27.08.2021) |  | O/O COAL SHORTAGE & LATER TO RSD FROM 00HRS OF 19.10.2021
9 | UPCL: U2 | 21:49 (27.08.2021) |  | O/O COAL SHORTAGE & LATER TO RSD FROM 00HRS OF 19.10.2021
Sl.NO | NAME OF THE LINE | OUTAGES |  | REMARKS | PRESENT STATUS
|  | FROM | TO
1 | 220kV Kudugi-G M Navar#4 | 21:06 (28.08.2020) |  | TRIPPED | WORK UNDER PROGRESS(RELAY REPLACEMENT)
2 | 315 MVA ICT #2 at RTPS | 18:42 (23.07.2021) |  | Tripped
3 | 220KV-AMBEWADI - PONDA-1 | 17:21 (25.10.2021) |  | Tripped
4 | 400kv Guttur-NAR | 02:06 (30.10.2021) |  | o/o on OV
5 | 400kv Kaiga-Guttur- 2 | 22:34 (30.10.2021) |  | o/o on OV
6 | 400KV-TALGUPPA - HASSAN-1 | 09:52 (31.10.2021) | 16:46 (31.10.2021) | O/O on L/C | CHARGED
7 | 400KV-BTPS - HIRIYUR-2 | 22:23 (31.10.2021) |  | o/o on OV
8 | 220kV Alipura-Ragalpadu | 04:56 (31.10.2021) | 06:23 (31.10.2021) | Tripped | CHARGED
9 | 220kV RTPS-Mallat | 06:00 (31.10.2021) | 06:25 (31.10.2021) | Tripped | CHARGED
10 | 220kV Bidnal-NPH | 09:19 (31.10.2021) | 18:32 (31.10.2021) | Tripped | CHARGED
11 | 220kV NRN-Kanbargi#2 | 10:26 (31.10.2021) | 13:47 (31.10.2021) | O/O on L/C | CHARGED
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32