## M.I Gen & lines-18-02-2024
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED (WHOLLY OWNED BY GOVERNMENT OF KARNATAKA UNDERTAKING)
INTERRUPTION DETAILS WITH REASONS ON |  |  | 2024-02-18
Sl.NO | GENERATING UNITS | OUTAGES |  | REMARKS
|  | FROM | TO
1 | RTPS: U1 | 20:00 (20.06.2022) |  | O/O COAL HANDLING ISSUE (BUNKER COLLAPSED)
2 | BTPS: U3 | 21:49 (14.02.2024) | 20:14 (18.02.2024) | O/O BOILER TUBE LEAKAGE
3 | BTPS: U2 | 00:03 (10.02.2024) |  | O/O TURBINE LUBEOIL HEADER PRESSURE DROPPING
4 | RTPS: U3 | 02:18 (18.02.2024) |  | O/O ANNUAL OVER HAULING
5 | RTPS: U2 | 00:46 (19.02.2024) |  | O/O TRIPPED DUE TO HRH BONNET LEAKAGE
6
7
8
9
10
11
Sl.NO | NAME OF THE LINE | OUTAGES |  | REMARKS | PRESENT STATUS
|  | FROM | TO
1 | 220KV Savadatti-Bidnal | 06:20 (20.12.2023) |  | O/O ON LINE CLEAR | 72DAYS
2 | 400KV BUS-2 @RTPS | 11:00 (22.01.2024) |  | O/O ON LINE CLEAR | 9 DAYS
3 | 220kV EPIP-ITPL | 12:59 (30.01.2024) |  | O/O ON LINE CLEAR | 15DAYS
4 | 220kV Narendra-Ghataprabha#1&2 | 11:00 (17.02.2024) |  | O/O ON LINE CLEAR
5 | 400kV Yalahanka-DHP #1 line | 08:09 (18.02.2024) | 15:56 (18.02.2024) | O/O ON LINE CLEAR
6 | 220kV Honnali-Davanagere #1&2 line | 09:45 (18.02.2024) | 10:10 (18.02.2024) | O/O ON LINE CLEAR
7 | 220kV Narendra-Hubli#1 | 10:04 (18.02.2024) | 18:26 (18.02.2024) | O/O ON LINE CLEAR
8 | 220kV Kemar-Varahi # 2 | 12:04 (18.02.2024) | 15:20 (18.02.2024) | O/O ON LINE CLEAR
9 | 220kV Talaguppa-STRP | 12:19 (18.02.2024) | 12:49 (18.02.2024) | O/O ON LINE CLEAR
10 | 220kV Shimogga-STRP | 12:20 (18.02.2024) | 12:46 (18.02.2024) | O/O ON LINE CLEAR
11 | 400kV Nalamangala-Talaguppa | 13:53 (18.02.2024) | 19:49 (18.02.2024) | TRIPPED
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
LINE OPENS DUE TO POWER REGULATION/OVER VOLTAGE
1 | 220kV Chickmangalore-SMG | 08:10 (17.02.2024) |  | O/O ON P/R
2
3
40
41
42
43
44
45
46
47
48
49
50