## Case to case
BANGALORE ELECTRICITY SUPPLY COMPANY LIMITED
Format-1
Proforma for reporting fatal / non-fatal accidents to departmental / non-departmental person and animals for the month of DECEMBER 2020
SL No | Name of the Circle | Name of Division | Name of Sub Division | Date of Accident | Place of occurrence of accident | Name and address of the victim/ owner In case of animal | Mech /Elec | Whether accident fatal/non-fatal, dept/non-dept/animal |  | Whether the cause of accident is attributable to KPTCL / ESCOMs or attributable to victim or due to natural calamity | Reasons | Analysis
[7 empty] | M/E | F/NF | D/ND |  |  |  | district
1 | South | Jayanagar | S2 | 05.12.2020 | 1st main road, Pothalappa garden, Augodi post, | Sri. Mahesh P, 40yrs, LM | E | NF | D | Victim | The victim climbed the pole for replacing the HG fuse, accidentally touched the HG fuse unit of another charged installations, fell down fromn the pole and got injured. | Neglect of safety measures | Banglore Urban
2 | South | Jayanagar | S5 | 02.12.2020 | Maruthi layout, 7th main, 3rd cross, Vasanthapura | Sri. Shomsuya | E | F | ND | Victim | The electrical accident occurred while carrying construction work of house by labours in second floor of building. The victim while lifting iron bars over lintel, the iron bars accidentally came in contact with 11kV overhead line running in front of the building and got electrocuted. | Accidental contact with 11kV line | Banglore Urban
3 | South | HSR | S8 | 11.12.2020 | Chikkabegur gate road, opp to Swati medical store, Hongasandra O&M | Sri. Sachin s/o Tejaswini, 16yrs | E | NF | ND | Victim | The victim Sachin had come to Sri. Ravikumar's house for studying purpose on 11.12.2020 nigt. Later victim went to terrace along with Sri. Purushotam s/o Kala, 17yrs( residing in Ravikumar's house) to bring the book kept on terrace at around 23:45hrs. Sri. Purushotam stated that when they went to terrace to collect the book, few papers flew away from the book and in order to collect the papers, Sachin jumped and accidetnally came in contact with 11kV line of F13 feeder of Naganathapura station which is passing near the building and got injured. | Accidental contact with 11kV line | Banglore Urban
4 | Kolar | Kolar | Kolar RSD | 12.12.2020 | Kondenahalli village | Kumari. Neethu Sindya, 7yrs Kondenahalli village | E | NF | ND | Natural Calamity | At 12pm, Victim was playing and her grand mother was washing the clothes in front of the house. When the agri feeder charged on12pm, immediately the 100KVA Transformer secondary wire got cut and fall on the victim & her grand mother. Grand mother escaped and secondary wire fell on 7yrs old girl and got injured. | Snapping of conductor LT | Kolar
5 | Kolar | Chikkaballapura | CSD | 05.12.2020 | Sadenahalli, O&M-4 unit | Sri.Ambrish s/o late.Narayanappa | E | NF | ND | Natural Calamity | Due to insulator breakage the LT wire fallen on the victim. | Snapping of conductor LT | Chikkaballapura
6 | Davanagere | Chitradurga | RSD | 11.12.2020 | Emmanagatta village | Sri. Vishwanath Sangana Gowda. JPM, Bharamasagara Section | E | NF | D | Victim | While doing changeover of Spur line of 11kV F9 Bahaddurgatta line from Bharamasagara MUSS, accidentally got electrocuted & got injured. | Neglect of safety measures | Chitradurga
7 | Davanagere | Chitradurga | RSD | 24.12.2020 | Siddapura village | Sri. M.Amruteshwara, Powerman, Hireguntanur Section | E | NF | D | Victim | While attending jump cut problem of 63KVA of TC Siddapura village, the Powerman Sri.Amruteshwar fell from the pole due to induction effect, got injured. | Neglect of safety measures | Chitradurga
8 | Tumkur | Tumkur | CSD-1 | 07.12.2020 | In Kuntammanahalli thota Sri. Lakshmi body work shop | Sri. Musthafa s/o Mohammad Amir | E | F | ND | Victim | The victim might have electrocuted due to leakage of current while he was working under lorry using grinding machine. | Within consumer premesis | Tumkur
9 | Tumkur | Tiptur | Tiptur | 13.12.2020 | In Hindiskere | Smt. Gayitramma w/o late Ramanna, 51yrs | E | F | ND | Victim | The victim got electrocuted when she went to bring drinking water from Sri. Shankaralingaiah s/o Patel Dodda Honnegowda Borewell IP set & accidentally came in contact with skinout messenger wire. | Within consumer premesis | Tumkur
10 | Tumkur | Tiptur | Turuvekere | 16.12.2020 | Near water pump house of Mallaghatta village | 1 Buffalo Owner: Sri. Nanjappa s/o Rudrappa | E | F | A | Natural Calamity | The buffalo got electrocuted when accidentally came in contact with grounding of 63KVA TC which was supplying power to Mallaghatta lake pump house. | Grounding near TC | Tumkur
|  | Circle |  | Fatal |  | Non Fatal |  |  | Animals | Total
|  |  |  | Dept | Non-Dept | Dept | Non-Dept
|  | North | [7 empty] | 0
|  | East | [7 empty] | 0
|  | West | [7 empty] | 0
|  | South |  |  | 1 | 1 | 1 |  |  | 3
|  | Rural | [7 empty] | 0
|  | Ramanagara | [7 empty] | 0
|  | Kolar |  |  |  |  | 2 |  |  | 2
|  | Tumkur |  |  | 2 |  |  |  | 1 | 3
|  | Davanagere |  |  |  | 2 |  |  |  | 2
|  | Total |  | 0 | 3 | 3 | 3 |  | 1 | 10
General Manager (Q,S&S)
BESCOM

## Acc stats
Name of ELECTIRICITY SUPPLY COMPANY: BESCOM
Yearwise Accidents Abstract
Sl No. | Year | Fatal |  | Non Fatal |  | Fatal Animal | Total
|  | Dept | Non-dept | Dept | Non-Dept
1 | 2016-17 | 12 | 106 | 55 | 26 | 37 | 235
2 | 2017-18 | 10 | 104 | 45 | 34 | 46 | 239
3 | 2018-19 | 8 | 128 | 47 | 44 | 56 | 283
4 | 2019-20 | 9 | 83 | 20 | 37 | 45 | 194
5 | 2020-21 (upto Dec) | 2 | 41 | 15 | 17 | 51 | 126